## INDEX
Uttar Gujarat Vij Company Limited, Mehsana
Performas for FY 2021-22
Performa No. | Particulars | Remarks/Report
SoP 001 | Fatal & Non Fatal Accident Report | Qtrly FY 2021-22
SoP 002 | Action taken report for safety measures complied for the accidents occurred | Half Yly. FY 2021-22
SoP 003 | Register for compiling the complaints classification wise | Qtrly FY 2021-22
SoP 004 | Actions or steps carried out by UGVCL towards public awareness in the year | Qtrly FY 2021-22
SoP 005 | Action taken report by the Redressal Committee | Qtrly FY 2021-22
SoP 006 | Failure of Distribution Transformer. | Qtrly FY 2021-22
SoP 011 A | System Average Interruption Frequency Index (SAIFI) | Qtrly FY 2021-22
SoP 011 B | System Average Interruption Duration Index (SAIDI) | Qtrly FY 2021-22
SoP 011 C | Momentary Average Interruption Frequency Index (MAIFI) | Qtrly FY 2021-22
SoP 012 | System Losses at EHT / 11 KV and below | Half Yly. FY 2021-22
SoP 013 | Meter Faults | Qtrly FY 2021-22
SoP 014 | Statement Showing the ATC losses, Collection efficiency and Billing Efficiency | Half Yly. FY 2021-22
SoP 015 | Release of New Connections | Half Yly. FY 2021-22
SoP 016 | Compensation Details | Qtrly FY 2021-22

## SoP001
Uttar Gujarat Vij Company Limited
QUARTER :- 2nd (July-21 to Sept.-21)
YEAR :-2021-22
Performa - SOP 001 : Fatal and Non-fatal accident report for quarter ending
Sr. No. | Name of area | No.of accidents during the quarter |  |  |  |  | Cumulative since the first quarter of the current FY
|  | Departmental |  | Out side
|  | FH | NFH | FH | FA | NFH | FH | FA | NFH
1 | Sabarmati | 0 | 3 | 7 | 10 | 3 | 16 | 24 | 11
2 | Mehsana | 2 | 1 | 2 | 7 | 0 | 5 | 11 | 3
3 | Palanpur | 1 | 3 | 8 | 12 | 2 | 11 | 17 | 9
4 | Himatnagar | 0 | 1 | 7 | 15 | 2 | 10 | 25 | 4
| TOTAL | 3 | 8 | 24 | 44 | 7 | 42 | 77 | 27

## SoP002
SOP 002 Action taken report for safety measures complied for the accidents occurred Half yearly 2021-22 up to Sept 21
Sr.No. | Circle | Location of Accident | Name of Victim/Owner & Designation | Type of Accident NFH/FH /FA | Dept/Outsider | Date | Name of supervisor & Designation | Detailed Reason of Accident | Finding of CEI/EI/ AEI | Remedies suggested by CEI / EI/ AEI in various cases | Whether the remedy suggested is complied | Action taken to avoid recurrence of such Accident. | Compensation Paid (in Rs)
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14
1 | PLN | Motasada | Solanki Narsibhai Jigabhai | NFH | Outsider | 1.04.2021 / 11:30 AM | NA | While emptiying dry grass from Truck,Victim climbed on shade constructed below 11 KV line,and comes in contact with live wire and got electrocuted. | CEI's Report not received |  |  | Aware consumer to avoid such accident
2 | PLN | Shamsherpura | Bhangi Rajubhai Virmaji | NFH | Outsider | 19.04.2021/11:15 AM | NA | A Eicher vehicle fill up with forage for animal from Dineshbhai Hakmaji Mali's farm then passing from Krantinagar to shamsherpura bus station neliya road and victim sitted over forage,and comes in contact with live wire and got electrocuted. (11 kv mahakali Ag feeder from 66 kv malgadh ss ) | CEI's Report not received |  |  | Aware consumer to avoid such accident
3 | PLN | Sedla | DINESHBHAI CHANDUBHAI FADVAL | FH | Dept | 15.05.2021 @ 10:20 A.M | S C Patel,Elect. Assistant | New 11 KV Raj feeder recently charged from 66 KV jetda ss, it is bifurcated of 11 KV Nanol AG feeder from 66 kv Asodar ss. While taking load of both existing feeder (i.e 11 Kv Nanol and 11 kv Yamuna Ag) feeder on New 11 KV Raj feeder. Line staff working on line by taking line clear of 11 KV Yamuna and 11 KV Raj feeder from 66 KV Jetda ss and 11 KV Nanol feeder section power disconnected by nearby AB switch in single phase schedule. While victim was doing jumpering at location on isolated part of Nanol Ag feeder and victim got electric shock. immediately he was shifted at civil hospital lakhani for primary treatment and on duty doctor declared dead. | CEI's Report not received |  |  | Suspension letter issue wide letter no-UGVCL/DOD-II/HR-40/17.5.2021 | 500000/-
4 | PLN | Jethi-Gangasagar | Chauhan Vipulsinh Baladevsinh | NFH | Dept | 21.05.2021 @ 11.00 A.M | R G Katara, Elect. Assistant | on dtd.21.05.2021 at about 11.00 a.m victim is climbing on shackle pole 11 kv bantawada ag feeder for rejumpering of Top conductor,while checking the power availibility in the line by right hand fingers from pole & suddnly V B Chauhan has been electrocuted and fall down on ground.then he is immediatly admitted to sanjivani hospital Iqbalgadh for primary treatment and then after shifted to MA ICU,Palanpur and then refer to ahmedabad narayani hospital rakhiyal for further better medical treatment. | CEI's Report not received |  |  | show cause notice issue-UGVCL/PLD-II/EST/37-A/2466 Dtd.25.05.2021
5 | PLN | Jaswantgadh | Rabari Ratnabhai Jivabhai (1-Goat) | FA | goat | 18.5.2021 | NA | At the time of fatal animal accident heavy rain & wind so phase wire binding open & from LT Shackle & touch with U-clamp & current passes through GI 8 no wire to ground.at that time goat passes near to the pole and got electocuted & died. | CEI's Report not received |  |  | Maintenance Carried out and Aware Owner of Animal for Safety
6 | PLN | Bhakhar(M) | Vaghela Hanmansinh Valsinh | FA | buffalo | 03.06.21 @ 01.30 | N.A. | During Site visit and statement of Eye witness on Dt 03.06.21 arround 01.30 hrs due to heavy cyclone with rain, the heavy tree branch of neem tree fall on 3phase 4 wire LT line and wires broken and at same time the buffalo which was tied in cattle shed suddenly ran away and came in live contact with broken LT line and got electrocuted and died on the spot | CEI's Report not received |  |  | Maintenance Carried out and Aware Owner of Animal for Safety
7 | PLN | Saral | Patel Valabhai Shantibhai | FA | cow | 04.06.2021 @ 01:30 pm | NA | 11 KV Laxmipura AG feeder (in 3-Ph Schedule power) supply which is emanating from 66 KV Dhanera SS. Due to 11 KV Laxmipura AG feeder (in 3-Ph Schedule power) supply HT conductor broken at from shackle pole at outer side at Location 99/31-32 to 33 and same was cow tied under tree and came (Giving Milk) in contact with live conductor and got electrocuted and she was died on the spot. | CEI's Report not received |  |  | Maintenance Carried out and Aware Owner of Animal for Safety
8 | PLN | Kant | Suratsinh somaji thakor | NFH | Dept(mech) | 17.06.2021 @11.30 AM | NA | Victim had given single phase Residential New Connection after completion of work he was trying to step down from LV line PSC pole. At second step from top of PSC pole his leg balance disturbed due to street light fixture then he fell down on ground and met with NON FATAL MECHANICAL Accident. | CEI's Report not received |  |  | Aware consumer to avoid such accident
9 | PLN | Suigam | Parmar Ranabhai Nanjibhai 1 Nos Buffalo | FA | buffalo | 21.06.21 @ 16.30 Hrs | NA | On Dtd. 21.06.21 around 04.30 Pm buffalo was passing from near transformer structure. At that time peacock was shorted between LT Stud and earthing of TC. So current was grounded. Same time buffalo came in contact with leakage current & died . | CEI's Report not received |  |  | Maintenance Carried out and Aware Owner of Animal for Safety
10 | PLN | Sarakla | Solanki Maganbhai Lebabhai | FA | buffalo | 23.06.2021/11:00 AM | NA | On date:23.6.2021 , As per Owner's statement , around 11:00 AM , There was sparked in owner's wiring and leakage current is passedthrough Fan circuit which was hanged on iron structure (Shed). There is no any burn injury found on body of buffalo, PM report not done by party, ELCB not provided by party in wiring. | CEI's Report not received |  |  | Maintenance Carried out and Aware Owner of Animal for Safety
11 | PLN | Shihori | jayantibhai Bhikhabhai Sampariya(valmiki) | FH | Outsider | 30.06.21 @ 6.15 AM | NA | Victim was seated under LV Line of old bus stand area and conductor was broken for unknown reason and as per confesion of eye witness he was electrocuted by LV Line conductor which was broken. | CEI's Report not received |  |  | Aware consumer to avoid such accident
12 | PLN | Juni Sarotri | Bhil Prakashbhai Kevalabhai | FA | cow | 10.7.2021 | NA | On date 10.07.2021 at approximate 07.00 pm due to heavy wind & rain started the conductor of 3p4w LT line passing near Farmhouse of Shri Prakashbhai kevalabhai Farmhouse was broken.The cow is tied near Lt line,but due to conductor broken she was run & come into cotact with live conductor & died. | CEI's Report not received |  |  | Maintenance Carried out and Aware Owner of Animal for Safety
13 | PLN | Pedagada | Nareshkumar Parthibhai Loh(Electrical Assistant-) | NFH | Dept | 14.7.2021 | Shri M.B.Parghi (ALM) | on dated 14/07/2021 at 11:35 am@, during attending line PF of 11kv Pedagada ag feeder, through oversite, while jumpering on A.B switch , due to snake climb on y phase 66 kv malan-vasan line isolator electric jerk comes on 11 kv side and Shri N.p.loh was eleculated and got electric shock.The current sparks on his left hand and left leg .He was then come below from the pole and go to for primary treatment at pvt hospital at malan village and then taken to MA ICU for Other reports.The doctor has checked him and said that he is out of danger and relieved after 03 hours also advised to take rest for one week | CEI's Report not received |  |  | Memo issue wide letter no-2905/15.7.2021
14 | PLN | Kansara | Shri Gamar Kalabhai Lalabhai | FA | buffalo | 15.7.2021 | NA | During site visit it is found that on Date 15.07.2021,05:30 PM due to heavy wind and rain pin insulator was puncture on shackle pole of 11 kv jethi ag feeder,and leakage current pass through earthing wire and earthing wire ,the Buffalo was passing near the pole & she get Trapped with stay wire ,she shake the head to free from stay and hence stay touched with the earthing wire and buffalow got electrocuted and died on spot. | CEI's Report not received |  |  | Maintenance Carried out and Aware Owner of Animal for Safety
15 | PLN | Bhadiya | Rabari Ronakbhai Rameshbhai | FH | Outsider | 19.07.21 @3.15 PM | N.A. | LT line Phase conductor touch with U clamp & current passing in earth wire, So leakage current pass in earth wire & at that time children playing near this pole at that time came in contact with earthing so this fatal accident occurred. | CEI's Report not received |  |  | Aware consumer to avoid such accident
16 | PLN | Nana-Meshra | FH (1)Choudhary Likhamaram Tulcharam & NFH-Sindhi AcharKhan IbrahimKhan | FH & NFH | Outsider | 25/07/2021 Approx. 13:05 Hrs. | NA | victim started cleaning and washing truck body at same time he has start truck engine and pulled the hydraulic liver of truck and while washing, truck body slowly lifted through hydraulic pump towards the 11 KV Border Ag feeder emanating from 66 KV Piluda SS at same time truck body came in contact with live HT line of Border AG feeder during single phase schedule victim Shri Likhama Ram got electric shock and death on the spot, hence fatal electric accident occurred. Other Shri Sindhi Achar Khan Ibhrahim Khan heard the sound of sparking and shouting he run to stop running truck engine to pull down the truck body and he was contact with live truck body hence non-fatal electric accident occurred. | CEI's Report not received |  |  | Aware consumer to avoid such accident
17 | PLN | Khimanavas | 1. Bhil Paruben Rahulbhai. 2. Bhil Babiben Rahulbhai | NFH | Outsider | 25.07.21 | N.A. | As per statement of Shri Bhil Rahulbhai Anabhai, His wife and baby girl was going for toilet accidently victim Shri Bhil Paruben Rahulbhai came in contact with snapped conductor of 11KV Reluchi Ag. Feeder and both got electric sock and Non fatal human accident occure | CEI's Report not received |  |  | Aware consumer to avoid such accident
18 | PLN | Rampura | Ashokbhai Jayantiji Thakor | FH | Outsider | 27.07.21 | N.A. | Victim chrged their mobile phone with loose wire whose insulation was damaged at so many location. This loose wire connected with socket, which socket was connected with Agriculture connection fuse board which was about 20 meter away. Socket was hanged under tractor trolley. Victim was contected with live portion of loose wire and got socked and died. | CEI's Report not received |  |  | Aware consumer to avoid such accident
19 | PLN | Rangpur | Patel Prakashkumar Babulal | FH | Outsider | 28/07/2021 & at 08:45 Hrs approx | NA | Victim Shri Patel Prakashkumar Babulal was reached in morning for spray of fertilizer at his own farm at Night duration one conductor broken of 4 wire LT line which is AG LT on ground at his farm at that time x'mer power supply is live victim working for spraying of fertilizer from his bucket and he was reached at live broken conductor and came in contact with broken conductor and got electric shock and death on the spot and fatal electrical accident occurred. | CEI's Report not received |  |  | Aware consumer to avoid such accident
20 | PLN | VARVADA | RABARI JALABEN MAGANBHAI | FA | cow | 28/7/21 & AT 10.15 AM APPROX | NA | 11 KV BRAHMANWADA AG FEEDER EMANATING FROM 66 KV KHALI SS WAS BROKEN DUE TOPIN PUNCTURE ON LOCATION NUMBER 110/37 AND COW WAS GRAZING NEAR LOCATION NUMBER 110/36 AND LIVE BROKEN CONDUCTOR FALLEN ON GRAZING COW AND COW GOT ELECTROCUTED AND DIED | CEI's Report not received |  |  | Maintenance Carried out and Aware Owner of Animal for Safety
21 | PLN | MAKTUPUR | THAKOR BHAVANJI TEJAJI | FA | cow | 28/7/21 & AT 9.55 AM APPROX | NA | ON DATED 28/7/21 , TIME 9.45 AM ON PHONE BY ELECTRICAL ASSISTANT OF MAKTUPUR , BINDING OF LT LINE SHACKLE INSULATOR OF PHASE WIRE OF SINGLE PHASE TWO WIRE LT LINE GOT BROKEN AND IT TOUCH WITH U CLAMP TO EARTHING GI WIRE AND SAME TIME COW CAME IN CONTACT WITH GI WIRE SO COW GOT ELECTROCUTED AND DIED | CEI's Report not received |  |  | Maintenance Carried out and Aware Owner of Animal for Safety
22 | PLN | Charada (M) | Chauhan Bhagavasinh Vajerajsinh | FA | buffalo | 31.7.21 | NA | on dtd.31.7.21 & 4 P.M the buffalo owner shri chauhan bhagavansinh vajerajsinh has taken the buffalo for the water drinlking at Village tank (havado) tank made near the LT pole & contact with Eathing wire & due to leackage current got elecrtocuted and died on the spot.but as the time of village helper checking there were no found leackage current. | CEI's Report not received |  |  | Maintenance Carried out and Aware Owner of Animal for Safety
23 | PLN | Jakhel | Thakor Pareshbhai Rameshbhai | NFH | Outsider | 05.08.21 @13.55 | N.A. | The LT cable of Jakhel village TC supplies from TC to LT line. One of LT cable jumper touched to earthwire of LT Pole. Hence Leakage currunt passes through earth wire. While playing cricket the ball came near LT Pole. The victim came in contact with earthwire where leackage current passes and victim electocuted and got electric shocked. | CEI's Report not received |  |  | Aware consumer to avoid such accident
24 | PLN | Vada | PATNI PRAVINBHAI DANABHAI | FA | buffalo | 08.08.21 @9.55 | N.A. | Due to current passing in neutral of Ag TC of Lallubhai Ramabhai Vaghari, Con No. 72521/00506/1. The near by TC some water logged. The buffalo came in contact with open GI wire of neutral earth & electrocuted & died on the spot. | CEI's Report not received |  |  | Maintenance Carried out and Aware Owner of Animal for Safety
25 | PLN | Duva | Rajput Juvaraji Badraji | FA | buffalo | 15.08.2021 | NA | While Buffalo tied below LT line of 11 KV Achwadiya Ag feeder of Existing TC-100 KVA and existing LT 3Q4W line passing at end pole no-9 end of pole of Shri Rajput Pratapji Badraji existing ag connection. Existing LT line one conductor broken from LT (4W) shackle insulator at from LT pole No. 9 (3Q4W) and buffalo come into live conductor contact and Buffalo got electrocuted and died on the spot. | CEI's Report not received |  |  | Maintenance Carried out and Aware Owner of Animal for Safety
26 | PLN | Dungrasan | PATEL DARSHANKUMAR BHARATBHAI | NFH | Dept | 18.8.21 @4.45 | N.A. | Victim DB Patel, EA(VS) that jumper burn at Dungarasan Golai AB Switch location no 31. The victim DB Patel and SM Patel, EA(REC) at Thara Office are gone to rectify jumper at Dungarasan Golai AB Switch. At location point the victim parked his bike and SM Patel, EA is extracting the operating rod for earthing while the victim DB Patel climb on double pole structure and toched the outgoing jumper of AB Switch of Bhavani AG Feeder. The Bhavani AG feeder in 1 ph, one side phase outgoing jumper is broken, hence the return power from load side to 66 KV SS is electrocucuted the victim and the NonFatal Accident occured. | CEI's Report not received |  |  | ask explaination wide letter no-UGVCL/THARA/HR/4002 Dt. 1.09.21
27 | PLN | Mahadeviya | Rabari (All) Netiibhai Dharmabhai Resi= (Kapasiya) | FA | buffalo | 28.8.2021 | NA | On date 28.08.2021 at approximate 11.00 am ,while the buffalows of Shri Nethibhai Dharmabhai Aal(Rabari) grassing in the D.S.Patel farm of Mahadeviya(Umarkot) village,one buffalow started rubbing with the stay wire of 11 KV Banas JGY line.Due to that the stay wire come into contact with the side conductor of 11 Kv Mahadev Ag feeder emanating from 66 KV Juni sarotri Sub station.Thus the power flow in the stay wire & the buffalow got electric shock & tried to leave but during this other 3 buffalows + 2 Calf near to her come into contact & got shocked & died.(Total 4 Buffalo And 2 Calf) | CEI's Report not received |  |  | Maintenance Carried out and Aware Owner of Animal for Safety
28 | PLN | Vadvas | Vaghela Fulsinh Ratansinh | FA | buffalo | Dt 31.08.2021, Time:04.45 pm approx | NA | On date 31.08.2021 at approximate 04.30 pm due to heavy cyclone with rain,the LT line phases came in contact with each other and one phase conductor broken down and fall on the buffalo and goat which were standing under the LT line and got electrocuted and died on the spot . | CEI's Report not received |  |  | Maintenance Carried out and Aware Owner of Animal for Safety
29 | PLN | UN | LODANA PRAHLADJI SADAJI | FA | Cow-1 & buffalo-1 | 31.08.21 @00.45 | NA | Dee to Kamalpur Ag feeder on fault of kite stick on PSC pole of Kamalpur Ag eminating from Unn ss. The current passed through kite stick to earth wire. The fencing of farm is attached with PSC pole hence the current passing from fencing to cow and buffalo which is tying with iron chain link. Unn MMG staff with LG Damor LM conform that removed the kite stick at top fitting and also the tripping in 66 KV SS conform the 11 KV line tripped due to kite stick. The fatal animal ( Cow-1 & buffalo-1 ) electrical accident occured due to fault current of 11 KV Kamalpur AG feeder | CEI's Report not received |  |  | Maintenance Carried out and Aware Owner of Animal for Safety
30 | PLN | Deesa | Prakashbhai Lavjibhai Umot/ Electrical Assistant | FH (Elect) | Dept. | 02.09.21 | Bipinbhai Somabhai Prajapati/ Lineman | victim and two other staff was alloted complain attending work.. In this work team supervisor was Shri Bipinkumar Somabhai Prajapati (LM). Victim was climbed on PSC pole to to attend 1-Ph. Complaint, on that pole there are 4-wire line including streetlight phase. While doing so he came in contact with live conductor as powersupply was ot isolated/switched off. Safety belt was not wore by victim so when he came in contact with live wire he got electric shock and fell down on ground and met with fatal accident. | CEI's Report not received |  |  | Supervisor Shri B.S.Prajapati Under Suspension wide letter no-UGVCL/PLD/Vahivat/Faraj Mokufi/BSP/113.04.09.2021 | 500000/-
31 | PLN | Palanpur | (1) Jaganiya Kokilaben Bhaveshbhai (2) Jaganiya Jaimin Bhaveshbhai (3) Jaganiya Ved Bhaveshbhai | FH | Outsider | Dt 02.09.21, time:16:30 Approx | N.A. | On dated 02.09.21,time:16:30hours approximate,the wire of the FOX HALOGEN kept farm got heated and same live wire fallen on fencing done for crop's protection from Animal in the farm and at the same time woman and her two child came in contact with live fencing got electrocuted and died . | CEI's Report not received |  |  | Aware consumer to avoid such accident
32 | PLN | Bapala | Fatal Human of Mrs. Luhar Pyariben Ragabhai & Kum. Luhar Ranjanben Ragabhai | FH | Outsider (Private Premises) | 07.09.2021 | NA | BOth Victim of Mrs. Luhar Ranjanben Ragabhai (age-48 Years) is trying to hanging wer clothes for drying purpose on iron wire (Centing Wire) at that time she got electric shock which is occured due to leakage current passing from their faulty ceiling fan to iron sheet roof shed (Iron Patra & Supporting Angles) to iron wire (on which she was trying to hanging of wet clothes for dry purpose). Further Victim of Shri Pyariben Ragabhai (Age-22 Years) also getting to electric shock during saving to her daughter of Kum. Ranjanben and she also electrocuted and died on the spot. Both victim died on the spot due to leakage of electric current shock in at home premises (Private Premises) as per primary reason. | CEI's Report not received |  |  | Aware consumer to avoid such accident
33 | PLN | Bhakodar | Rabari Khodabhai Mashrubhai/01 nos Buffalo-Owner-Rabari Khodabhai Mashrubhai | FH & FA | Outsider | Dt 07.09.21, time:16:30 Approx | N.A. | On dated 07.09.21,time:16:30 hours approximate, Due to heavy Cyclone with rain,the big neem tree came out along with root and fall on 2W LT line and the victim and his buffalo who were passing at that time,the both neem tree & LT line fall on both victim and both are electrocuted and died on the spot | CEI's Report not received |  |  | Aware consumer to avoid such accident
34 | PLN | LOTIYA | PATEL GANDABHAI VIRCHANDBHAI | FH (Outsider) | Outsider | 08.09.21 @14.00 | NA | On dtd. 8.09.21 at about 14.00 Hrs said accident occurred at Lotiya to Dhrandavda Neliya, Patel Gandabhai Virchandbhai Ag Flat rate connection, Site visited by SDO & team on Dtd. 09.09.21 , As per statement of Gandabhai V. Patel'S Son Mahendrabhai G PAtel said at the time of binding DO fuse link with his wooden operating rod of Ag TC he got electric shock & fallen on ground but as per investigation , there will be no any spot found on wooden operating rod, TC incoming cable jumpers & DO fuse. More over at that time no any tripping recorded on 66 KV Dahisar SS, Lotiya Ag feeder. | CEI's Report not received |  |  | Aware consumer to avoid such accident
35 | PLN | Velavas | Popatji pradhanji madaniya | NFH | Dept(mech) | 13.09.2021 | NA | on dtd.13.09.2021 the victim shri popatji pradhanji madaniya while climbing on Ag TC loc.no-153 of Ratanpur Ag feeder for complain suddenly his leg slip and he fell down on ground and met with non fatal mechanical accident. | CEI's Report not received |  |  | Aware consumer to avoid such accident
36 | PLN | Sonvadi ta: Amirgadh | Rabari Netabhai Hidabhai | FA | buffalo | 24.9.2021 | NA | During site visit it is found that on Date 24.09.2021,04:30 PM due to pin insulator was puncture on pin pole of 11 kv balundra ag feeder,and ht conductor broken and fall in the water collected on the ground,the Buffalo and calf sitting in water come got electric shock , buffalo died and calf after 2 days on 26.9.2021. | CEI's Report not received |  |  | Maintenance Carried out and Aware Owner of Animal for Safety
37 | PLN | Vasi | Rabari Lalabhai Bijolbhai | FA | One cow and two calves | 27.9.2021 | NA | Dt. 27/09/2021,at about 10:30 am at side we have found that one ag con.of rabari Lalabhai Bijolbhai sevice wire was fixed at angel of shed . The wire cutdown slightly and gets touch with angle and leakage current spread in all angle and chhanel off all shed. One cow and two calves among approx 13 nos was touched with iron angle and get electric shock and died . | CEI's Report not received |  |  | Maintenance Carried out and Aware Owner of Animal for Safety
38 | HMT | Navi Kadoli, Aambavadi Vistar | Patel bharatkumar shamalbhai | FA(COW) | cow | 18.05.2021 | NA | Due to "Tauktae" cyclone weather conditions , heavy wind flowing during evening hours & B'coz of that Live LT Line Conductors emanating from kadoli village transformer was snapped & fallen on cow . Thus Cow came in direct contact with the live current wire & Died at spot . | ACCIDENT OCCURRED DUE TO LT CONDUCTOR BROKEN DUE TO HEAVY WIND TREE FALLEN ON LINE & COW CAME IN CONTACT | LT LINE MAINTAIANCE SHOULD BE DONE PERIODICALLY & PRPOPERLY | LEAKAGE CURRENT REMOVED & LOCATION RECTIFIED | LEAKAGE CURRENT REMOVED & LOCATION RECTIFIED | 30000
39 | HMT | GABAT | COW OF SHRI REVABHAI GIGABHAI BHARWAD | FA(COW) | cow | 20-05-2021 | NA | 7-8 Cows of above said owner were grazing around in AG LT was there in AG land,also one GI wire for earthing was connected.due to cyclone,thiS GI wire snapped and fell on ground.while starting the vasadara AG feeder (in fault),leakage current flew in GI wire and at the same time,cow passed over the GI wire and got electrocuted and died on spot. | ACCIDENT OCCURRED DUE TO LT CONDUCTOR BROKEN DUE TO HEAVY WIND TREE FALLEN ON LINE & COW CAME IN CONTACT | LT LINE MAINTAIANCE SHOULD BE DONE PERIODICALLY & PRPOPERLY | LEAKAGE CURRENT REMOVED & LOCATION RECTIFIED | LEAKAGE CURRENT REMOVED & LOCATION RECTIFIED | 30000
40 | HMT | IPLODA | TARAR PRAVINBHAI KALUBHAI | FA | buffalo | 26.05.2021 | NA | An incident was taking place in the Ag Land of victim on date 26/05/2021 morning approx 7:00 am where the buffalow was came in contact with the open distributuon box of 100 KVA transformer of 11 KV Ipaloda AG feeder and got electocuted and died. | CEI PENDING |  |  | LOCATION RECTIFIED | 15000
41 | HMT | G.SHAMALAJI | RABARI RAMABHAI GOBARBHAI | FA | cow | 19.05.21 | NA | On dtd. 19.05.2021 at 10:00 aprrox. Due to heavy rain and wind sevice wire broken and touched to RCC piller so cow came in contact with RCC piller got electrocuted & died on the spot…. | ACCIDENT OCCUREDED DUE TO SERVICE BROKEN & TOUCH EARTHING WIRE ,COW CONTACT WITH EARTH WIRE & DIED | LT LINE MAINTAIANCE SHOULD BE DONE PERIODICALLY & PRPOPERLY | LEAKAGE CURRENT REMOVED & LOCATION RECTIFIED | SERVICE WIRE REPLACE LEAKAGE CURRENT REMOVED & LOCATION RECTIFIED | 30000
42 | HMT | BHADRESHAR | MAKWANA DASHRATH NATHUSINH | FA | cow | 6.6.21 |  | on datted 6.6.21 at time 2:30pm during cyclone & heavy rain one neem tree branch fallen on single phase 3 wire jgy lt line in front house of makwana dashrathsing nathusih where one cow standing near cattel shed in this situation live phase conductor snapped near cow.the cow come in contact with this live conductor and fatal electrical accident occured to cow. | ACCIDENT OCCURRED DUE TO LT CONDUCTOR BROKEN DUE TO HEAVY WIND TREE FALLEN ON LINE & COW CAME IN CONTACT & DIED ON THE SPOT | LT LINE MAINTAIANCE SHOULD BE DONE PERIODICALLY & PRPOPERLY | LEAKAGE CURRENT REMOVED & LOCATION RECTIFIED | LEAKAGE CURRENT REMOVED & LOCATION RECTIFIED | 30000
43 | HMT | VAGHPUR | ALPESH N PATEL | FH MECH | DEPT | 7.6.21 |  | The incidence occurred at ramdevnagar (petapara of waghpur village) near infront of jognimatamandir. Shri A N Patel had removed 3 LT Fuse From D.B. and checked that no power is there. thenafter tried to remove branched by operating rod. But not suceed so he climed over neem tree. But the tree dry branch by which he tried climb above suddenly broked and so lost his balance and lied down on earth where RCC road.he lied down with his back and head. Immediately taken him in eeco car by villagers at CHC, Prantij. On duty Doctor have checked him and declared dead. | CEI's Report not received |  |  | PURELY MECHNICAL | 138275
44 | HMT | Malpur | Vaghari Dilipbhai Chandubhai | FH | Outsider | 10.06.2021 | NA | A Fatal Human Electrical Accident occured on date 10/06/2021 at approx 12:30 pm on the 11 KV line of Malpur Urban feeder. When victim was climbed on HT girder pole to save the pegion bird with iron road on line at that time the iron road touched to the line conductor and victim got electric shock and died on the spot. The victim was climbed on pole himself without inform to anyone. | CEI's Report not received |  |  | AWAREING PEOPLE FOR NOT DO UNAUTHORIZED WORK | 50000
45 | HMT | Juna vadvasa | Parmar Bhikhaji Somaji | FA | buffalo & cow | 16.06.2021 | NA | An incident was taking place compount of house Parmar Bhikhaji Somaji were 3 ph 5 wire LT line of 11KV Ambaji jgy feeder LT line passe front of Parmar Bhikhaji Somaji house, at yesterday evening time Conductor of juna vadvasa JGY LT line broken due to heavy rain and cyclone and one buffalo & one cow whose tied under LT line at that time LT conductor broken and came in contact with cattels and got electocuted and died. | ACCIDENT OCCURRED DUE TO LT CONDUCTOR BROKEN DUE TO HEAVY WIND TREE FALLEN ON LINE & BUFFALOCAME IN CONTACT | LT LINE MAINTAIANCE SHOULD BE DONE PERIODICALLY & PRPOPERLY | LEAKAGE CURRENT REMOVED & LOCATION RECTIFIED | LEAKAGE CURRENT REMOVED & LOCATION RECTIFIED | 30000
46 | HMT | VAGHESHVARI | BHAGORA KANTIBHAI KALABHAI | FA | cow | 19.06.2021 | - | On dtd. 19.06.2021 at 09:00 aprrox. Due to heavy rain and wind Ag LT wire broken and fallen on the ground, a cow came in contact with LT wire & electrocuted & died on the spot…. | CEI's Report not received |  |  | LOCATION RECTIFIED | 15000
47 | HMT | Padarvali dungali nu gauchar,VIRPUR | BHARWAD JIVANBHAI KHENGARBHAI | FA(BUFFALO) | buffalo | 19.6.2021 | NA | During site inspection , A Buffalo was found died near supporting stay wire of said agricultural transformer center . At the time of inspection there was no any symptoms of leakage current found at incident location . But may be a Buffalo was died due to any instantaneous leakage current in stay wire by any other means during it's direct contact with supporting stay wire . | CEI's Report not received |  |  | LOCATION RECTIFIED | 15000
48 | HMT | MATHASURIYA | BUFFALO OF SHRI CHAUHAN JANAKBA INDRAVIJAYSINH | FA | buffalo | 20.6.2021 | NA | ABOVE SAID OWNER WERE GRAZZING AROUND IN VILLAGE LAND OF SHRI CHAUHAN JANAKBA INDRAVIJAYSINH IN MATHASURIYA VILLEGE. 3 WIRE JGY LT POLE WAS THERE IN MATHASURIYA LAND AT THA TIME DURING RAINY SEASON,ALSO RAIN STARTED AT LOCATION.EHILE THAT 1 NOS. OF SUBAVAR TREE BRANCH ARE FALLEN ON 3 WIRE JGY LT LINE & & ONE PHASE WIRE ARE SNAPPED FROM LT SHACKLE INSULATOR & CAME IN CONTACT WITH EARTHINFG WIRE OF PSC POLE & GI WIRE OF SAID SERVICE CONNECTION WHICH DIRECTLY CONNECTED TO GALVENIZED ROOF OF SAID OWNER HOUSE WHERE NEAR BY TABELA OF BUFFALO HAD.SO THAT LEAKAGE CURRENT FLOW THROUGH OUT GALVENIZED ROOF. WHILE THAT OE OF BUFFALO CAME IN CONTACT WITH ANGLE OF SAID TABELA GALVENIZED ROOF. SO LEAKAGE CURRENT FLOW THROUTH ITS BODY & DIED | CEI's Report not received |  |  | LOCATION RECTIFIED | 15000
49 | HMT | DANTRAL | DABHI RAMESHBHAI JUMABHAI | FA | buffalo | 28.06.2021 |  | On dtd. 28.06.2021 at 11:30 aprrox. A buffalo was grazzing near by transformer structure there might be flow of momentary leakage current due to LT fault & got electrocuted & died | CEI's Report not received |  |  | LOCATION RECTIFIED | 15000
50 | HMT | KELAVA | DHRANGI MANIBEN CHUNILAL | FH | OUTSIDER | 29.6.21 |  | ON DATE 28.06.2021 LATE NIGHT RAIN WITH HEAVY WIND COMES THATS WHY LT JUMPER WIRE BURNT AND FALL ON OTHER LT CONDUCTOR AND COME AND CONTACT WITH GI EARTHING WIRE AS WELL AS STAY SUPPORT TO POLE. EARLY MORNING ON DATE 29.06.2021 AT 6.15 SHE WAS GOING TO DOWN FROM HER HOUSE TO ROAD ON WAY SHE WAS SLIPPED AND IMMEDIATELY SHE HAS CATCH UP STAY AND CAUSES ACCIDENT OCCURES. | CEI's Report not received |  |  | LOCATION RECTIFIED | 50000
51 | HMT | DOTAD | K P PARMAR(E.A) | NFH | DEPT | 30.06.2021(12:45 NOON) | CO-WORKER N.P. RAVAL(E.A.) & K.A.PATEL(E.A.) | During the attending of feeder fault of 11KV Kalakuva ag feeder from 66KV Golwada S/S, The switch location no 14/8 was isolated and feeder was attended but when same switch reconnected at that time feeder was in fault again so Jumper of loc No 14/52 was removed by victim and the switch location no 14/8 reconnected and feeder was in fault again so colleague of Victim N P Raval has replaced faulty Disc insulator on location no 14/51 and then colleague of victim was seat on switch has reconnected switch and feeder was fully attended and victim climbed on shackle pole to rejumper which was removed during attending of fault without confirming with person/co-worker who had operated the switch during fault attending work and electrocuted and got burns. Victim was sent to CHC Lambadiya for primary treatment and on duty doctor has reffered victim to Life line hospital Idar for further treatment. | CEI's Report not received |  |  | STAFF AWARE FOR WORK WITH SAFETY NOEMS
52 | HMT | JABCHITARIYA | Ninama Nirubhai Nanjibhai | FH | OUTSIDER | 15.7.2021 | NA | victim climed on terrace of his shopping centre & touch damped wooden support to live line 11 KV VASAYA JGY near by shopping centre & got shock & died. | CEI's Report not received |  |  | AWARING PEPOLE FOR DO SAFE DISTANCE OF CONSTRUCTION WORK & MAKE SAFE DISTANCE FROM ELECTRIC ALINE WHILE WORKING | 50000
53 | HMT | CHORIWAD | BULLOCK(OWNER NAME:THAKRDA MANAJI RAMJI) | FA | bullock | 27.7.21 | NA | DUE TO LT CONDUCTOR BROKEN OF CHORIWAD AG FEEDER AND CONDUCTOR WAS HANGING ON TREES OF STREET AND AT THAT TIME BULLOCK CART WAS PASSING THROUGH THE STREET AND BULLOCK TOUCHED THAT WIRE AND ACCIDENT OCCURED.SPACER ALREADY PROVIDED. | CEI's Report not received |  |  | LOCATION RECTIFIED | 12500
54 | HMT | NANDOJ (KHEROJ KAMPA) | PATEL RAVJIBHAI DEVAJIBHAI | FA | buffalo | 30.07.2021 | NA | On dtd. 30.07.2021 at 04:00 Pm aprrox. Due to heavy wind Ag LT wire broken and fallen on Buffalo while eating grass under line came in contact with LT wire & electrocuted & died on the spot…. | CEI's Report not received |  |  | LOCATION RECTIFIED | 15000
55 | HMT | RAMPUR(GAMBHOI), SMASHAN CAMPUS | Parmar Sahdevsinh Kanusinh | NFH | OUTSIDER | 14.7.21 | NA | As per message received from villagers, DE Gambhoi has visited the site immediately. At accident site no any eye witness found, but as per site situation, 11 KV Rajpur JGY feeder HT line passing from smashan area of Rampur(Gambhoi) village & at between location pole number from 31 to 32,there is an illegal toilet constructed under 11 KV HT line. Hence there is a possibility that victim could climbed on terrace of toilet and touched with live conductor of 11 KV Rajpur JGY feeder and fell down in toilet. Then after victim was taken at civil hospital, Himatnagar for further treatment. | CEI's Report not received |  |  | AWARING PEPOLE FOR DO SAFE DISTANCE OF CONSTRUCTION WORK & MAKE SAFE DISTANCE FROM ELECTRIC ALINE WHILE WORKING
56 | HMT | VADALI KAMPA | PATEL VISHNUBHAI ISHVARBHAI | FA | buffalo | 17.7.21 |  | The reason for Animal fatal accident is due to some internal fault of Consumer premises return power back to transformer centre via LT line, a buffalo was grazzing near tc came in contact with lekage current therough earth wire got electrocuted and died | CEI's Report not received |  |  | LOCATION RECTIFIED | 15000
57 | HMT | FINCHOD | RABARI KAMLESHBHAI GOBARBHAI | FA | cow | 20.7.21 | NA | A COW WAS PASSING NEAR AG TC CAME IN CONTACT WITH TRANSFORMER CENTER EARTHINGWIRE AND GOT ELECTRUTED AND DIED AT THE SPOT | CEI's Report not received |  |  | LOCATION RECTIFIED | 15000
58 | HMT | Modasa | TADVI MANUBHAI GANIYABHAI | FH | Outsider | 24.07.2021 | NA | AS PER LETTER RECIEVED FROM THE POLICE STATION AT THIS OFFICE ON DT. 26.07.2021 , DURING SITE INSPECTION AS PER THE EYE WITNESS STATEMENT THE VICTIM WAS DOING THE WORK OF CUTTING BRICKS AT CONSTRUCTION SITE USING A CUTTER MACHINE CONNECTED AT THE LOAD SIDE OF THE METER. MEANWHILE HE CAME IN CONTACT WITH THE SAID MACHINE AND DUE TO SHOCK HE FELL DOWN FROM THE THIRD FLOOR OF THE BUILDING AND DIED. HE MIGHT HAVE EXPERIENCED SUCH SHOCK DUE TO SOME INTERNAL FAULT IN THE MACHINE. | CEI's Report not received |  |  | CONSUMER AWARE FOR SAFETY & INSTALLATION OF ELCB | PRIVATE PREMISES
59 | HMT | NADRI | BAROT KANUBHAI PABJIBHAI (OWNER) & CHAMAR RAMAN MULABHAI | FA | bullock | 25.07.2021 | NA | Due to cyclone and heavy rainfall on dt.:25.07.2021, a conductor of AG LT of 11 KV VAGDI AG emanating from Rupal SS was broken and was lying on the land. The victim Shree CHAMAR RAMANBHAI MULABHAI was passing by the location where the broken conductor was lying, alongwith his bullock-cart. While going through the location the bullock come in proximity of the live conductor lying and got electrocuted. The current then was passed on to the bullock-cart and there on to Shree CHAMAR RAMANBHAI MULABHAI. As a consequence of this event, the bullock died on the spot and Shree CHAMAR RAMANBHAI MULABHAI rescued himself by jumping of the cart immediately as he experienced the electric shock. Then after Shree CHAMAR RAMANBHAIMULABHAI was taken at civil hospital, Himatnagar for further treatment. | CEI's Report not received |  |  | LOCATION RECTIFIED | 12500
60 | HMT | SALERA | GAMAR MALABHAI HARSANBHAI | FA | cow | 29.7.21 | - | Under Kheroj sdn at Salera Village a cow was passing near JGY LT Pole came in contact with pole earthing wire as there was LT 1C AB cable insulation cut and touched with D clamp and got electrocuted and died | CEI's Report not received |  |  | LOCATION RECTIFIED | 15000
61 | HMT | GORA | DESAI RANCHHODBHAI VALJIBHAI | FA | buffalo | 02.08.2021 |  | WHILE GRAZING BUFFALO HORNS WERE RUBBED WITH STAY WIRE OF 3 WIRE LI LINE POLE AND DURING THIS TIME SATY INSULATOR BROKEN & SERVICE WIRE OF PATEL MEGABHAI KARSANBHAI CONN. JOINTS TOUCH WITH ANGLE & BUFFALO ELECTROCUTED . | CEI's Report not received |  |  | LOCATION RECTIFIED | 15000
62 | HMT | NARANPURA | VANZARA RAMSINGBHAI PRATAPBHAI | FA | buffalo | 03.08.21, Time 17:30 | - | Unde Deshotar sdn at Naranpura Village a buffalo was passing near DO structure of Rampur Ag feeder and itched with horn to GI wire so GI wire came in contact with jumper and got electrocuted and died . | CEI's Report not received |  |  | LOCATION RECTIFIED | 15000
63 | HMT | DHAROD | RATHOD RAMSINH JAVANJI | FA | cow | 03.08.21 | - | One Conductor of LT line snapped from LT stand Pole and touched to D clamp so lekage current came to trnasformer where Cow came in contact with earthing of tc centre & get electrouted and died | CEI's Report not received |  |  | LOCATION RECTIFIED | 15000
64 | HMT | Mora | Tarar Hiraben Revabhai | FA | cow | 04.08.2021 | NA | An incident was taken on the place near LT pole of 1 phase 3 wire LT line in fali opposite to mora village bus pick up stand.As per eye witness statement,Cow owner smt. Tarar Hiraben Dhulabhai had taken her two cows for grazing, while returning to her home, one cow was suddenly dragged near the pole and fall down near the pole under mud. Another cow suddenly do jump and gone away from the location, and owner also experienced shock on her feet.Accident took place approx. 3 p.m. on dt. 4.8.21 under rainy condition. When Line staff reached there, there was no leakage found near that pole and rain was also stopped. | CEI's Report not received |  |  | LOCATION RECTIFIED | 15000
65 | HMT | HATHIYA | BODAT SHAILESHBHAI MAXIBHAI | FH | OUTSIDER | 8.8.20 |  | Fatal Accident of Outsider shri Bodat Shaileshbhai Maxibhai At village Hathiya,Ta: Bhiloda Dist: Aravalli Was occurred on dtd 08.08.2021 Approx time 4:00 pm got Electric Shock Due to victim Climed on Ag transfomer centre of near by his house and touch to live transformer drop out fuse and live current passed to body and victim was falldown and died | CEI's Report not received |  |  | AWAREING PEOPLE FOR NOT DO UNAUTHORIZED WORK
66 | HMT | MOYAD NATHAJIVAS | RATHOD DHULSINH SARDARSINH | FA | buffalo | 22.8.21 |  | THE WW MOTOR OF MOYAD(NATHJIVAS )VILLAGE WAS SHORT. DUE TO THAT LEACKAGE RETURN CURRENT FLOW FROM MOTOR TO TRANSFORMER NEUTRAL WIRE AND THEN TRANSFORMER FENCING. THERE WERE ALSO WATER LOGGING BELOW THE TRANSFORMER STRUCTURE. MEANWHILE BUFFALO CAME IN CONTACT WITH THE FENCING GOT ELECTROIFIED AND DIED ON SPOT. | CEI's Report not received |  |  | LOCATION RECTIFIED | 15000
67 | HMT | Gopawada | VARSAT LALIBEN MONGHABHAI | FH | Outsider | 2.9.21 | NA | An incident was taken on the place near LT pole of 1 phase 2 wire lt line (LT ABC) near house of Varsat Monghabhai Somabhai Village :- Gopavada. Smt. Varsat Laliben Monghabhai was working in farm near her house. While working in farm, due to rain and some reason, she touched the LT pole and got contacted to earth wire of LT pole and got electrocuted and died on site. Existing LT line is L.T. A.B.C. line of 2 wire. Due to some reason L.T. A.B.C. slipped from LT Shackle insulator and get contacted with D-Clamp and insulation of L.T. A.B.C. got damaged. Earth wire is tied to D-Clamp, hence Earth wire was Live. Accident took place approx. 11.00 a.m. on dt. 02.09.2021 under rainy condition. When we visited the site with technical staff, leakage found on the earthing wire, and is now rectified after site verification. X'mer center earthing was also checked and no leakage found before and after site verification of accident place. | CEI's Report not received |  |  | LOCATION RECTIFIED
68 | HMT | Jotasan | Kher Kajalben Hagrabhai Age:13 Year | FH | Outsider | 5.9.21 | NA | While victim had tried to insert 2 wire without 2 pin plug connected to a toofan fan in her house at that time by mistake she switched on when 1 wire was inserted but another was in her hand, thus victim got electructed and victim sent to Lambadiya hospital and doctor declared victim died. The incident is occured in consumer premise so there is no any responsibility of UGVCL. | CEI's Report not received |  |  | CONSUMER AWARE FOR SAFETY & INSTALLATION OF ELCB | PRIVATE PREMISES
69 | HMT | TAJPURI | PARMAR JASIBA KATUSINH | FA | buffalo | 6.9.21 |  | During site inspection it was found that 2 Nos of Buffaloes was died below 11 KV Kundol AG line Conductors . The black burning spots was found at Conductors surface . The said 11 KV Kundol AG line was located at hilly surfaces . Also due to various monsoon & cyclone effects , One Existing PSC Pole of said line was tilted. As per the Buffaloes owner statement both Buffaloes were eating grass at that location & comes in direct contact with the live current wire & Died . | CEI's Report not received |  |  | LOCATION RECTIFIED
70 | HMT | Gajan | SANGITABEN DULESINH PARMAR | FA | buffalo | 10.9.21 |  | An incident was taken place at 200 KVA T/C of TATA service station TC behind shreeji ice factory.As per eye witness statement,Parmar Ashvinbhai amrutbhai had taken buffaloes for grazing at the open space behind Shreeji Ice factory near Gajan Toll plaza, while grazing the Buffalo of smt Sangitaben Dulesinh Parmar was got shocked and suddenly dragged near the 200 KVA transformer centre and fall down under transformer centre. | CEI's Report not received |  |  | LOCATION RECTIFIED
71 | HMT | PALLACHAR | 1.OD CHANDANIBEN HASMUKHBHAI 2. OD RINABEN HASMUKHBHAI | NFH | OUTSIDER | 11.9.21 | NA | Victim got in contacted with galvenized roof of her own house and the said galvenized roof was in contacted with broken outgoing wire after meter installation. Victim mother went to save her daughter & she also got electrocuted & the said accident occurred.As per eye witness , outgoing wire after meter installation was broken by squirrel in his (Pvt)premises. UGVCL is not responsible for this accident. After this incident family member called to 108 ambulance & take her both to nearby prantij CHC centre for preliminary treatment. | CEI's Report not received |  |  | CONSUMER AWARE FOR SAFETY & INSTALLATION OF ELCB | PRIVATE PREMISES
72 | HMT | Shinawad | RAVAL LALABHAI KALABHAI | FA | cow | 14.9.21 |  | An incident was occurred at agriculture land of Patel Vinubhai Khumabhai ,were 3 ph 4 wire AG LT line of 11KV Dariyapur AG feeder passes through agriculture land of Patel Vinubhai Khumabhai, Conductor of LT line broken due to heavy rain and wind in last night ,in early morning near broken LT line conductor cow may be contact with broken LT Line conductor at the time of grassing and got electrocuted. | CEI's Report not received |  |  | LOCATION RECTIFIED
73 | HMT | AMBABAR | 1)BHAGORA BHUPENDRABHAI SHANKARBHAI (2)BARANDA SAVJIBHAI JIVAJIBHAI | NFH | DEPT | 21.9.21 |  | On dtd. 21.09.2021 at 11:45 Am aprrox. At ambabar village at Rathod Natvarsinh Dhutarsinh AG T/C complaint during attending complaint due to return power got shocked and falled from tc structure and got injured. | CEI's Report not received |  |  | AWARING STAFF FOR WORK WITH SAFTY TOOLS SAFE & MAKE PROPER EARTHING .
74 | HMT | KATWAD | Raval Shaileshbhai Kodarbhai | FA | Goat | 25.9.21 |  | During site inspection it was found that 1 No. of Goat was died near chain link fencing of 11 KV Hapa Jgy village TC structure. As per the Goat owner statement goat was passing near the fencing and suddenly fall down & died . | CEI's Report not received |  |  | LOCATION RECTIFIED
75 | HMT | CHADARADA | CHARPOT KAMLESHBHAI RAMANBHAI | FH | OUTSIDER | 28.9.21 |  | VICTIM WAS GONE TO 'ON' AG MOTOR THROUGH FUSE BOARD AND GOT IN CONTACTED WITH BROKEN FUSE WIRE AND GOT ELECTROCUTED AND FALLEN DOWN ON GROUND AND DEAD. | CEI's Report not received |  |  | CONSUMER AWARE FOR SAFETY & INSTALLATION OF ELCB | PRIVATE PREMISES
76 | HMT | TAJPUR | PRAHLADJI FATAJI MAKWANA | FH | OUSIDER | 28.9.21 |  | Victim got in contacted with iron wire for drying clothes which was tied near his toilet.The said iron wire touched to galvenized roof of Joitabhai becharbhai chaudhry house & also galvenized roof was in contacted with broken outgoing service wire(meter out going) .Thus leakage current was passed from meter outgoing broken service to galvanized roof & then iron wire tied with the same roof. Meanwhile victim was gone for toilet & came in contacted with iron wire & said Accident occurred.UGVCL is not responsible for the said accident.& After this family member called to 108 ambulance & take him to nearby prantij CHC centre & doctor declared him died. | CEI's Report not received |  |  | CONSUMER AWARE FOR SAFETY & INSTALLATION OF ELCB | PRIVATE PREMISES
77 | MSN | Jetpur | Prajapti Vishabhai Mohanbhai | FH | O/S | 2021-04-04 | N/A | IN A FARM OF DY EX.ENG GWRDC VICTIM WORK AS AN OPRATER IN THIS WELL VICTIM WORK FOR MAINTEANACE OF PANNEL DURING SINGLE PHASE POWER OF KISHAN AG FEEDER DUE TO MAINTEANACE WORK DO FUSE OF TRANSFORMER IS ISOLATED BY VICTEIM AFTER WORK DONE OF SECONDARY SIDE (CONSUMER END WORK) OF TRANSFORMER VICTIM CLIMB ON TC STRUCTURE AND DO BINDING WORK ON SECONADRY SIDE OF DO FUSE IT SELF DURING THIS BINDING WORK VICTIME CONTACT WITH LIVE CONDUCTOR OF PRIMARY SIDE DO FUSE AND FELL DOWN FRON TC STRUCTURE AND GET DIED. | CEI's Report not received |  |  | VICTIM HIMSELF FAULTY. DUE TO HIMSELF CLIMB ON TC STRUCTURE | 50000
78 | MSN | Jashpura | Owner Of Cow Of Rabari Motibhaio Malabhai | FA | cow | 2021-05-01 | N/A | DUE TO HEAVY WIND THE BIG NEEM TREE BRANCH FALLEN ON THE 11KV LINE PASSING NEAR IT AND PSC POLE BROKENFROM BOTTOM AND WIRE CONTACT WITH THE COW TIED DOWN THE LINE AND GOT ELECTROCUTED. | CEI's Report not received |  |  | VICTIM DIED DUE TO PSC POLE BROKEN DUE TO TBIG TREE FALLEN. | 15000
79 | MSN | Mehsana | Vinodbhai Natavarbhai Modi | NFH(Elect) | O/S | 2021-05-21 | N/A | Idle damaged GTPL internet cable was crossing above 11 KV Hubtown feeder. From victim's terrace this internet cable was passing to other premises which is located opposite to victim's premises. The same internet cable was loosed and touched to the 11 KV Hubtown feeder which is passing under the internet cable. And some how victim came in contact with internet cable on his terrace and got electrocuted. | CEI's Report not received |  |  | Awareness programme done to do not cross unauthorized line above or under of UGVCL overhead Lines.
80 | MSN | Mehsana | Ankaj Rajeshbhai Rajpoot | NFH(Elect) | O/S | 2021-06-05 | N/A | At the Under constructed Box culvert Road behind Krunal Residency, The victim was going to handle the 3 meter long aluminum box pipe and accidently came in contact with lowest conductor of 11 KV line of Ramosana JGY feeder passing above the under constructed box culvert road. As the raising work was not executed due to deep excavation of both the sides of the road. The under Signed has repeatedly informed to R&B officials through phone call and also during joint visit to filled up the excavated road sides but unfortunately the excavation has not filled and the clearance of the line is reduced to about 12 feet from upper surface of box culvert. The victim immediately admitted to Civil Hospital, Mehsana and he is well conscious. | As per CEI Reporrt R&B Dept is responsible for the accident. |  | N/A | R&B Dept is responsible for the accident.
81 | MSN | Sendhal | Rabari Bachubhai Bhurabhai | FA |  | 19-06-2021 | N/A | On dated 19/06/2021, while visited accident place it has been observed that for private lighting purpose unathorized illegally hanging bulb on pole with holder and 5A Switch was found at LT 2 wire pole , which was 4 feet above from ground level and jointed with flaxible wire, Wire insulation was not properly found, which was jointed with GI wire & touched to LT pole, buffalo touch to pole and illegal flaxible live wire so, current passed and buffalo got electrocuted. | CEI's Report not received |  |  | Awareness programme done for safty in villages for removing unathorised street light | 1500
82 | MSN | Mehsana | Owner Of Cow Rabari Laxmiben Bharatbhai | FA | cow | 2021-06-18 | N/A | It was rainy a day and raining very heavyli with very high wind. Due to this one of the LT line conductor of Shitala para transformer snapped at the first span near the transformer.As it was raining heavily, the area surrounding was water logged. There was very heavy traffic for the line staff to reach the conductor snapped site.When the cow went near the sanpped conductor, she got electrocuted and died on the spot. | CEI's Report not received |  |  | Proper maintenance of line is carried out at regular interval. | 15000
83 | MSN | Ganeshpura | Owner Of 4 Nos Of Cow Shri Rabari Punjabhai Khengrabhai | FA | cow | 2021-06-22 | N/A | The said accident occurred on Dtd:22.06.2021 approximate 15:30 hrs.On DTD: 22.06.2021 LT line feeding power to patel amabhai prabhudas A1 consumer this LT line passing over jitendrabhai manibhai patel farm out of 3ph 4wire LT line top wire snapped from LT shackle insulator and fallen on ground Due to wind and damaged pole by neem tree passes in to step of psc pole and when 04nos Cow grazing in this farm and touched with fallen wire and got shocked and fatal animal accident occurred to 04 NOS Cow of Shri Rabari punjabhai khengrabhai. | Conductor broken from Shackle so it isimportant to do maintanance of LT line | To Be Carried Maintnence at Regular Time | Yes | LT Line Converted In HT Line And Damage Pole Replaced | 60000
84 | MSN | Mota Kothasana | Buffalo Of Smt. Jadeja Laxmiba Amarsinh | FA | buffalo | 2021-07-04 | N/A | The Said Accident occurred on dtd.04.07.2021 at about 10.30 AM,There was leakage current found in house wiring of chauhan Rajusinh Pruthvisinh,village-Mota Kothasana, connection no-22772/1031/2.This leakage current returnback to LT network of UGVCL company through service wire of that consumer.This leakage current reach to Transformer centre through LT network.There was water logging near transformer center.So buffalo came in contact with leakage current through water logging and fatal animal accident occured to buffalo of Smt- Jadeja Laxmiba Amarsinh. | CEI's Report not received |  |  | Requred ELCB in load side for protect leakage current | 15000
85 | MSN | Anandpura | Chaudhri Vinaben Maheshbhai | FH | O/S | 2021-07-14 | N/A | Accident occurred on dtd. 14.07.2021 at about 05.00 PM. Victim had come in touch with mono-block motor when she was working in cloth/vessel area (chokdi). Motor was on and leakage current found on motor body and got electrocution. | CEI's Report not received
86 | MSN | Bhimpur | Smt. Priyanka Harshadbhai Parmar | FH | O/S | 2021-07-18 | N/A | The Said Accident occurred on dtd.18.07.2021 at about 10.00 AM,PARMAR PRIYANKA HARSHADBHAI(DAUGHTER OF HARSHADBHAI ISWARBHAI PARMAR),AGE-11 YEAR APPROX. AFTER FILLING WATER IN POT FROM WATER TAP WHICH IS OUTSIDE OF HER HOUSE WAS GOING TO KITCHEN WHICH IS BACK SIDE OF HER HOUSE AND MAKE ELCTRIC SWITCH ON IN THE KITCHEN AND SHE FELT ELECTRIC SHOCK. AND EXPIRE ON THE WAY WHEN GOING TO HOSPITAL. | CEI's Report not received |  |  | People were educate install ELCB there premises.
87 | MSN | Motidau | Rabari Shambhubhai Nagajibhai | FA | cow | 2021-07-25 | N/A | On date 25.07.2021,there was heavy raining, water logged surrounding the area near the LT PSC POle.The insulation of yello colored insulated streetlight phase of incoming 4 core cable on PSC pole was damaged and due to heavy rain and wind the open portion of the street light phase wire came in contact with the stay clamp and hence current passed to earth through GI earthing wire. Both the cow passing nearer to the pole and came in contact with the pole and got electrocuted. | CEI's Report not received |  |  | Proper maintenance is carried out at regular interval. | 30000
88 | MSN | Dudharampura | Patel Keyurbhai Bhagvanbhai(EA) | FH | Dept. | 2021-07-26 | N/A | On date 26.07.21, as per site visit , While replacing Service cable (2 core) of Consumer as directly received complain by victim of Thakor Anupji Ravtaji Consumer Num-28409100717 on LT 2W AB Conductor Pole,on same pole the another Service connection provided to Thakor Bakaji jitaji (consumer num- 28409101793) , its Service cable Insulation was damage and may be victim came in contact with live Phase of service cable & got electric shock. Detail investigation is in progress. | CEI's Report not received |  |  | Employees are instructed to cut off power while working on line.
89 | MSN | Umri | Gamar Vaghjibhai Keshrabhai | NFH(Elect) | Dept. | 2021-07-29 | Shri R C Jadav(EA) | ON DATE 29.07.21 AT ARROUND 03.00 PM ,GAMAR VAGHJIBHAI KESHARABHAI,ELECTRCAL ASSISTANT, TO ATTENDT PF OF 11 KV KHARI AG FEEDER,HE CLIMB ON TAP POLE ,LOC NO-37 OF 11 KV KHARI AG FEEDER TO CUT TAPLINE JUMPER AND HE GOT ELECTRIC SHOCK AND FALL DONE FROM POLE. | CEI's Report not received |  |  | Cross checking done for safty tools and tackles and earthing should be compalsary before working on line.
90 | MSN | Chanasma | Makawana Jitendrakumar Maganlal - Ele. Assistant | FH(MECH) | Dept. | 2021-08-20 | 1) Shri K.I.Prajapati, Line Inspector,2) Shri A.A.Rathod, Line Man,3) Shri H.S.Thakor, Line Man 4) Shri M.V.Patel, Line Man | On date 20.08.21, as per site visit, Victim was working at Newely erected LT Line which was not Charged. Victim was stringing of LT 4C- Cable on LT 8Mtr Pole of Police Quarter -B (Old). During stringing of Cable, suddenly victim has fall down from 8-Mtr PSC Pole and fallan on CC Block and his head was striked with small parking wall. Detail investigation is in progress. | CEI's Report not received |  |  | Employees are intructed to use all safety gadgets while working on line.
91 | MSN | Ved | Buffalo Of Bharvad Sakatabhai Ganeshbhai | FA | one Buffalo and one Cow | 2021-08-31 | N/A | On Date 31.08.2021 As per site visit A 3ph 4w open LT Line from Village Transformer center, open conductor broken Between 4th and 5th psc pole and fallen on the wayof Nagalsha dargah, appox 5:30 AM shri Bharvad Sakatabhai Ganeshbhai (Owner) was went to Home from vada for milking work with one Buffalo and one Cow.When buffalo was direct touched with broken live conductor , got electrocuted and buffalo Died. | CEI's Report not received |  |  | Proper maintenance is carried out at the accidnet site.
92 | MSN | Kheralu | Owner Of Cow Rabari Govabhai Kurshibhai | FA | cow | 2021-09-01 | N/A | On date 1.9.2021 Aprox. 03.00 pm cow of shri Rabari Govabhai Kurshibhai was grazing in gochar area near by Ag land, At that time leakage current was coming out on earthing wire of AG TC because of LT shackle Insulator fired (damage). It may be possibility of Fallen lighting stroke, LT shackle insulator fired. | CEI's Report not received |  |  | Protection should be require for leakage current
93 | MSN | Sonar | Cow Of Bharvad Menaben Amarabhai | FA | cow | 2021-09-09 | N/A | As per Telephonic information given by owner A cow was died due to electric current.At that time immidiatly We visited site. We saw cow was died near PSC Pole .There is no any live conductor broken and burnt jumper has been touched with psc pole and GI wire.There was Gi wire passing through top of psc pole to bottom side up to 3rd step and rounded at this step of PSC Pole.So there was no cause found for cow got eletrocuted and died. | CEI's Report not received |  |  | Coated jumpers are provided with sufficient distance from pole and earthing wire to avoid such type of leakage current.
94 | MSN | Suraj | Owner Of Buffalo Rabari Arjanbhai Sartanbhai | FA | buffalo | 2021-09-23 | N/A | AT VILLAGE SURAJ ON KADI JOTANA ROAD AS PER EYE WITNESS ON DT 23.9.21, WHILE PASSING TOWARD TRANSFORMER CENTER OF A R PATEL HIGHSCHOOL AT VILL SURAJ A SHE BUFFALO GOT ELECTROCUTED MIGHT BE DUE TO LEAKAGE CURRENT PASSING THROUGH THE NEUTRAL EARTHING TO WET LAND. AND ACTUAL REASON IS UNDER INVESTIGATION AS POWER SUPPLY OF INFECTED TC IS DISCONNECTED. | CEI's Report not received |  |  | ACCIDENT OCCURE DUE TO SCHOOL SIDE INTERNAL WIRING FAULT AND LEAKAGE CURRENT PASSED ON THAT TC. INFORM TO CONSUMER INSTALLED ELCB, & PROPER EARTHING
95 | MSN | Memna | Cow Calf Of Raval Talashibhai Ambarambhai | FA | cow | 2021-09-27 | N/A | As per telephonic information given by owner. A cow calf was died due to electric current.At that time immidiatly visited site. A cow calf was died near Village transformer centre . At site found there is leackage current in fencing of tc structure through broken stay wire. A stay wire was broken and one side of stay wire touched with angle of transformer and other tail of stay wire with fencing . Leackage Current came out from LT network to LT stud(neutral) of transformer, Neutral earthing wire connected with LT stud(neutral) of transformer and also touched with angle of transformer, So leackege current passing from neutral earthing wire to fencing though angle of transformer and broken stay wire .While cow child-calf passing near tc structure fencing and touched the tc fencing ,So cow child-calf got eletrocuted and died. | CEI's Report not received |  |  | Broken stay wire rectified and proper maintenance is carried out.
96 | SBT | UNAVA | RAMESHBHAI MATHURBHAI RAVAL | FH | Outsider | 1.5.21 |  | PM report yet not received so it is not cleared to deside whether victim got electrical or mechanical accident while cutting tree branch and fell down from height. During site visit small tree branch was on LT line and no any evidence of electrical accident derived. | As per CEI no any evidence regarding electric shock observed on victim body. So CEI has not provided clear opinion. | NA | NA | NA
97 | SBT | UVARSAD | RABARI VASHRAMBHAI NAGJIBHAI | FA | cow | 16.5.21 |  | .In uvarsad village,Rabari vas in premises (Vada) of Shri Rabari Vashrambhai Nagjibhai .He tied his cow in vada.Near to this Premises 4 wire LT Line Of Ananteshvar Mahadev TC (Dental Jgy Feeder) is Passing.At Around 21:55 o,clock Due to heavy Wind And Rain One conductor of this LT line is broken and fall on the cow and due to electric current fatal accident occured. | AS per CEI if UGVCL had shutdown power during cyclone then such accident might be avoided | NA | NA | UGVCL at no fault | 15000
98 | SBT | KOCHARIYA | BHARVAD GOPALBHAI LAGHRABHAI | FA | buffalo | 17.5.21 |  | Due to tree fallen on LT ABC wire, pole is come in contact with GI wire of psc pole and power supply is live, same time buffalo is passing nearby broken pole and cause in contact with GI wire of psc pole and got electrocuted. | CEI's Report not received |  |  | Maintenance carried out at location of accident | 15000
99 | SBT | PIYAJ | Thakor Kanuji Bhalaji | FA | buffalo | 18.5.21 |  | Due to TAUKTE cyclone,heavy rain with wind was there .And There were 7 nos. of Buffalos passing under the line,at the same time LT conductor snapped .So 2 nos.of buffalos were directly came in contact with live current and electrocuted and died . | Victim came in contact with snapped wire and died. | CEI suggested periodical maintanance of lines to avoid such accident. | Yes | Rectification of snapped conductor done along with Line Maintanance. | 17500
100 | SBT | SAIJ | Thakor Madhuben Bhalaji | FA | buffalo | 18.5.21 |  | Due to TAUKTE cyclone,heavy rain with wind was there .When Buffalo was passing under the line,at the same time LT conductor snapped .So buffalo was directly came in contact with live current and electrocuted and died on spot. | Victim came in contact with snapped wire and died. | CEI suggested periodical maintanance of lines to avoid such accident. | Yes | Rectification of snapped conductor done along with Line Maintanance. | 15000
101 | SBT | VIRMAGAM | Unknown | FA | cow | 18.5.21 |  | At verify site ABC three phase 4 W LT conductor mount on RSJ pipudi round pole . ABC insulation was puncture and heavy wind and cyclone hence leakage current flow through pipudi round Pole and contact to one white cow and died and another red cow touch white cow also died. | CEI's Report not received |  |  | Power leakage removed and Maintenance carried out at location of accident
102 | SBT | SANAND | 1. MANJUBEN RAMBHAI CHUNARA 2. VISHNUBHAI RAMBHAI CHUNARA | FH | Outsider | 18.5.21 |  | Nr Navjivan Doctor house lift outside roof fallen on 3 ph 5 wire it line due to heavy wind. It cause 1 nos. lt conductor damaged & fallen on ground area where already water logging. Victim walk besides Navjivan Doctor house & got electrocuted immediately his sister walk behind her brother @ she also electrocuted. | CEI's Report not received |  |  | Maintenance carried out at location of accident | 100000
103 | SBT | KATHWADA | SAURABHBHAI BALDEVBHAI RABARI | FA | buffalo | 18.5.21 |  | As per message received on 18.05.2021about at 9.30 am, so due to present situation of cyclone effect with heavy wind and rain the DO fuse made off this transformer . Whole day due to cyclonic effect with heavy wind and rain site was visited on 19.05.2021, DOfuse made on and check no leakage current was on there fencing , neutral and earthing . No cause was found for fatal accident . | CEI's Report not received |  |  | No leakage current onserved during site visit. As per PM cow died due to electric shock. So payment proceedure was carried out as per UGVCL norms. | 15000
104 | SBT | KOLAVADA | SHARDABEN KANJIBHAI THAKOR | FA | buffalo | 18.5.21 |  | Due to 440V LT conductor broken from pole & live outgoing wire touched the buffalo and electrocuted | CEI's Report not received |  |  | Maintenance carried out at location of accident
105 | SBT | SANSOLI | 1. FH-Ratilal Hukabhai Parmar 2. FH-Kokilaben Ratilal Parmar 3. NFH-Sonalben Ratilal Parmar | FH-NFH | Outsider | 20.5.21 |  | There is no connection of UGVCL in his house, they take unauthorised power supply from near house , in his house no proper wiring that wire touch with iron wire contact with both husband and wife both died. | CEI's Report not received |  |  | NA
106 | SBT | Aslali | Chaudhary Vishnubhai Hirabhai (EA, Mehsana City S/dn. | NFH | Dept | 21.5.21 |  | while the cyclone damage work was going on at Bhagvan estate, the PSC pole next to victim suddenly broke and the pole fell directly on the victim standing below,hitting the victim in the leg. | CEI's Report not received |  |  | NO anyone's fault
107 | SBT | VASAI | Narendrasinh Prabhatsinh Chauhan | FA | buffalo | 28.5.21 |  | On 28.5.21, 11 kv Mahijada Ag feeder TC one of the phase conductor was snapped and laying on ground, buffalo while grazing near came in direct contact with live wire and got electrocuted and died on the spot. | CEI's Report not received |  |  | Maintenance carried out at location of accident | 15000
108 | SBT | SHILAJ | Kishorsing Dipsing Ravat | NFH | Outsider | 31.5.21 |  | Victim unconsciously (mental disorder as per division office reporting) climb on transformer center and got non fatal electrical accident. | CEI's Report not received |  |  | NA
109 | SBT | NARODA | Bharvad Vihabhai Ramabhai | FA | cow | 19.5.21 (Reported on 4.6.21) |  | Cow was passing below LT line of Gnadhinagar area and due to cyclone at that time conductor snapping of LT line 3 ph 4w open LT line top conductor and might have come into contact with broken LT wire of LT line and may have got electrocuted . | CEI's Report not received |  |  | Maintenance carried out at location of accident
110 | SBT | VALAD | Sanjaybhai Jasubhai Dantani | FH | Outsider | 2.4.21 (Reported on 3.6.21) |  | Victim had surrounded the boundary of his survey land with GI wire, which was at the time of incident connected to "Zatka Machine". Meanwhile when the M/c was on, victim was trying to get outside of GI wired fencing and thus got electrocuted and died on spot. as per panchnama No nearby electric line passing. | As per CEI only fencing to be provided surrounding the farm. | No any kind of electric machine to be utilized. | NA | UGVCL at no fault
111 | SBT | Hirapur | Jivabhai Varsangbhai Makwana | FA | buffalo | 5.6.21 |  | While buffalo passing from near to transformer center closer to the expose of electrical connection of load side get in touch with wire and got electrocuted and died. | CEI's Report not received |  |  | NA
112 | SBT | Nandej | 1. NFH-Hiteshbhai Vishnubhai Patel (E.A.) 2. NFH-Dignesh Prahladbhai Parmar (E.A.) | NFH | Dept | 9.6.21 |  | Eventhough all relevant line switches cut off including 11 KV DO removed on TC but due to beehive of koder presence in LT distribution box, LT fuse was not cut off. Thenafter when victims were working on that TC return momentary return power came from railway station side. after this incident observed that power of few lights and fans were on at railway station. with having auto shifting arrengement when UGVCL power goes off. All relevant 1 phase and 3 phase meters of LT circuits of that TC, MRI data taken but return power was observed only in railway circuit side meter. | CEI's Report not received |  |  | Vide letter no.UGVCl/SBTDO/Tech-2/6691 dtd.15.7.2021, Railway department was asked to investiget regarding cause of return power.
113 | SBT | JETALPUR | Arvindbhai Mansingbhai Damor (ALM) | NFH | Dept | 11.6.21 |  | WHILE CT OPERATED CHECKING PROGRAM, DURING WIRING OF ACCUCHECK WIRING, 2 PHASE GOT SHORTED IN MAIN SWITCH ACCIDENTALLY AND DUE TO ARC FLASHOVER VICTIM SUFFERED THE BURNS IN RIGHT HAND PALM AND FOREHEAD AND IMMEDIATELY VICTIM WAS SHIFTED TO RUDRAKSH HOSPITAL AT BAREJA. | CEI's Report not received |  |  | Vide letter no. UGVCL/SBTCO/9573 dtd.11.10.2021, all divisions are asked to purchase face shild and compulsory utilizing during CT meter checking.
114 | SBT | ZAK | KULDIPSINH DHIRUSINH VAGHELA | FH | Outsider | 11.6.21 |  | Illegal construction of first floor roof with 11 KV HT pole in the premises, resulting the distance of nearest HT conductor to the floor is only 1.4 meter and the victim himself comes in contact with the live HT wire for doing his work on the first floor open roof. | CEI's Report not received |  |  | Notice issue vide letter no.UGVCL/Dahegam R/Tech/1360 dtd.14.6.2021 for registering application for line shifting at office. | 50000
115 | SBT | Gundi | Rathod Khimjibhai Shivabhai | FH | Outsider | 12.6.21 |  | Sarthak org Pvt ltd contractor and labour carried out work of Pvt earthing by manually drilling machine in factory premises near transformer & after work completed they come to under tc structure where iron pipe (long drill machine) touched to ht bushing of transformer on right side of conductor and therefore accident occurred. | CEI's Report not received |  |  | NA | 50000
116 | SBT | Mahijada | P.K.DHUSA (E.A) | NFH | Dept | 15.6.21 |  | While attending the feeder PF of 11 KV Mahijada Ag fdr, fault of jumper was traced and the same jumper was rectified by the victim and while just stepping down from the transformer t.c, sudden arc flashover was observed, due to which right hand and right elbow of the victim suffered electric burns and also fell down on the ground. | CEI's Report not received |  |  | Instruction given to take care while working with the line.
117 | SBT | Sanand | Raval Ranchhodbhai Khodabhai | FH | Outsider | 19.6.21 |  | Raval Ranchhodbhai's 2 nos Goat walk near LT pole & touched energised stay wire & got electrocuted. Immediately its owner late Shri Raval Ranchhodbhai tried to remove their both goat he is also electrocuted. | CEI's Report not received |  |  | Maintenance carried out at location of accident | 50000
118 | SBT | Sanand | Raval Ranchhodbhai Khodabhai | FA | Goat | 19.6.21 |  | Raval Ranchhodbhai's 2 nos Goat walk near LT pole & touched energised stay wire & got electrocuted. | CEI's Report not received |  |  | Maintenance carried out at location of accident | 3000
119 | SBT | Ghamij | Valmiki Nareshbhai Dineshbhai | FH | Outsider | 23.6.21 |  | Actual reason of accident is not decided .NO leakage found | CEI's Report not received |  |  | NA
120 | SBT | Bakrol | Shaileshbhai Jesingbhai Chunara | FH | Outsider | 27.6.21 |  | Victim himself climbed on Ex HT line pole of 11 KV bhavda Ag feeder and touch the 11 KV conductor and got electrocuted. | CEI's Report not received |  |  | NA
121 | SBT | Daduka | Hanubhai Babubhai Dodiya | FA | buffalo | 28.6.21 |  | While buffalo passing from AB switch double pole structure the horns of the buffalo stucked into the guy wire which came into contact with live wire of AB switch jumper, buffalo got electrocuted and died. | CEI's Report not received |  |  | Maintenance carried out at location of accident | 15000
122 | SBT | Shahpur | Butabhai Meghabhai Bharwad | FA | buffalo | 29.6.21 |  | Baffalo was passing on the road and might have come into contact with broken LT wire and may got electrocuted and died on the spot. | CEI's Report not received |  |  | Maintenance carried out at location of accident | 15000
123 | SBT | Nanodara | Ko.Patel Jivanbhai Nathabhai | FA | buffalo | 26.5.21 |  | Due to 11 KV Kavla Ag feeder LT line R phase conductor broken and fallen on buffalo and baby buffalo and they got electrocuted. | CEI's Report not received |  |  | Maintenance carried out at location of accident | 16500
124 | SBT | Ranesar | Dilipbhai Babubhai Pargi | FH | Outsider | 1.7.21 |  | Victim had come to do his daily watering work on 1.7.21 at 7.45 A.M. He was carrying 15 amp switch plug board and a live wire with more joints in his hand to turn on electric motor when his left hand was in contact with more jointed wire and was electrocuted. Unfortunately the protective electric device installed at customer place did not work and this caused an electric accident and there after their power supply is cut off with immediate effect. | CEI's Report not received |  |  | NA
125 | SBT | Vanzar | Bharvad Sureshbhai Mahadevbhai | FA | buffalo | 3.7.21 |  | Buffalo was moving around AB switch pole and came in contact with stay wire, stay wire got broken and pilled along with buffalo and came in contact with the live wire of HT of AB switch jumper and got electrocuted and died. | CEI's Report not received |  |  | Maintenance carried out at location of accident | 15000
126 | SBT | Chandkheda | Amarsinhbhai Dharamsinhbhai Rabari | FA | cow | 12.7.21 |  | On dt.12.07.2021 at approximately 8:30 hrs an electrical accident took place in Ashvamegh society with a TC of 200 KVA Cap. It was a fatal accident of COW owned by shri Amrutbhai Dharmashibhai Rabari.Accident site had a LT UG network MSP between house no. B-64 and B-65 , a cow was passing through road to a pit like vessel placed near to MSP for eating food,due to rainy condition and water logging near to MSP some leakage current passed through ground and thus got electrocuted and died.As per circular and party consent for LT UG Network all work of wiring ,earthing and accident prevention is to be maintained by party. | CEI's Report not received |  |  | NA
127 | SBT | Kasipura | Rameshbhai Melebhai Zala | NFH | Outsider | 15.7.21 |  | Victim himself climbed on temple tarrace for adjusting the santing plate for construction and their victim came in contact with 11 KV conductor and got electrocuted. | CEI's Report not received |  |  | NA
128 | SBT | Bhayla | Kanubhai Rupabhai Vagat | NFH | Dept | 21.7.21 |  | While climbing on PSC pole victim lost his grip from pole and fell down from a height of 8 to 10 feet and got mechanical accoident | CEI's Report not received |  |  | Mechanical accident. Instructed to observed the location before starting of work.
129 | SBT | Bavla | Ketulbhai Babubhai Gajjar (E.A. Emp. No.13009) | NFH | Dept | 22.7.21 |  | He was climbing LT 8mtr psc pole in Amrish society to solve LT complaint, pole was very old and it had a stay as soon as he reached middle of pole, pole broke from bottom and he jumped down due to fear and injured his left ankle. | CEI's Report not received |  |  | Mechanical accident. Instructed to observed the location before starting of work.
130 | SBT | Bavla | Vijaybhai Dwarkadas | FH | Outsider | 24.7.21 |  | Victim came in contact with fencing of TC from which lickage current was passing. Reason for lickage current is contact of fencing with LT distribution box due to nearby house debris fallen at TC location. | CEI's Report not received |  |  | Maintenance carried out at location of accident | 50000
131 | SBT | Dhamatwan | Chandkhan Safikhan | FH | Outsider | 29.8.21 |  | Victim himself stand on loaded truck and talking on phone at that time he wiped plastic cover(tadpatri) and plastic cover (tadpatria) contact with live conductor of 11 kv Radhe Jgy feeder, victim got electrocted and died | CEI's Report not received |  |  | NA
132 | SBT | Mahadevpura | Chauhan Amjubhai Popatbhai | FA | cow | 6.9.21 |  | Cow passing through Kanani vas where LT ABC (deteriorated) wire at pole no 6 from Kananivas broken and down on earth at that time cow passing through seri (road) the conductor come in contact with cow lag and cow fatal on site. | CEI's Report not received |  |  | Maintenance carried out at location of accident
133 | SBT | Vishalpur | Azad Alam Shakilbhai Ansari | FH | Outsider | 6.9.21 |  | There was a leakage current on the compressor motor and so it was spreaded over on the compressor, when the victim came in contact with the iron cage of compressor he got shocked and electrocuted. | CEI's Report not received |  |  | NA
134 | SBT | Khoraj | Devipujak Fulabhai Chhanabhai | FA | buffalo | 8.9.21 |  | The buffalow passing near through transformer structure, due to electric shock , due to any accidental cause of entangling the earthing wire coming down from the structureof the transformer , buffalo was electrocted and died | CEI's Report not received |  |  | Maintenance carried out at location of accident
135 | SBT | Bakrol-Bajrang | Arvindbhai Rameshbhai Mina | FH | Outsider | 8.9.21 |  | Victim was working on construction site, he was opening wooden shuttering with an iron rod and during that iron rod might have touched to 11 kv Swagat JGY conductor and got electrocuted and fall down. | CEI's Report not received |  |  | NA
136 | SBT | Dashela | Rabari Ishvarbhai Varvabhai | FA | cows | 8.9.21 |  | Live neutral wire broken from LT pole and fall on ground, while two cows passing near by this broken conductor she came directly contact with neutral wire and leakage return current passing through cows body to earth by reason she got electrocuted and died on the spot | CEI's Report not received |  |  | Maintenance carried out at location of accident | 30000
137 | SBT | Moti Jok | Rameshbhai Karsanbhai Mundhava | FA | cow | 9.9.21 |  | Owner and cow passing through the road and touched girder pole where this accident happened. The accident happened due to LT ABC wire deteriated (city-1 feeder) and touched near by existing girder pole, as girder pole slightly move towards LT line due to rain and girder get potentially charge and as cow touched with gider get shocked. | CEI's Report not received |  |  | Maintenance carried out at location of accident | 15000
138 | SBT | Rajoda | Gohil Anandiben Dilipsinh | FA | 4 nos. buffalo | 15.9.21 |  | Due to land slide near the lake, the neem tree fell into the lake along with the LT pole, due to the friction of the tree with the ABC conductor the insulation of ABC lT line got demaged, which caused the power to descend into the GI wire of the earthing of LT pole and the power spread throughout the water of the lake. Four nos of buffalos died of electrocution while drinking water from the lake. | CEI's Report not received |  |  | Maintenance carried out at location of accident | 60000
139 | SBT | Kolwada | Mittalben Umangbhai Prajapati | FH | Outsider | 16.9.21 |  | Due to internal wiring short circuit, victim got electric shock and died. | CEI's Report not received |  |  | NA
140 | SBT | Dholka | Vijaybhai Hathibhai Dindore | FH | Outsider | 18.9.21 |  | Hathibhai Sanabhai Dindore and victim Vijaybhai Hathibhai Dindore came at Dholka with concrete mixer truck where work for RCC road is in progress. They park vehicle below 11 KV HT line of Balram urban feeder and Vijaybhai climbed on the vehicle for cleaning. During that his hand came in contact with HT line and got electrocuted and died. | CEI's Report not received |  |  | NA
141 | SBT | Kotada | Mevada Ranchhodbhai Gobarbhai | FA | buffalo | 18.9.21 |  | Buffalo was passing through pothiyadada vistar, Kotda where buffalow rub its head with TC structure pole while earthing wire stuck with its horns and got electrocuted | CEI's Report not received |  |  | Maintenance carried out at location of accident | 15000
142 | SBT | Nandej | Udesinh Chehusiinh Darbar | FA | buffalo | 19.9.21 |  | Due to the failure of change over switch (wire was failed and got shot at party side, so return power was coming from DG set (tower connection) on earthing and buffalo was roaming nearby and got electrocuted and died. | CEI's Report not received |  |  | Maintenance carried out at location of accident
143 | SBT | Randheja | Devrajbhai Somabhai Rabari | FA | cow | 22.9.21 |  | Pole and conductor was broken and fallen on Cow passing there, So got electroducted and died. | CEI's Report not received |  |  | Maintenance carried out at location of accident
144 | SBT | Adalaj | Damor Navinbhai Ramanbhai | NFH | Dept | 28.9.21 |  | During checking CT connection given, PT of accuchek meter one phase during PT connection consumer's TPN switch connector comes out with live phase and touch to the near phase. So phase to phase spark creat and flame comes due to flame and spark Shri Navinbhai Damor , EA burnt on mouth, chest, shoulders and hands. | CEI's Report not received |  |  | Vide letter no. UGVCL/SBTCO/9573 dtd.11.10.2021, all divisions are asked to purchase face shild and compulsory utilizing during CT meter checking.
145 | SBT | Nilki | Waghela Rajeshbhai Meghabhai | NFH | Outsider | 30.9.21 |  | As victim was working with fitting work of tiles of Marvadi Samaj mandir at Vill. Nilki was seeing his tiles work after completion and came back towards terrace of Thakor Bhopabhai babubhai where existing 11 kv Trent ag was passing and touched the line and got electrocuted. | CEI's Report not received |  |  | NA
146 | SBT | Sarsavadi | Chauhan Kuldeepsinh Navalsinh | NFH | Outsider | 30.9.21 |  | As victim was mentally unstable and he came in the morning near Sarsavadi WW TC which is feeding power supply by 11 kv Ashoknagar JGY feeder and he climbed on that live TC and touched the HT side jumper and gor electrocuted. | CEI's Report not received |  |  | NA

## SoP 003
Uttar Gujarat Vij Company Limited
QUARTER :- 2nd (July- 21 to Sept. - 21)
Performa SoP 003 B:
APPENDIX - B
REGISTER FOR COMPILING THE COMPLAINTS CLASSIFICATION WISE
Classification | Pending complaint of previous quarter | Complaints received during the quarter | Total complaints | No.of complaints redressed during the month |  |  |  |  | Balance complaints to be redressed (4) - (9) | Classification of complaint
|  |  |  | In stipulated time |  | Beyond stipulated time |  | Total (5) to (8)
|  |  |  | Within 50% of stipulated time | Within stipulated time | Upto double the stipulated time | More than double the stipulated time
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11
A(i) | 0 | 34712 | 34712 | 27629 | 7078 | 5 | 0 | 34712 | 0 | Loose conn. from pole
A(ii) | 0 | 17462 | 17462 | 15008 | 2450 | 4 | 0 | 17462 | 0 | Int.due to line breakdown
A(iii) | 0 | 4905 | 4905 | 3251 | 1654 | 0 | 0 | 4905 | 0 | Interruption due to failure of transformer
B(i) | 0 | 975 | 975 | 708 | 267 | 0 | 0 | 975 | 0 | Ordinary case, which requires no augmentation
B(ii) | 0 | 761 | 761 | 571 | 190 | 0 | 0 | 761 | 0 | Where augmentation is required
C(i) | 0 | 6244 | 6244 | 4488 | 1756 | 0 | 0 | 6244 | 0 | Stopped/Defective Meters
C(ii) | 0 | 2552 | 2552 | 1954 | 598 | 0 | 0 | 2552 | 0 | Billing on average basis for more than two bills
D(i) | 0 | 3852 | 3852 | 2797 | 1055 | 0 | 0 | 3852 | 0 | Loose Wires
D(ii) | 0 | 864 | 864 | 673 | 191 | 0 | 0 | 864 | 0 | Inadequate ground clearance
E(i) | 0 | 960 | 960 | 688 | 272 | 0 | 0 | 960 | 0 | For current bills where no additional information is required
E(ii) | 0 | 1244 | 1244 | 816 | 428 | 0 | 0 | 1244 | 0 | Where additional information relating to correctness of reading etc. is required
F(i) | 0 | 693 | 693 | 437 | 256 | 0 | 0 | 693 | 0 | Where extension of mains is not required
F(ii) | 0 | 411 | 411 | 302 | 109 | 0 | 0 | 411 | 0 | Where extension of mains is required
F(iii) | 0 | 1237 | 1237 | 934 | 303 | 0 | 0 | 1237 | 0 | Modification in connected load
F(iv) | 0 | 1629 | 1629 | 1141 | 488 | 0 | 0 | 1629 | 0 | Name change/reconnection
G | 0 | 372 | 372 | 245 | 127 | 0 | 0 | 372 | 0 | Refund of amount due in regard to temporary connection
H | 0 | 9118 | 9118 | 7008 | 2110 | 0 | 0 | 9118 | 0 | Others
Total | 0 | 87991 | 87991 | 68650 | 19332 | 9 | 0 | 87991 | 0

## SoP 004
Uttar Gujarat Vij Company Limited
QUARTER :- 2nd (July - 21 to Sept.- 21)
Performa SoP 004
Sr. No. | Actions or steps carried out by UGVCL towards public awareness in the quarter | Likely number of consumers influenced | Details about media
1 | Display board of SOP at circle, Division & S/Dn | 253334 | Notice Board
2 | Display board of Name of information officers under RTI Act 2005 at Circle,Division,Sub- division offices. | 258854 | Notice Board
3 | Consumer care centers at various places | 230730 | Verbal & Notice Board at CCC
4 | Advertisement through Daily News papers | 118458 | Daily News papers
5 | Pamphlets distributed among public | 213223 | Pamphlets
6 | Advertisement through slide in TV / Banners | 176241 | T V Channels
7 | On Web site of Uttar Gujarat Vij Company Limited | 218169 | Internet
8 | Through Regular Energy Bills | 3372785 | Energy Bill
9 | Others | 8447 | CD

## SoP 005
Uttar Gujarat Vij Company Limited
QUARTER :- 2nd (July - 21 to Sept.- 21)
YEAR :-2021-22
Performa SoP 005 B: Action taken report by the Redressal Committee
Sr. No. | Month | Date and time meeting conducted | No. of complaints registered at the meeting | No. of complaints pending at the end of the meeting | Nos of cases Disposed | Location of Hearing
1 | July.21 | 03.07.2021 | 4 | 0 | 4 | Circle office Sabarmati
|  | 09.07.2021 | 4 | 2 | 2 | Circle office Sabarmati
|  | 17.07.2021 | 3 | 1 | 2 | Circle office Sabarmati
|  | 23.07.2021 | 4 | 1 | 3 | Circle office Sabarmati
2 | Aug.21 | 07.08.2021 | 4 | 2 | 2 | Circle office Sabarmati
|  | 10.08.2021 | 3 | 1 | 2 | Corporate Office, Mehsana
|  | 13.08.2021 | 3 | 3 | 0 | Circle office Sabarmati
|  | 21.08.2021 | 3 | 1 | 2 | Circle office Sabarmati
|  | 26.08.2021 | 1 | 0 | 1 | Corporate Office, Mehsana
|  | 27.08.2021 | 4 | 3 | 1 | Circle office Sabarmati
3 | Sept.21 | 08.09.2021 | 6 | 2 | 4 | Circle office Sabarmati
|  | 17.09.2021 | 4 | 0 | 4 | Circle office Sabarmati
|  | 24.09.2021 | 4 | 4 | 0 | Circle office Sabarmati

## SoP 006
Uttar Gujarat Vij Company Limited
QUARTER :- 2nd (July- 21 to Sept.- 21)
Performa SoP 006 : Failure of Distribution Transformer.
Sr. No. | Class | No. of existing Distribution transformer at the start of the quarter | No.of Distribution transformers added during the quarter | Total number of Distribution transformers | Total number of Distribution transformer failed during the quarter | % failure rate of Distribution transformer
|  | A | B | C=A+B | D | H= (D) * 100/C
1 | 11KV | 345887 | 3606 | 349493 | 9465 | 2.7082
Total |  | 345887 | 3606 | 349493 | 9465 | 2.7082

## SOP011-(AG)
Uttar Gujarat Vij Company Limited
QUARTER :- 2nd (July-21 to Sept.-21)
YEAR :-2021-22
SoP 011 - A : System Average Interruption Frequency Index (SAIFI) for AG. Dominant Category
Sr. No | Month | Ni - Number of Customers for each sustained interruptions (in numbers) | NT - Total No of customers served (in Numbers) | CI=∑ Ni | SAIFI = ∑ Ni/Nt (Monthly SAIFI)
1 | 2 | 3 | 4 | 5 | 6=5/4
1 | 2021-07-01 | 517506 | 589668 | 2612429 | 4.4303
2 | 2021-08-01 | 478408 | 591408 | 2026691 | 3.4269
3 | 2021-09-01 | 525999 | 593283 | 2989243 | 5.0385
SoP 011 - B : System Average Interruption Duration Index (SAIDI) for AG. Dominant Category
Sr. No | Month | Ri = Restoration Time for each sustained interruption event (in hours) | Ni - Number of interrupted Customers for each sustained interruption event (in numbers) | Ri* Ni - Total customer interruption Duration | NT - Total No of customers served (in Numbers) | Customer Intt. Duration CMI = ΣRi*Ni | SAIDI = ΣRi*Ni/Nt (Monthly SAIDI)
1 | 2 | 3 | 4 | 5 = 3 * 4 | 6 | 7 | 8=7/6
1 | 2021-07-01 | 1902-02-09 17:00 | 517506 |  | 589668 | 2352-06-29 04:42 | 0.28028
2 | 2021-08-01 | 1901-07-18 03:46 | 478408 |  | 591408 | 2228-05-16 06:08 | 0.2028
3 | 2021-09-01 | 1902-05-11 23:43 | 525999 |  | 593283 | 2408-08-15 17:48 | 0.31313
SoP 011 - C : Momentary Average Interruption Frequency Index (MAIFI) for AG. Dominant Category
Sr. No | Month | IMi = Number of Momentary interruptions for the month (in numbers) | Nmi = Total no of customers for each momentary interruptions (in numbers) | Imi =Nmi Number of customer Momentary interruptions (in numbers) | Nt - Total no of customers served (in numbers) | Customer Intt. ΣImi*Nmi | MAIFI=ΣImi*Nmi/Nt
1 | 2 | 3 | 4 | 5 = 3 * 4 | 6 | 7 | 8=7/6
1 | 2021-07-01 | 16647 | 554527 |  | 589668 | 3966605 | 6.7268
2 | 2021-08-01 | 15213 | 548301 |  | 591408 | 3578307 | 6.0505
3 | 2021-09-01 | 19397 | 561012 |  | 593283 | 4595162 | 7.7453

## SOP011-(JGY)
Uttar Gujarat Vij Company Limited
QUARTER :- 2nd (July-21 to Sept.-21)
YEAR :-2021-22
SoP 011 - A : System Average Interruption Frequency Index (SAIFI) for JGY category
Sr. No | Month | Ni - Number of Customers for each sustained interruptions (in numbers) | NT - Total No of customers served (in Numbers) | CI=∑ Ni | SAIFI = ∑ Ni/Nt (Monthly SAIFI)
1 | 2 | 3 | 4 | 5 | 6=5/4
1 | 2021-07-01 | 1870047 | 2149941 | 7172242 | 3.336
2 | 2021-08-01 | 1713434 | 2156361 | 5090931 | 2.3609
3 | 2021-09-01 | 1950538 | 2162565 | 9513826 | 4.3993
SoP 011 - B : System Average Interruption Duration Index (SAIDI) for JGY category
Sr. No | Month | Ri = Restoration Time for each sustained interruption event (in hours) | Ni - Number of interrupted Customers for each sustained interruption event (in numbers) | Ri* Ni - Total customer interruption Duration | NT - Total No of customers served (in Numbers) | Customer Intt. Duration CMI = ΣRi*Ni | SAIDI = ΣRi*Ni/Nt (Monthly SAIDI)
1 | 2 | 3 | 4 | 5 = 3 * 4 | 6 | 7 | 8=7/6
1 | 2021-07-01 | 1900-06-10 16:02 | 1870047 |  | 2149941 | 334191 | 0.15544
2 | 2021-08-01 | 1900-04-19 21:07 | 1713434 |  | 2156361 | 238894.1125 | 0.11079
3 | 2021-09-01 | 1900-07-08 13:46 | 1950538 |  | 2162565 | 406828.2472 | 0.18812
SoP 011 - C : Momentary Average Interruption Frequency Index (MAIFI) for JGY category
Sr. No | Month | IMi = Number of Momentary interruptions for the month (in numbers) | Nmi = Total no of customers for each momentary interruptions (in numbers) | Imi =Nmi Number of customer Momentary interruptions (in numbers) | Nt - Total no of customers served (in numbers) | Customer Intt. ΣImi*Nmi | MAIFI=ΣImi*Nmi/Nt
1 | 2 | 3 | 4 | 5 = 3 * 4 | 6 | 7 | 8=7/6
1 | 2021-07-01 | 6990 | 2066650 |  | 2149941 | 16667836 | 7.7527
2 | 2021-08-01 | 5908 | 2056539 |  | 2156361 | 14365233 | 6.6618
3 | 2021-09-01 | 7943 | 2085453 |  | 2162565 | 19380499 | 8.9618

## SOP011-(OTHER THAN AG-JGY)
Uttar Gujarat Vij Company Limited
QUARTER :- 2nd (July-21 to Sept.-21)
YEAR :-2021-22
SoP 011 - A : System Average Interruption Frequency Index (SAIFI) for Other than AG & JGY category
Sr. No | Month | Ni - Number of Customers for each sustained interruptions (in numbers) | NT - Total No of customers served (in Numbers) | CI=∑ Ni | SAIFI = ∑ Ni/Nt (Monthly SAIFI)
1 | 2 | 3 | 4 | 5 | 6=5/4
1 | 2021-07-01 | 844336 | 1148741 | 2812498 | 2.4483
2 | 2021-08-01 | 746011 | 1150151 | 2173455 | 1.8897
3 | 2021-09-01 | 860390 | 1151654 | 3221533 | 2.7973
SoP 011 - B : System Average Interruption Duration Index (SAIDI) for Other than AG & JGY category
Sr. No | Month | Ri = Restoration Time for each sustained interruption event (in hours) | Ni - Number of interrupted Customers for each sustained interruption event (in numbers) | Ri* Ni - Total customer interruption Duration | NT - Total No of customers served (in Numbers) | Customer Intt. Duration CMI = ΣRi*Ni | SAIDI = ΣRi*Ni/Nt (Monthly SAIDI)
1 | 2 | 3 | 4 | 5 = 3 * 4 | 6 | 7 | 8=7/6
1 | 2021-07-01 | 1900-04-22 23:41 | 844336 |  | 1148741 | 2205-10-28 17:43 | 2:20
2 | 2021-08-01 | 1900-03-20 21:25 | 746011 |  | 1150151 | 2098-07-17 16:45 | 1:31
3 | 2021-09-01 | 1900-05-05 22:04 | 860390 |  | 1151654 | 2204-05-03 06:50 | 2:19
SoP 011 - C : Momentary Average Interruption Frequency Index (MAIFI) for Other than AG & JGY category
Sr. No | Month | IMi = Number of Momentary interruptions for the month (in numbers) | Nmi = Total no of customers for each momentary interruptions (in numbers) | Imi =Nmi Number of customer Momentary interruptions (in numbers) | Nt - Total no of customers served (in numbers) | Customer Intt. ΣImi*Nmi | MAIFI=ΣImi*Nmi/Nt
1 | 2 | 3 | 4 | 5 = 3 * 4 | 6 | 7 | 8=7/6
1 | 2021-07-01 | 2656 | 925988 |  | 1148741 | 4434578 | 3.8604
2 | 2021-08-01 | 2221 | 948040 |  | 1150151 | 3618714 | 3.1463
3 | 2021-09-01 | 2564 | 939087 |  | 1151654 | 4073162 | 3.5368

## SOP011-(OVERALL)
Uttar Gujarat Vij Company Limited
QUARTER :- 2nd (July-21 to Sept.-21)
YEAR :-2021-22
SoP 011 - A : System Average Interruption Frequency Index (SAIFI) for UGVCL as a whole
Sr. No | Month | Ni - Number of Customers for each sustained interruptions (in numbers) | NT - Total No of customers served (in Numbers) | CI=∑ Ni | SAIFI = ∑ Ni/Nt (Monthly SAIFI)
1 | 2 | 3 | 4 | 5 | 6=5/4
1 | 2021-07-01 | 3231889 | 3888350 | 12597169 | 3.2397
2 | 2021-08-01 | 2937853 | 3897920 | 9291077 | 2.3836
3 | 2021-09-01 | 3336927 | 3907502 | 15724602 | 4.0242
SoP 011 - B : System Average Interruption Duration Index (SAIDI) for UGVCL as a whole
Sr. No | Month | Ri = Restoration Time for each sustained interruption event (in hours) | Ni - Number of interrupted Customers for each sustained interruption event (in numbers) | Ri* Ni - Total customer interruption Duration | NT - Total No of customers served (in Numbers) | Customer Intt. Duration CMI = ΣRi*Ni | SAIDI = ΣRi*Ni/Nt (Monthly SAIDI)
1 | 2 | 3 | 4 | 5 = 3 * 4 | 6 | 7 | 8=7/6
1 | 2021-07-01 | 1902-11-13 08:43 | 3231889 |  | 3888350 | 611163.934 | 3:46
2 | 2021-08-01 | 1902-01-25 22:18 | 2937853 |  | 3897920 | 431350.066 | 2:39
3 | 2021-09-01 | 1903-03-25 11:33 | 3336927 |  | 3907502 | 703759.2736 | 4:19
SoP 011 - C : Momentary Average Interruption Frequency Index (MAIFI) for UGVCL as a whole
Sr. No | Month | IMi = Number of Momentary interruptions for the month (in numbers) | Nmi = Total no of customers for each momentary interruptions (in numbers) | Imi =Nmi Number of customer Momentary interruptions (in numbers) | Nt - Total no of customers served (in numbers) | Customer Intt. ΣImi*Nmi | MAIFI=ΣImi*Nmi/Nt
1 | 2 | 3 | 4 | 5 = 3 * 4 | 6 | 7 | 8=7/6
1 | 2021-07-01 | 26293 | 3547165 |  | 3888350 | 25069019 | 6.4472
2 | 2021-08-01 | 23342 | 3552880 |  | 3897920 | 21562254 | 5.5317
3 | 2021-09-01 | 29904 | 3585552 |  | 3907502 | 28048823 | 7.1782

## SoP 012
Uttar Gujarat Vij Company Limited
Year 2021-22 (April - 21 to Sept. - 21)
Performance SoP 012 - System Losses at EHT / 11 KV and below
SoP 012 - CALCULATION OF SYSTEM LOSSES AT EHT / 11 KV
Losses in 11 KV System and Connected Equipment
i | Energy Delivered into EHT / 11 KV and LT Distribution System from EHT / 11 KV SS (Mus) | A | 13571.3914
ii | Energy Sold (Billed) EHT direct sales (Mus) | B | 1418.4179
iii | Energy Sold (Billed) in the 11 KV LT system (Mus) | C | 11002.2135
iv | Total Sales (Mus) | (B+C) | 12420.6314
v | Losses (Mus) | {(A) - (B+C)} | 1150.76
vi | % Losses | {(A) - (B+C)} X 100 / (A) | 8.4793

## SoP013
Uttar Gujarat Vij Company Limited
QUARTER :- 2nd (July - 21 to Sept.- 21)
Performa SoP 013 : Meter faults
Consumer Category | No. of faulty meters at the start of the quarter | No. of faulty meters added during the quarter | Total No. of defective / faulty meter | No. of faulty Meters repaired and replaced | No. of faulty meters pending at the end of the quarter
| 1 | 2 | 3=2+1 | 4 | 5=3-4
Single Phase | 3840 | 30510 | 34350 | 31352 | 2998
Three Phase | 1279 | 5553 | 6832 | 5838 | 994
Total | 5119 | 36063 | 41182 | 37190 | 3992

## SoP 014
Uttar Gujarat Vij Company Ltd ,Mehsana
QUARTER : 1st (April-21 to Sept-21)
YEAR: 2021-22
Performa SoP 014: Statement Showing the ATC losses, collection efficiency and Billing Efficiency
Qtr. | Months | Units input (Mus) | Units Billed (Mus) | Billing Efficiency | Revenue Billed (Rs. Crore) | Revenue Collected (Rs. Crore) | Collection Efficiency* % | Business Efficiency | AT & C Losses %
|  | A | B | C=(B/A)*100 | D | E | F=(E/D)*100 | G=(C*F)/100 | H=100-G
I | 2021-04-15 | 2614.837 | 2180.661 | 83.3957 | 1048.771 | 1226.238 | 100 | 83.3957 | 16.6043
| 2021-05-15 | 2418.938 | 2109.92 | 87.2251 | 1021.606 | 1082.785 | 100 | 87.2251 | 12.7749
| 2021-06-15 | 2133.023 | 2117.845 | 99.2884 | 1030.584 | 1295.529 | 100 | 99.2884 | 0.71157
| Sub Total | 7166.798 | 6408.426 | 89.4183 | 3100.961 | 3604.552 | 100 | 89.4183 | 10.5817
II | 2021-07-15 | 2168.005 | 2034.964 | 93.8634 | 1165.689 | 1410.569 | 100 | 93.8634 | 6.1366
| 2021-08-15 | 2514.326 | 2030.03 | 80.7385 | 1126.804 | 1442.31 | 100 | 80.7385 | 19.2615
| 2021-09-15 | 1722.2624 | 1947.2114 | 113.0612 | 1132.4384 | 1453.6582 | 100 | 113.0612 | -13.0612
| Sub Total | 6404.5934 | 6012.2054 | 93.8733 | 3424.9314 | 4306.5372 | 100 | 93.8733 | 6.1267
III | 2021-10-15 |  |  | #DIV/0! |  |  | #DIV/0! | #DIV/0! | #DIV/0!
| 2021-11-15 |  |  | #DIV/0! |  |  | #DIV/0! | #DIV/0! | #DIV/0!
| 2021-12-15 |  |  | #DIV/0! |  |  | #DIV/0! | #DIV/0! | #DIV/0!
| Sub Total | 0 | 0 | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0!
IV | 2022-01-15 |  |  | #DIV/0! |  |  | #DIV/0! | #DIV/0! | #DIV/0!
| 2022-02-15 |  |  | #DIV/0! |  |  | #DIV/0! | #DIV/0! | #DIV/0!
| 2022-03-15 |  |  | #DIV/0! |  |  | #DIV/0! | #DIV/0! | #DIV/0!
| Sub Total | 0 | 0 | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0!
Grand Total |  | 13571.3914 | 12420.6314 | 91.5207 | 6525.8924 | 7911.0892 | 100 | 91.5207 | 8.4793
| * | Collection Efficiency above 100% is taken as 100%

## SoP015
Uttar Gujarat Vij Company Limited
Year 2021-22 (Apr. - 21 to Sept. - 21)
Performa SoP 015 : Release of New connection : Status as on 31.09.21
Consumer Category | Total No. of consumers connected at the beginning of half year (i.e. as on Apr-21) | Pending at the beginning of the of the Half year (i.e. as on Apr.-21) | New Applications received during the half-year | No. of Connections released during the Half year | No. of Applications pending at the end of Half year | Total no. of consumers connected at the end of the half year (Sept.-21)
Domestic | 2895696 | 6221 | 54412 | 43822 | 14150 | 2939518
Commercial (GLP) | 25941 | 8 | 458 | 308 | 59 | 26249
Industrial LT (NRGP & LTMD) | 416391 | 2485 | 14132 | 11155 | 3348 | 427546
Agriculture (Total) | 393644 | 25097 | 8980 | 5576 | 27566 | 399220
Industrial HT | 4962 | 36 | 274 | 212 | 9 | 5174
Total | 3736634 | 33847 | 78256 | 61073 | 45132 | 3797707

## SoP016
Uttar Gujarat Vij Company Limited
QUARTER :- 2nd (July- 21 to Sept.- 21)
Performa SoP 016 : Compensation details
COMPENSATION DETAILS
Sr. No. | Event | Compensation | No. of cases where compensation was given (in numbers) | Amt.of compensation paid (in Rs.)
1 | Duty to provide supply | Rs.50 per day of delay from the limit specified in the performance regulations | …NIL… | …NIL…
a) New connection
b) Additional load
c) Temporary supply
d) Shifting service connection
e) Transfer of service connection
f) Change in tariff category of consumer
2 | Complaints in billing | Rs.50 for non reply within the period prescribed in Regulations
3 | Replacement of meters | LT Rs.25 per day of delay maximum Rs.2,500 and HT Rs. 250 per day of delay maximum of Rs. 5,000/-
4 | Interruption of supply | LT Rs.25 for every 6 hrs. of delay maximum of Rs.500 and HT Rs. 50 for every 6 hrs. delay maximum Rs. 1000
5 | Voltage fluctuations and complaints | Rs.50 for failure to visit or convey findings within the stipulated period
6 | Responding to consumers complaints | Rs. 25 for each day of delay maximum Rs. 500
7 | Grievance Handling | Rs. 25 for failure in handling grievance.
| TOTAL :- |  | …NIL… | ……NIL…..