## MG COVER PAGE
Name of Distribution Licensee: M G V C L
Quarter : Q-III (OCT- NOV-DEC - 2021)
Year: 2021-22

## SOP-1
Name of Distribution Licensee: M G V C L
Quarter : Q-III ( OCT.-NOV.-DEC.- 2021)
Year: 2021-22
Performa - SoP 001: Fatal and Non-fatal accident report
NUMBER OF ACCIDENTS FOR THE THIRD QUARTER 2021-22
Sr.No | Name of Area/Circle | No of accidents in the quarter |  |  |  |  | Cumulative since the first quarter of the current FY 2021-22 |  |  | Cumulative since the first quarter of the last FY 2020-21
|  | Departmental |  | Outside |  |  | TOTAL |  |  | TOTAL
|  | FH | NFH | FH | FA | NFH | FH | FA | NFH | FH | FA | NFH
1 | Baroda City | 0 | 0 | 0 | 0 | 0 | 1 | 4 | 1 | 1 | 2 | 1(1-Mech)
2 | Baroda (O&M) | 0 | 0 | 2 | 3 | 0 | 5 | 23 | 4 | 7 | 25 | 14(1-Pvt)
3 | Anand | 0 | 2 | 1 | 1 | 1 | 7 | 10 | 3 | 6(2-PVT) | 5 | 2
4 | Godhra | 0 | 0 | 1 | 2 | 2 (1-Pvt) | 7 | 31 | 5 (1-Pvt) | 15(3-PVT) | 30(1-PVT) | 7
5 | Nadiad | 1 | 0 | 1 | 3 | 0 | 6 | 16 | 2 | 10(2-PVT) | 10 | 7
| TOTAL | 1 | 2 | 5 | 9 | 3 (1-Pvt) | 26 | 84 | 15 (1-Pvt) | 39(7-PVT) | 72(1-PVT) | 31(1-Pvt)
[6 empty] | 20 (1-Pvt) |  |  | 125 (1-Pvt) |  |  | 142
FH – Fatal Human, FA – Fatal Animal, NFH – Non-fatal Human
The format is to be sent quarterly
Note: Above figures for cummulative accident i.e. from April21 to Dec'21 are inclusive of 1 No. of Non-fatal Human Accident occurred in Private premises under Godhra Circle. | [9 empty] | 7 Nos. of Fatal Human accident in Pvt Premises (Anand-2,Nadiad-2 & Godhra Circle-3), 1 No of Fatal Animal accident in Pvt. Premises in Godhra circle and 1 No of Non-Fatal Human accident in BOM circle.

## SOP-II
Performa – SoP 002: Action taken report for safety measures complied for the accidents occurred
ACTION TAKEN REPORT FOR SAFETY MEASURES COMPLIED FOR THE ACCIDENTS OCCURED IN THE SECOND QUARTER OF FY 2020-21
Sr. No | Location of Accident and details of the victim | Date of occurrence | Type of Accident | Cause of Accident | Findings of CEI / EI / AEI | Remedies suggested by CEI /EI / AEI in various cases | Whether the remedy suggested is complied | Action taken to avoid recurrence of such Accident | Circle
1 | VALAND JAYESHBHAI DAHYABAHI, DHOLI-VIRPUR (DEBHARI AG/80), Vill-Dholi, Tal-Virpur, Dist-Mahisagr | 2021-10-03 | NFHO | A Non fatal Human electrical accident occurred to Shri Jayeshbhai Dahyabhai Valand at Dholi village Ta. Virpur Dist.Mahisagar on Dtd. 03.10.2021 at time 18:10 hours (approximate). | Awaited | NA | NA | Nil | Godhra
2 | (1)Vijaybhai Bachubhai Vasava (2)Gajaraben Bachubhai Vasava, Nr.Meldi Mata Temple,Koyli Chara Vistar, Vill-Koyali, Dist-Vadodara | 2021-10-04 | FHO | A broken Street light conductor was hanging from the LT PSC pole which was disconnected from the both end.(i.e supply side and load side).The both victimtouched the same conductor and got electrocuted. | Awaited | NA | NA | RESTRINGING OF BROCKEN CONDUCTOR | Baroda O&M
3 | ASHWINBHAI RAYJIBHAI PATEL AND NARMADABEN ASHWINBHAI PATEL, SIMADA FALIYU, Vill-Paniya, Tal-Limkheda, Dist-Dahod | 2021-10-04 | PVT-NFHO | UPTO METER WIRING WAS IN HEALTHY CONDITION. AT LOAD SIDE YELLOW COLOURED TWO CORE WIRE FOUND PUNCTURE AND IT MAY TOUCHED TO IRON SWING. ACCIDENTALLY BOTH VICTIM MIGHT GET TOUCHED THAT ELECTROCUTE IRON SWING RESULTING IT IN ELECTROCUTION | Awaited | NA | NA | Nil | Godhra
4 | BUFFALO OF KAMLESHBHAI RAMESHBHAI SOLANKI, Vill-DETHALI, Tal-Matar, Dist-Kheda | 2021-10-05 | FA | AT THE TIME OF PANCHNAMA NO POWER LEKAGE FOUND AND BUFFALO DIED NEAR TRANSFORMER CENTER BETWEEN 2 POLS | Awaited | NA | NA |  | Nadiad
5 | Mahendrabhai Ramprasad Meena, Nr Swaminarayan Mandir, Vill-Gopalpura, Tal/Dist-Anand | 2021-10-05 | NFHO | The victim (Contractor labour) climbed on PSC pole before instruction of supervisor Lineman and suddenly came in contact with 11KV live line and met with non fatal accident. | Awaited | NA | NA | Nil | Anand
6 | Dilipbhai Ravajibhai Solanki, Plot No.C-1/3-4,Pavan Pressure Cast,GIDC,Vidyanagar, Dist-Anand | 2021-10-07 | NFHD | During joined HT solar testing of PAVAN Pressure cast,GIDC area,vidyanagar sdn,Shri Dilipbhai Ravajibhai Solanki ,meter tester of Anand City Labwasa making accucheck wiring in solar generation meter for testing and then while going to connect PT wiring in | Awaited | NA | NA | Nil | Anand
7 | BUFFALO OWNER SHREE ARVINDBHAI JASHUBHAI SOLANKI, Vill-Shivpura sim, Tal-Savli, Dist-Vadodara | 2021-10-08 | FA | SHE BUFFALO OF SHREE SOLANKI ARVINDBHAI JASHUBHAI WAS GRAZING IN SHIVPURA SIM VISTAR.11KV RAMNAGAR HT LINE IS PASSING THROUGH THERE 2 NO POLE OF THE SAID FEDEER HAVE TILTED DUE TO HEAVY RAIN AND NATIONAL HIGHWAY WORK IS ALSO GOING ON AT THE SAID LOCATION. | Awaited | NA | NA | New pole Erected | Baroda O&M
8 | Buffalo of Smt. Rehanabibi Yakubmiya Malek, Vill-Rudan, Tal-mahemdabad, Dist-Kheda | 2021-10-12 | FA | The Buffalo came in contact with GI wire of TCDP and electrocuted due to leakage current passing through GI wire of transformer earthing. | Awaited | NA | NA |  | Nadiad
9 | Cow of Maheshbhai Ratnabhai Bharwad, Ghanchi Talavadi, Vill-Marida Road, Tal-Nadiad, Dist-Kheda | 2021-10-13 | FA | LT Jumper Burnt on DP structure and animal might have come in contact with earthing wire | Awaited | NA | NA |  | Nadiad
10 | Maheshbhai Ratnabhai Bharwad, Ghanchi Talavadi, Vill-Marida Road, Tal-Nadiad, Dist-Kheda | 2021-10-13 | FHO | While making attempt for saving his own cow | Awaited | NA | NA |  | Nadiad
11 | BUFFALO OF JAGDISHBHAI MAGANBHAI VASAVA, Vill-Kurali, Tal-karjan, Dist-Vadodara | 2021-10-26 | FA | LT LIVE (ONE PHASE) WIRE WAS SNAPPED AND CAME IN CONTACT WITH THE BUFFALO | Awaited | NA | NA | RESTRINGING OF BROCKEN CONDUCTOR | Baroda O&M
12 | Arvindbhai Chimanbhai Prajapati, Maniaji chauhan Farm, Vill-Bava na Muvada, Tal-Kapadvanj, Dist-Kheda | 2021-10-28 | FHD | The concern linestaff team memner who worked in same team in which Lt Mr A.C.Prajapati worked and from primary investigation it is come to notice that victim had allotted the work of charging the new Transformer (HVDS) with the other 4 nos team member und | Awaited | NA | NA |  | Nadiad
13 | HUKIYABHAI DULSING NINAMA, NEAR MAHAKALI TEMPLE DARPAN ROAD, Vil/Tal/Dist-Dahod | 2021-11-11 | FHO | IT IS OBSERVED THAT VICTIM WAS LYING ON IRON (PATRA) SHED OF OWNER OF THE HOUSE SHRI MAHESH PARSING GANAVA. ON FURTHER INVESTIGATION IT WAS OBSRVED THAT 1-PH 2C SERVICE WIRE WAS TANGLED WITH HIS BODY. AS IT WAS DARK IN EARLY MORNING, BURNT MARKS WAS NOT SEEN ON HIS BODY. | Awaited | NA | NA | Service line replaced with GI, reel & egg insulator | Godhra
14 | Manojbhai Punvasi Pasvan, Vil-Bakrol, Tal/Dist-Anand | 2021-11-20 | FHO | The victim was passed through under 11KV line of iskonfeeder at near rambug society, mahivas area of vidhyanagar, the victim got electrocuted due to came live contact with snapped conductor of iskon feeder and got dead at site. | Awaited | NA | NA | 15 Span conductor replaced from 34mm2 to 55 mm2 | Anand
15 | Natubhai Kabhaibhai Solanki, Nr.ECP Canal,Ampad village, Tal/Dist-Vadodara | 2021-11-25 | FHO (Mech) | Accidently LT Psc pole fallen on the victim during passing on the bicycle during Repairing work done by the Line staff of Koyli sub division at near ECP canal, Near Ampad village. | Awaited | NA | NA | mechnical | Baroda O&M
16 | Mustakali Mosamali Saiyad, Nr. ONGC Colony main gate & Compound wall, Vill-Kansari, Tal-Khambhat, Dist-Anand | 2021-11-27 | NFHD | 11 KV ONGC Urban feeder Maintenance & Tree cutting work given to victim & his team and by mistake/unknowlingly victim start tree cutting on 11 KV Kalodara AG Feeder in stead of 11 KV ONGC Feeder and came in live 11 KV feeder contact & Fallen down suddenly. | Awaited | NA | NA |  | Anand
17 | Shri.Ranjitbhai Ramsangbhai Gohil's buffalo, Vil-Lakodra, Tal-Karjan, Dist-Vadodara | 2021-11-28 | FA | From the observation of the place it seems that HT line was passing between highway and lakodara sim near village lake. Due to fault occurred in line and break line one conductor fallen down on earth. While buffalo might have came in contact with broken conductor. | Awaited | NA | NA | RESTRINGING OF BROCKEN CONDUCTOR | Baroda O&M
18 | BUFFALO OF SHRI NILESHBHAI BADHARBHAI PARMAR, KRUSHNANAGAR SOCIETY, Dharmaj, Tal-Petlad, Dist-Anand | 2021-12-01 | FA | GI wire came in contact with joint of service wire with ABC on LT Pole. Leakage current came through GI wire on Iron's Shed. The She Buffalo came in conact with the Support angle of Shed and Elecrocuted | Awaited | NA | NA | New Service wire provided | Anand
19 | PATEL GULABBHAI KADVABHAI , TEKRI FALIA SARSAV , Tal-Godhra, Dist-Panchmahal | 2021-12-06 | FA | A BUFFALO DIED DUE TO LEAKAGE CURRENT FLOW FROM JOINT OF LT ABC ON LT SHACKLE POLE NO 3 DUE TO DETERIORATED LT TAP GOT IN TOUCH WITH MESSENGER WIRE OF THE LT ABC THROUGH THIS MESSENGER WIRE THE LEAKAGE CURRENT FLOWED TO THE GI WIRE EARTHING OF THE LT POLE | Awaited | NA | NA | Lt joint made proper and sufficient clearance provided from messanger conductor & by providing LT Tap roll | Godhra
20 | BAFFELLO OF PREMILABEN VIKRAMBHAI KHANT, VIRNIYA (GHANA FALIYA), Tal-Lunawada, Dist-Mahisagar | 2021-12-13 | FA | AG LT LINE AB CABLE PUNCTURE AND TOUCH WITH U-CLAMP AND U-CLAMP CONTACT WITH EARTHING G.I WIRE AND LEAKAGE CURRENT FLOW THROUGH THIS G I WIRE. THE BUFFALO CAME IN CONTACT WITH G I WIRE AND ELECTROCUTED. | Awaited | NA | NA | AB Cable replaced | Godhra

## SOP-3
Name of Distribution Licensee: M G V C L
Quarter : Q-III (OCT- NOV-DEC - 2021)
Year: 2021-22
REGISTER FOR COMPILING THE COMPLAINTS CLASSIFICATIONWISE Q-III 2021-22
Performa SoP 003 B: |  |  |  | APPENDIX-B (already in the SoP regulation)
Classification | Nature of Complaints | Pending complaints of previous qtr. | Complaints received during the qtr. | Total Complaints =2+3 | No. of Complaints redressed during the quarter. |  |  |  |  | Balance Complaints to be redressed. (4) – (9)
[5 empty] | In stipulated time |  | Beyond stipulated time |  | Total (5) to (8)
[5 empty] | Within 50% of stipulated time. | Within stipulated time. | Up to double the stipulated time | More than double the stipulated time
| 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10
A(i) | Loose Connection | 0 | 60208.4218 | 60208.4218 | 29394.6056 | 30813.8161 | 0 | 0 | 60208.4218 | 0
A(ii) | Intruption due to line Break down | 0 | 36873.1419 | 36873.1419 | 20276.0348 | 16597.1071 | 0 | 0 | 36873.1419 | 0
A(iii) | Intruption due to T/C Fail | 0 | 10739.0877 | 10739.0877 | 7287.2258 | 3451.8619 | 0 | 0 | 10739.0877 | 0
B(i) | Quality of power supply,ordinary case which require no Augmentation | 0 | 8761.7453 | 8761.7453 | 3915.2236 | 4846.5217 | 0 | 0 | 8761.7453 | 0
B(ii) | Quality of power supply,ordinary case which require Augmentation | 0 | 4391.3736 | 4391.3736 | 2120.374 | 2270.9996 | 0 | 0 | 4391.3736 | 0
C(i) | Meters- Stoped/Defective meter | 0 | 13128.8226 | 13128.8226 | 6314.6962 | 6814.1264 | 0 | 0 | 13128.8226 | 0
C(ii) | Meters- Billing on average basis for > two bills | 0 | 6669.2554 | 6669.2554 | 3383.9946 | 3285.2608 | 0 | 0 | 6669.2554 | 0
D(i) | Over head lines - loose wires | 0 | 6328.282 | 6328.282 | 3518.2269 | 2810.0551 | 0 | 0 | 6328.282 | 0
D(ii) | Over head lines - in adiquate ground clearance | 0 | 2117.1277 | 2117.1277 | 1183.4927 | 933.635 | 0 | 0 | 2117.1277 | 0
E(i) | Bills- for current bills where no addl information required | 0 | 4903.9932 | 4903.9932 | 2626.8002 | 2277.193 | 0 | 0 | 4903.9932 | 0
E(ii) | Bills- for current bills where addl information required | 0 | 2822.6777 | 2822.6777 | 1535.1237 | 1287.5541 | 0 | 0 | 2822.6777 | 0
F(i) | Service connections- where extention of mains is not required | 0 | 5799.3221 | 5799.3221 | 3683.8184 | 2115.5036 | 0 | 0 | 5799.3221 | 0
F(ii) | Service connections- where extention of mains is required | 0 | 3254.8579 | 3254.8579 | 1698.5641 | 1556.2937 | 0 | 0 | 3254.8579 | 0
F(iii) | Service connections- Modification in connected load | 0 | 2921.2497 | 2921.2497 | 1477.4257 | 1443.8241 | 0 | 0 | 2921.2497 | 0
F(iv) | Service connections- Name change/reconnection | 0 | 3154.3593 | 3154.3593 | 1677.298 | 1477.0614 | 0 | 0 | 3154.3593 | 0
G | Refund of amount due inregard to temp conn | 0 | 817.2316 | 817.2316 | 452.6821 | 364.5495 | 0 | 0 | 817.2316 | 0
H | Others | 0 | 17077.0504 | 17077.0504 | 8961.9726 | 8115.0779 | 0 | 0 | 17077.0504 | 0
| TOTAL | 0 | 189968 | 189968 | 99507.559 | 90460.441 | 0 | 0 | 189968 | 0
The format is to be sent quarterly
The quarterly reporting of the year means reporting for the period 1st Quarter as Jan – Mar, 2nd Quarter as Apr – Jun, 3rd Quarter as Jul – Sep and 4th Quarter as Oct – Dec of the year.
For any other complaints not mentioned in the classification, the sequence for (H) can be used.

## MG SoP 04
Name of Distribution Licensee: M G V C L
Quarter : Q-III (OCT- NOV-DEC - 2021)
Year: 2021-22
Performa SoP 004 : Publicity carried out while displaying the contact details of consumer complaints centers
Particulars should also cover the details of consumer awareness program conducted, advertisement done through various media like TV, newspaper, radio, pamphlets & booklet distributions, Displays etc. The development of website and any medium through which public education is carried out can be included.
Sr. No | Actions or steps carried out by distribution licensee towards public awareness in the quarter | Likely number of consumers influenced
1 | RTI Officers Name is displayed at customer care centre on each office | 3365294
2 | Necessary information regarding time schedule for new connection and solving complaints is display on the board. | 3365294
3 | Contact nos. of various officers of the company for emergency contact is also displayed at customer care centre. | 3365294
4 | Displayed safety posters at various S/dn,Divisions | 4300
5 | Safety Meeting with Line Staff at various S/dn,Divisions on Every Monday (Line staff influenced) | 14200

## SOP-5
Name of Distribution Licensee: M G V C L
SOP Q-II (July-Aug-Sept-21)
Year: 2021-22
Performa – SoP 005 B: Action taken report by the Redressal Committee
Sr. No | Month | Date and Time Meeting conducted | No of complaints registered at the meeting | No. of complaints pending at the end of the meeting
1 | 1st Month of the quarter (OCT'21) | 20.10.21,11.30 am at Corporate Office | Corp-01 Godhra-02 Total=3 | Corp-Nil Godhra-02 Total=02
2 | 2nd Month of the quarter (Nov'21) | Nil | Corp-01 Godhra-01 Total=2 | Corp-01 Godhra-03 Total=04
3 | 3rd Month of the quarter (DEC'21) | 17.12.21,11.30 am at Corporate Office & 15.12.2021,11.00 am at Godhra Circle | Corp-01 | Nil

## SOP-6
Name of Distribution Licensee: M G V C L
Financial Year: 2021-22
Quarter : Q-III (Oct-Nov-Dec-2021 )
Performa SoP 006: Failure of Distribution Transformer
Sr. No. | Name of Circle | Nos. of existing Distribution Transformers at the start of the quarter | Nos. of Distribution Transformers added during the quarter | Total number of Distribution Transformers on end of quarter | Total number of Distribution transformer failed during quarter-III | % failure rate of Distribution transformer
|  | A | B | C=A+B | D | H = (D)*100/C
1 | Baroda O&M | 50631 | 518 | 51149 | 1010 | 1.9746
2 | Baroda City | 8807 | 69 | 8876 | 3 | 0.033799
3 | Anand | 23517 | 380 | 23897 | 172 | 0.71976
4 | Nadiad | 30745 | 524 | 31269 | 298 | 0.95302
5 | Godhra | 53474 | 1717 | 55191 | 1233 | 2.2341
| MGVCL | 167174 | 3208 | 170382 | 2716 | 1.5941

## SOP-8
Name of Distribution Licensee: M G V C L
Quarter : Q-III ( OCT.-NOV.-DEC.- 2021)
Year: 2021-22
Performa SoP 008: Sample Test result for Neutral Voltage
Compliance Sample Test Report for Neutral Voltage
-1 | -2 | -3 | -4 | -5 | -6
Sr. No | Category of consumers | Sample Size | Standard specified in regulation | Deviation of results from the sample test (Numbers) | % age compliance
|  | (Numbers) |  |  | (6) = (5)*100/(3)
| LT consumers | 1416 | 2% | 0 | 0
1 | Domestic | 1020 | 2% | 0 | 0
2 | Commercial | 237 | 2% | 0 | 0
3 | Industrial | 18 | 2% | 0 | 0
4 | Agricultural | 133 | 2% | 0 | 0
5 | Public water works | 8 | 2% | 0 | 0
| HT consumers | 5 | 2%
6 | HT industrial | 5 | 2% | 0 | 0

## SOP-9
Name of Distribution Licensee: M G V C L
Quarter : Q-III ( OCT.-NOV.-DEC.- 2021)
Year: 2021-22
Performa SoP 009: Sample Test result for Voltage variations
Compliance Sample Test Report for voltage variations
-1 | -2 | -3 | -4 | -5
Voltage Level | Sample Size (numbers) | Limit or prescribed standard | Deviation of results from the sample test (Numbers) | % age compliance
(5) = (4)*100/(2)
Low Voltage | 18 | +6% to -6% | 0 | 0
High Voltage | 3 | +6% to -9% | 0 | 0
Extra High Voltage | 1 | +10% to -12.50% | 0 | 0

## SOP-10
Name of Distribution Licensee: M G V C L
Quarter : Q-III ( OCT.-NOV.-DEC.- 2021)
Year: 2021-22
Performa SoP 010: Sample Test result for Harmonics
Compliance Sample Test Report for Harmonics
-1 | -2 | -3 | -4 | -5 | -6
Sr. No | Category of consumers | Sample size (Numbers) | Limit or standard prescribed | Deviation of results from the sample test (Numbers) | %age compliance
(6) = (5)*100/(3)
1 | LT consumers | 34 | 3.5% | 0 | 0
2 | HT consumers | 4 | 3% | 0 | 0
3 | EHT consumers | 1 | 3% | 0 | 0
Note: The licensee shall also submit along with the above harmonic data, the records of customer wise drawls of harmonic currents measured at various strategic points.
The formats SoP 008, SoP 009 and SoP 010 have to be sent annually.
For the purpose of annual submissions, the year end has to be considered as the end of December month of a particular year.

## SOP-11
Q-3(Oct-Dec-21)
Year: 2021-22
SoP 011 –A: System Average Interruption Frequency Index (SAIFI)
Sr. No | Month | Ni - Total no of customers for each momentary interruptions | NT - Total no of customers served |  |  | Past year corrosponding Month
1 | 2 | 3 | 4 | 5 | 6=5/4
1 | Oct' 21 | 3112269 | 3359364 | 12439556 | 3.7029 | 3.57
2 | Nov' 21 | 3073774 | 3374981 | 8974690 | 2.6592 | 2.51
3 | Dec' 21 | 3147911 | 3365294 | 11149786 | 3.3132 | 3.6
|  |  | 10099639 | 32564032 | 3.2243 | 3.22

## SOP-11-B
Q-3(Oct-Dec-21)
Year: 2021-22
SoP 011 – B System Average Interruption Duration Index (SAIDI)
Sr. No | Month | ri = Restoration Time for each interruption event | Ni - no of interrupted customers for each sustained interruption event | ri * Ni – Total customer interruption Duration | ri=Restoration Time for each interruption event | Ni= No of Interrupted customers for each sustained Interruption | NT - Total no of customers served | Customer Interruption Duration |  |  | Past year corrosponding Months
[9 empty] | MINS. | HRS.
1 | 2 | 3 | 4 | 5= 3 X 4 | 3 | 4 | 5 | 6 | 7=4/3 | 7A | MINS. | HRS.
1 | Oct' 21 | July |  |  | 804638 | 3112269 | 3359364 | 998598401 | 297.2582 | 0.20625 | 382 | 0.26528
2 | Nov' 21 | August |  |  | 585781 | 3073774 | 3374981 | 768573558 | 227.7268 | 0.15833 | 298 | 0.20694
3 | Dec' 21 |  |  |  | 618366 | 3147911 | 3365294 | 795095914 | 236.2634 | 0.16389 | 437 | 0.30347
[6 empty] | 9333954 | 10099639 | 2562267873 | 253.699 | 0.17639 | 372 | 0.25833

## SOP-11-C
Q-3(Oct-Dec-21)
Year: 2021-22
SoP 011 – C: Momentary Average Interruption Frequency Index (MAIFI)
Sr. No | Month | Number of Momentary interruptions Imi | Nmi - Total no of customers for each momentary interruptions | NT - Total no of customers served |  |  | Past year corrosponding Month
1 | 2 | 3 | 4 | 5 | 6 | 7
1 | Oct' 21 | 19501 | 2911618 | 3359364 | 32878366 | 9.7871 | 11.46
2 | Nov' 21 | 17669 | 2855860 | 3374981 | 29769680 | 8.8207 | 9.59
3 | Dec' 21 | 16888 | 2931868 | 3365294 | 28745579 | 8.5418 | 9.59
|  |  |  | 10099639 | 91393625 | 9.0492 | 10.21

## SOP-13
Name of Distribution Licensee: M G V C L
Financial Year: 2021-22
Quarter : Q-III (Oct-Nov-Dec-2021 )
Performa SoP 013: Faulty Meters Replacement
Consumer Category | No. of faulty meters at the start of the quarter | No. of faulty meters added during the quarter | Total no. of defective / faulty Meter | No. of faulty Meters repaired and replaced | No of faulty meters pending at the end of the quarter | Remark
| 1 | 2 | (3)=(2)+(1) | 4 | (5)=(3)-(4)
1 PHASE
MGVCL | 12135 | 28116 | 40251 | 27176 | 13075
3 PHASE
MGVCL | 3495 | 1261 | 4756 | 3130 | 1626

## MG SoP 16
Name of Distribution Licensee: M G V C L
Quarter : Q-III ( OCT.-NOV.-DEC.- 2021)
Year: 2021-22
Performa SoP 016: Compensation details
COMPENSATION DETAILS
Sr.No. | Event | Compensation | No of cases where compensation was given (in numbers) | Amt of compensation paid (in Rs.)
1 | Duty to provide supply | Rs. 50 per day of delay from the limit specified in the performance regulations | 0 | 0
| a) New Connection |  | 0 | 0
| b) Additional Load |  | 0 | 0
| c) Temporary supply |  | 0 | 0
| d) Shifting service connection |  | 0 | 0
| e)Transfer of service connection |  | 0 | 0
| f) Change in tariff category of consumer |  | 0 | 0
2 | Complaints in billing | Rs. 50 for non reply within the period prescribed in Regulations | 0 | 0
3 | Replacement of meters | LT- Rs. 25 per day of delay - maximum Rs.2,500 and HT - Rs. 250 per day of delay - maximum of Rs.5,000 | 0 | 0
4 | Interruption of supply | LT- Rs. 25 for every 6 hrs of delay- maximum of Rs. 500 and HT- Rs. 50 for every 6 hrs delay- maximum Rs. 1000/- | 0 | 0
5 | Voltage fluctuations and complaints | Rs. 50 for failure to visit or convey findings within the stipulated period | 0 | 0
6 | Responding to consumer's complaints | Rs. 25 for each day of delay- maximum Rs. 500 | 0 | 0
7 | Grievance Handling | Rs.25 for failure in handling grievance | 0 | 0
TOTAL |  |  | 0 | 0

## SOP-12
Performa SoP 012 : System Losses at EHT/ 11 KV |  |  |  | OCT-21 TO DEC-21
CALCULATION OF SYSTEM LOSSES AT EHT/ 11 KV
1 | Losses in 11 KV System and Connected Equipment
| i. | Energy Delivered into EHT/ 11 KV and LT Distribution System from EHT/ 11 KV SS (MUs) | A | 10115.0791
| ii. | Energy Sold (Billed). EHT direct sales (MUs) | B | 1956.7076
| iii. | Energy Sold (Billed) in the 11 KV LT system (MUs) | C | 7375.2253
| iv. | Total Sales (MUs) | (B+C) | 9331.9329
| v. | Losses (MUs) | {(A) - (B+C)} | 783.1462
| vi. | % Losses | {(A) - (B+C)} X 100 / (A) | 7.7424

## SOP-14
Performa SoP 014: Statement Showing the ATC losses, collection efficiency and Billing Efficiency | [8 empty] | F.Y. 2021-22
Quarter | Month | Units Input (MUs) | Units Billed (MUs) | Billing Efficiency % | Revenue Billed (Rs. Crs) | Revenue Collected (Rs. Crs) | Collection Efficiency % | Business Efficiency % | ATC Loss%
|  | A | B | C = (B/A)*100 | D | E | F = (E/D)*100 | G = (C*F)/100 | H = 100 - G
Q-I | April'21 | 1246.711 | 1086.2582 | 87.1299 | 686.57 | 612.77 | 89.2509 | 77.7642 | 22.2358
| May'21 | 1172.5739 | 1057.0496 | 90.1478 | 749.64 | 663.51 | 88.5105 | 79.7903 | 20.2097
| June'21 | 1127.2341 | 1082.643 | 96.0442 | 731.64 | 719.91 | 98.3968 | 94.5044 | 5.4956
| Q-I | 3546.519 | 3225.9508 | 90.961 | 2167.85 | 1996.19 | 92.0816 | 83.7583 | 16.2417
Q-II | July'21 | 1202.7921 | 1071.1743 | 89.0573 | 757.52 | 767.77 | 101.3531 | 90.2623 | 9.7377
| August'21 | 1191.5756 | 1060.6757 | 89.0146 | 778.04 | 762.81 | 98.0425 | 87.2721 | 12.7279
| September'21 | 1055.8423 | 1028.6806 | 97.4275 | 776.9 | 771.82 | 99.3461 | 96.7904 | 3.2096
| Q-II | 3450.21 | 3160.5306 | 91.604 | 2312.46 | 2302.4 | 99.565 | 91.2055 | 8.7945
2021-22 | Half Year | 6996.729 | 6386.4814 | 91.2781 | 4480.31 | 4298.59 | 95.944 | 87.5759 | 12.4241
Q-III | October | 1148.3822 | 1038.4053 | 90.4233 | 762.52 | 764.42 | 100.2492 | 90.6486 | 9.3514
| November | 999.6382 | 967.3917 | 96.7742 | 746.74 | 750.45 | 100.4968 | 97.255 | 2.745
| December | 970.3297 | 939.6546 | 96.8387 | 705.83 | 761.14 | 107.8362 | 104.4271 | -4.4271
| Q-III | 3118.3501 | 2945.4516 | 94.4554 | 2215.09 | 2276.01 | 102.7502 | 97.0532 | 2.9468