## MG COVER PAGE
Name of Distribution Licensee: M G V C L
Quarter : Q-I (April-May-June- 2022)
Year: 2022-23

## MG SoP 01
Name of Distribution Licensee: M G V C L
Quarter1 (APR-21 to JUN-21)
Year:2022-23
Performa - SoP 001: Fatal and Non-Fatal electrical accident report
NUMBER OF ACCIDENTS FOR THE 1st QUARTER OF 2022-23
Sr.No | Name of Area/Circle | No of accidents in the quarter |  |  |  |  | Cumulative since the first quarter of the current FY 2022-23 |  |  | Cumulative since the first quarter of the Last FY 2021-22
|  | Departmental |  | Outside |  |  | TOTAL |  |  | TOTAL
|  | FH | NFH | FH | FA | NFH | FH | FA | NFH | FH | FA | NFH
1 | Baroda (City) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 4 | 1
2 | Baroda (O&M) | 0 | 1 | 1 | 1 | 3 | 1 | 1 | 4 | 8 | 26 | 8
3 | Anand | 0 | 0 | 0 | 2 | 1 | 0 | 2 | 1 | 7 | 11 | 3
4 | Godhra | 0 | 1 | 6 (4-Pvt) | 3 (1-Pvt) | 0 | 6 (4-Pvt) | 3 (1-Pvt) | 1 | 10 (1-Pvt) | 35 | 5 (1-Pvt)
5 | Nadiad | 0 | 3 | 6 (2-Pvt) | 4 | 2 | 6 (2-Pvt) | 4 | 5 | 7 | 17 | 3
| TOTAL | 0 | 5 | 13 (6-Pvt) | 10 (1-Pvt) | 6 | 13 (6-Pvt) | 10 (1-Pvt) | 11 | 33 (1-Pvt) | 93 | 20 (1-Pvt)
FH – Fatal Human, FA – Fatal Animal, NFH – Non-fatal Human | [5 empty] | 34 |  |  | 34 |  |  | 146
PVT - Private Premises Accident.

## SoP 002
Performa – SoP 003: Action taken report for safety measures complied for the electrical accidents occurred
ACTION TAKEN REPORT FOR SAFETY MEASURES COMPLIED FOR THE ELECTRICAL ACCIDENTS OCCURED IN THE FIRST QUARTER OF FY 2022-23
1 | 2 |  |  | 3 | 4 |  |  | 5 | 6 | 7 | 8 | 9 | 10
Sr. No | Location of Accident and details of the victim | Address | sdn | Date of occurrence | Type of Accident | Installation | Accident Type | Cause of Accident | Findings of CEI / EI / AEI | Remedies suggested by CEI /EI / AEI in various cases | Whether the remedy suggested is complied | Action taken to avoid recurrence of such Accident | Circle office | Reason
1 | NAGINBHAI MANUBHAI THAKOR, KHODIYAR VISTAR,TEKRA FALIYU, Vill-Jalundh, Tal-Khambhat, Dist-Anand |  |  | 2022-04-01 | NFHO |  |  | A DAILY WAGES WORKER HAD CLIMBED ON IRON PIPE TO FIX SCAFFOLDING. IN THE MEAN TIME GETS UP AND HE MIGHT HAVE TOUCHED THE OPEN CONDUCTOR TO 11 KV JALUNDH FEEDER. THE SAID HT LINE WAS PASSING ABOVE THE HOUSES NEARER TO SCAFFOLDING STRUCTURE.THUS HE GOT ELECTROCUTED | Unauthorized work on line found | NO | No | POLE SHIFTELD & HEIGHT OF LINE MAINTAIN AS PER REGULATION | Anand | 6
2 | KOMALBEN MANGALSING DANGI, MOTA HATHIDHARA AAMBLA FALIYA, Tal-Limkheda, Dist-Dahod |  |  | 2022-04-02 | FHO |  |  | NEAR THE HT LINE OF PANIVELA AG FEEDER, THE GIRL CLIMBED ON THE KHAKHRA TREE AND THEN TRIED TO CUT DOWN THE BRANCHES OF KHAKHRA TREE. IN RESULT BRANCHES FALLEN ON THE R PHASE OF 11KV PANIVELA AG FEEDER LIVE WIRE AND POWER CAME THROUGH THE BRANHES AND THE GIRL GOT ELECTROCUTED | AWAITED | NA | NA | MAINTENANCE OF 11 KV HT LINE IS CARRIED OUT. ALL THE TREE BRANCHES WHICH WERE NEARBY THE LINE ARE REMOVED. | Godhra | 6
3 | Karansinh R Rathod, NR. CANAL AT VISANAGAR, Vill-EKALVELU, Tal-Thasra, Dist-Kheda |  |  | 2022-04-05 | NFHD |  |  | THERE WAS FEEDER FAULT ON 11 KV MULIYAD JGY FDR, AFTER ISOLATING FAULTY SECTION, HE STARTED PETROLLING OF LINE AND FOUND 11 KV PIN POLE TOP FITTING TILTED NEAR CANAL AT VISNAGAR, VILL- EKALVELU, HE CLIMBED POLE TO RECTIFY FAULT. AS HE TOUCHED THE TOP FITTING HE GOT ELECTROCUTED. HE HAS VIOLATED THE SAFETY NORMS. | Earthing should be done and safety article must be used while working on line | Proper Earthing should be done on both side while working on line and Safety article should be used while working on line | yes | it is instruced line staff to carried out work after proper Erthing work and safety article must be used by line staff | Nadiad | 3
4 | LALSINH DALELSINH RATHOD, PAULTRY FARM, NEAR VAIJANATH MAHADEV TEMPLE, Vill/Tal-Matar, Dist-Kheda |  |  | 2022-04-15 | FHO |  |  | THE VICTIM WAS MAINTENING THE WATER SPRAYER SYSTEM OF PAULTRYFARM FROM ROOF OF THE UNDER LINE CONSTRUCTION. AS THE VICTIM STOOD UP AND ELECTRICUTED WITH ACCIDELTLY CONTACT WITH LIVE HT LINE | AWAITED | NA | NA | Notice has been issued wide letter no KHD/T/2271/16.04.2022 to remove construction below the line | Nadiad | 6
5 | MEHULKUMAR PRADHYUMANSINH BARIYA, Hirapura Lat, Vill-Vadol, Tal-Mahemdabad, Dist-Kheda |  |  | 2022-04-16 | NFHO |  |  | Victim climbed on Double Pole structure to find their buffalos., suddenly his right hand touched live wire of 11KV Ranchhodpura AG feeder ( as per his father's statement). Due to contact with live wire he got electrocuted. | Victim climbed on Double Pole structure to find their buffalos., suddenly his right hand touched live wire Due to contact with live wire he got electrocuted. | have to avoid unauthorized work | yes | Vistim was instructed to avoid unauthorized work with electric line | Nadiad | 6
6 | SHOKAT IMAMSHA DIWAN, Vill-SANAPURA, Tal-Karjan, Dist-Vadodara |  |  | 2022-04-20 | NFHO |  |  | From the observation of the place it seems that HT line was passing between Land survey No-208,Sanapura vill.sim. victims father was cutting grass in the farm and his boy was walking around in the farm. Then the victim boy accidentally touched his left hand with live conductor passing over the said farm and victim got electrocuted. | Awaited | NA | NA | CONDUCTOR RESTRING WORK COMPLETED AND POLE PLUMBING WORK COMPLETED | Baroda O&M | 2
7 | Viniben Salambhai Raval, Raval Faliya, VILL-Tarsang, Tal-Shahera, Dist-Panchmahal |  |  | 2022-04-22 | FHO-Pvt |  |  | As per statement of eyewitness, victim along with eyewitness were going to cut grass in the field of Vinshu sakal Raval. Moving ahead in the field, victim came in contact of the fencing erected along the field of Vinshu sakal Raval and fell on the ground | AWAITED | NA | NA |  | Godhra | 8
8 | BARIYA RAMANBHAI HIRABHAI, PARMAR PRAVINBHAI DHULABHAI HOUSE CON NO-07411/50018/6, Vill-Maghasar, Tal-Halol, Dist-Panchmahal |  |  | 2022-04-22 | FHO-Pvt |  |  | AT THE TIME OF ACCIDENT VICTIM WAS HANGING WET CLOTHES ON IRON WIRE THIS WIRE IS STRUNG BETWEEN TWO PILLAR INSIDE CONSUMER PREMISE THOS TWO PILLARS ARE CONNECTED TO METAL PIPES AND METAL SHED STRUCTURE DUE TO SUB STANDARD AND HAZARDUS INTERNAL WIRING WITH MANY JOINTS. THE CURRENT LEAKAGE TOOK PLACE AND VICTIM ELECTROCUTED | AWAITED | NA | NA | NOTICE ISSUED TO CONSUMER. CONNECTION WAS DISCONNECTED AFTER TAKING NEW TEST REPORT MAKE CONNECTION LIVE. | Godhra | 8
9 | RAHUL VIJAYBHAI TALPADA, MANEK CHOK, Vill/Tal-Nadiad, Dist-Kheda |  |  | 2022-04-26 | NFHO |  |  | Victim was putting 'Tadpatri' on wooden bamboo between two shops namely 'Bihari Samosa' and 'Janta Snake'. All of a sudden his head touched live conductor of 11KV Santram feeder passing over that area and victim got electrocuted. | Unauthorized work should not carried out nearby line | Unauthorized work should not carried out nearby line |  | Unauthorized work should not be carried out nearby line | Nadiad | 6
10 | Chauhan Jigneshbhai Vanrajbhai,Joshi Faliya,Vill-Chalali,Ta-Kalol,Dist-Panchmahal |  |  | 2022-05-10 | FHO |  |  | While doing the work of Mandap decoration at Village Chalali , victim came in contact with live conductor of 11 KV Line got electric shock and met with non-fatal accident. A non-fatal accident is converted in fatal on dtd.14.05.2022 | AWAITED | NA | NA | NOTICE ISSUED TO CONTRACTOR FOR MANDAP DECORATION. NEW EARTHING PROVIDED ON POLE . LINE MAINT. IS ALSO CARRIED OUT | Godhra | 6
11 | Baffalo of Bhikhabhai Chandubhai Parmar,behind dairy Vill-Sandesar,Ta-Kathlal,Dist-Kheda |  |  | 2022-05-13 | FA |  |  | Due to heavy wind flow, A neem tree branch fallen on LT line so one conductor broken and fallen on ground where Buffalo was tied, suddenly baffalo came in contact with live wire and get electroduced. | AWAITED | NA | NA | broken wire was removed | Nadiad | 1
12 | Kanchanbhai Chandubhai Damor,Tatarpura To Kellanpur Road Vill-Tatarpura,Ta/Dist-Vadodara |  |  | 2022-05-16 | NFHO |  |  | Shriji electrical contractor labour(victim) was working on LT line stringing of fail transformer of shri bhagvanbhai patel agriculture of tatarpura village. This LT line & Pipariya Ag HT line cross each other on pole No. B14. During stringing LT wire touch with live wire of 11kv pipriya ag line and victim got electrocuted. | Awaited | NA | NA | INSTRUCTION TO THE CONTARCOR DDURING THE WORK MUST BE WARED SAFETY ARTICLES | Baroda O&M | 2
13 | Shri K B Makwana (LI),Parvadi charel faliu Vill-Parvadi,Ta-Godhra,Dist-Panchmahal |  |  | 2022-05-17 | NFHD |  |  | Mass maintance program was arrnged on 11 kv vadelav jgy & 11 kv vavdi ag fdrs.The victim was doing rejumpering on dodp structure of 11 kv vavdi ag fdr nr charel faliu. The psc pole of 11 kv dahod rd fdr damaged by jcb which carrying pipe line work. The conductor of Dahod road fdr touched Vavdi fdr, on which victim was doing re-jumpering work. Thus victim got electrocuted. | AWAITED | NA | NA | NEW PSC POLE ERECTED AND CONDUCTOR RESTRINGING WORK DONE. | Godhra | 2
14 | Machhi Kalpesh Naginbhai,Vill-Malod,Ta-Karjan,Dist-Vadodara |  |  | 2022-05-23 | NFHD |  |  | 11kv Nareshwar AG On fault, victim with staff was petrolled the line and found conductor broken on sim opposite malod vill. Taken line clear for all parallel feeder and confirm to line was discharged. There after all 3 phase made short and earth befor conductor joining. During conductor joining work, the back power from other source might have passed in 11KV line and victim was electrocuted. | Awaited | NA | NA | NO CAUSE FOUND FOR BACK CURRENT | Baroda O&M | 8
15 | Baraiya Dilipbhai Rameshbhai,Paramjyot Society Vill-Limbasi,Ta-Matar,Dist-Kheda |  |  | 2022-05-23 | FHO-Pvt |  |  | On date23.05.2022, time 20:45 approx. victim Shri dilipbhai rameshbhai baraiya was going to bath in their bathroom at own home. During bath work victim accidently touched the open lamp holder which placed in bathroom corner. so victim got electric shock. | AWAITED | NA | NA | Private premices | Nadiad | 8
16 | Buffalo owner Geetaben B Vaghri,Vill-Gada,Ta-Sojitra,Dist-Anand |  |  | 2022-05-23 | FA |  |  | on date 23.05.2022 at approx. 14:15 hrs 2 no's of buffalo of gitaben bahadurbhai vaghari. ware grassing near water canal village gada by her husban bahadurbhai bachubhai vaghari during grassing both buffalo went into canal to drink water. There was a broken conductor of open LT line due to tree branch fallen on it. At that time both buffalo came in contact with live wire and died. | Awaited | NA | NA | REBINDING OF CONDUCTOR & RESTRING OF LT LINE | Anand | 1
17 | Patel Dipakbhai Dahyabhai,Modaj Sim Vistar Vill-Modaj, Ta-Mehmdabad,Dist-Kheda |  |  | 2022-05-28 | FHO |  |  | Non Fatal Accident Converted to Fatal Electrical Accident. victim fiddling with the stay wire of DODP Structure. it is seen at site that stay wire cut near the anchor rod. While fiddling with the stay wire accidentally contacts with live conductor and he got electrocuted. | AWAITED | NA | NA | Broken stay wire removed and provide new stay | Nadiad | 6
18 | Bullock of shri Adesinh mangalsinh,Vill-kandach,Ta-Kalol,Dist-Panchmahal |  |  | 2022-06-03 | FA |  |  | As per site visit it is found that on dated 3-06-2022 @10:00 hrs a fatel animal accident occurred to BULLOCK of shree adesinh mangalsinh of village kandach service line was shorted got leakage current path through the G I WIRE in the service wire | AWAITED | NA | NA | FUSE PROVIDED. EARTHING IS REACTIVATED. NOTICE OF DANGER SIGN BOARD IS PROVIDED | Godhra | 2
19 | Natvarbhai Karshanbhai Prajapati,near pramukh poojan residency,Vill-Kasor,Ta-Anand,Dist-Anand |  |  | 2022-06-05 | FHO |  |  | WHILE PICK UP MANGO FROM MANGO TREE WITH THE HELP OF IRON ROD , IRON ROD ACCIDENTALLY CONTACT WITH 11 KV LINE AND GOT ELECTRIC SHOCK AND DIED ON THE SPOT | Awaited | NA | NA | Line Maintenance work completed | Anand | 6
20 | Maheboobhai Rasulbhai khokhar,opp. 66kv traj ss Vill-Traj,Ta-Matar,Dist-Kheda |  |  | 2022-06-07 | NFHD |  |  | On dt:-07.06.2022, time approx. 08:00 pm Maheboobbhai Rasulbhai khokhar(ALM) was o duty to attend the feeder fault of 11kv Manav jgy feeder with line staff k.p.bhavsa(LM), MP Damor(vs ea) ad T D Malek(EA). During petrolling they found jumper of 11kv manav burnt at Loc 12. K P Bhavsar taken LC & M R Khokhar was replacing jumper & other 2 line staff were on ground. During jumper work he was electrocuted as there was power of two different feeders on the said pole. | AWAITED | NA | NA | instructed to use safety tools and awarenes s program was carried out | Nadiad | 3
21 | BUFFALO of Hiteshbhai Karamshibhai Bharvad, Kachhai sim vistar,Vill-Kachhai,Ta-Mehmadavad,Dist-Kheda |  |  | 2022-06-09 | FA |  |  | DUE TO HEAVY WIND TREE BRANCH FALLEN ON OPEN LT CONDUCTOR ,SO PHASE TO PHASE SHORTED AND CONDUCTOR BROKEN.HENCE BUFFALO CAME TO CONTACT WITH BROKEN LIVE LT OPEN WIRE AND GOT ELECTROCUTED AND DIED. | AWAITED | NA | NA | LT line maintenance is carried out | Nadiad | 1
22 | Sohilkhan Yasinkhan Pathan,Kolivad,Vill-Shahera,Ta-Shahera,Dist-Panchmahal |  |  | 2022-06-13 | FHO-Pvt |  |  | No leakage current path found in preliminary investigation. There is no legal electric connection found in the shop(location), outside which the accident occured. Also no eyewitness were available though the location is in the middle of the market. Detail | AWAITED | NA | NA | Notice issued to the shop owner regarding illegal extension of Shed near the LT PSC Pole. | Godhra | 8
23 | Sanjaybhai Rameshbhai Prajapati ,Pandya Faliyu,Vill-Dhamod,Ta-Lunavada,Dist-Mahisagar |  |  | 2022-06-13 | FHO-Pvt |  |  | At site, Load side private wire runing alongwith the service wire found demaged and as per eyewitness the sparking was seen by victim in wiring and may come in contact live wire and while removed the same may got electric shock. | AWAITED | NA | NA | Nil | Godhra | 8
24 | COW OWNER SHRI JALAMSINH RAMSINH PARMAR, Vill-Sonipur,Ta-Halol,Dist-Panchmahal |  |  | 2022-06-14 | FA |  |  | It is found that due to service line short of Ramanbhai M Chauhan having consumer No. 07342100609 leakage current pass through LT line to transformer center and current circulate to earthing wire and same time cow which are passing near to transformer and | AWAITED | NA | NA | TC AND LINE MAINT. IS CARRIED OUT. EARTHING OF TC AND POLE IS REACTIVATED. SERVICE LINE OF CONSUMER IS REPLACED. | Godhra | 2
25 | Cow of Vohra Idrishbhai Rasulbhai,Pariej-kheda road,Vill-Pariej,Ta-Matar,Dist-Kheda |  |  | 2022-06-20 | FA |  |  | LT abc4wire insulation damaged and leakage current occured and ccident took place | Awaited | NA | NA | Insulated wire replaced. Two pole erected under existing line and raised height of line. | Anand | 2
26 | HE BUFFALO of Mansuri Mohhmad sajid Ayubhusen, Near Rabiyapark tc,Vill-Dabhoi,Ta-Dabhoi,Dist-Vadodara |  |  | 2022-06-20 | FA |  |  | On dtd -20-06-2022 he buffalo was grazing in common plot of rabiya park and passing near TCDP of rabiya park tcsuddenly buffalo came in contact with GI wire of PSC pole earthing and gets eloctructed | Awaited | NA | NA | Earthing of Transformer Done and faulty ELCB of Consumer is Replaced by Consumer | Baroda O&M | 2
27 | Cow of Mahendrasinh Dolatsinh Mahevar,Somnath Faliyu,Vill-Janod,Ta-Balasinor,Dist-Mahisagar |  |  | 2022-06-20 | FA |  |  | Tree branch fallen on the opern Street light wire and Street light wire touched with the supporting angle nad Earthing wire was tied with this angle.Due to rainy water on the ground leakage current paased in ground and Cow (Tied near by LT PSC pole) got s | AWAITED | NA | NA | Proper Earthing is done | Nadiad | 2
28 | SHE COW, OWNER NAME BHARVAD RAJUBAI NAGJIBHAI, Near Saraswati Nagar TC,Vill-Mehmadavad,Ta-Mehmadavad,Dist-Kheda |  |  | 2022-06-23 | FA |  |  | ON DT.:23.06.22 ABOUT 16:05 COW EATING GRASS IN FIELD COME IN CONTECT WITH TCDP EARTHING WIRE AND GET ELECTROCUTED AND DIED AT SITE AND ELECTRICAL ACCIDENT OCCURED... | AWAITED | NA | NA | LT maintenance was done and earthing provided. Leakage current vanished from earthing. | Nadiad | 2
29 | Akashbhai Rajeshbhai Zala,near sumar logistic,Vill-Hariyala,Ta-Kheda,Dist-Kheda |  |  | 2022-06-26 | FHO |  |  | Akashbhai Rajeshbhai Zala was passing with ladder (Height 10 mtr Approx) towards the live wire. and accidentally came in contact with 11 KV Sai Feeder and electriduted. Victim was died on 30 June 2022 | AWAITED | NA | NA | Unauthorized work should not be carried out nearby line | Nadiad | 6
30 | Javanbhai Sukhabhai Parmar,at his Farm,Vill-NIRMALI NA MUVADA DUDHATHAL,Ta-Kapadwanj,Dist-Kheda |  |  | 2022-06-26 | FHO-Mech |  |  | ON DATED 26.06.2022 AROUND 18:30 HRS HEAVY WINDFALL, RAIN AND THUNDERSTORM CAME AT THE AREA OF DUDHATHAL VILLAGE AND IT’S PETAPARA NIRMALI NA MUVADA. DUE TO THAT A BIG TREE NEARER TO VICTIM’S KACHHA HOUSE (CHHAPRA) WAS ACCIDENTALLY FALLEN ON LT LINE PSC | AWAITED | NA | NA | For safty purpose transformer power supply made off | Nadiad | 7
31 | Sindhi Bachubhai Hasanbhai,near Anugrah Hospital,Vill-Karjan,Ta-Karjan,Dist-Vadodara |  |  | 2022-06-27 | NFHO |  |  | THE VICTIM CLIMBED THE TREE TO CUT THE BRANCHES OF THE TREE FOR GOAT FODDER WITH IRON-HANDLED CUTTER WHICH PASSES THE HT LINE OF 11 KV HANDOD JFY FEEDER OVER THE TREE. SUDDENLY,AN IRON BAR IN THE VICTIM'S HAND CONTACTED WITH THE LIVE CONDUCTOR PASSING OVE | Awaited | NA | NA | PARTY SIDE FAULT | Baroda O&M | 6
32 | Gohel Bhavnaben Sureshbhai,kamal faliyu,Vill-Baroda,Ta-Matar,Dist-Kheda |  |  | 2022-06-27 | FHO-Pvt |  |  | On date:-27.06.2022 victim was fill up the water through electic motor. during this work victim was connect folding pin of motor and got electric shock and died on the spot | AWAITED | NA | NA | Private premices | Nadiad | 8
33 | Buffalo of Solanki Pankajsinh M,Vill-Bahi,Ta-Sehera,Dist-Panchmahal |  |  | 2022-06-28 | FA-Pvt |  |  | The Place at where the victim (Buffalo) laid down at the time of site visit, was approax 2 mtr away from the existing AG LINE(4-W ABC) of Sakariya AG Feeder. It is also noted that the farm in which the said accident occured was covered by the fencing (iro | AWAITED | NA | NA | Notice issued to the farm owner regarding covering of PSC pole by the fencing | Godhra | 8
34 | Himnashubhai Babubhai Makwana,near amdavadi bajar,Vill-Nadiad,Ta-Nadiad,Dist-Kheda |  |  | 2022-06-30 | NFHD |  |  | WHILE WORKING ON 11 KV U/G CABLE WHICH IS DISCONNECTED FROM 11 KV LINE, WHILE WORKING ON CABLE AFTER 1 HOURS SUDDENLY FIRE FLAME COME OUT FROM CABLE AND HIMNSHUBHAI B MAKWANA SCARED DUE TO SUDDEN FIRE AND NON FATEL ACCIDENT CASE MADE | AWAITED | NA | NA |  | Nadiad | 4

## MG SoP 03
Name of Distribution Licensee: M G V C L
Quarter : Q-I (APRIL-MAY-JUNE 2022)
Year: 2022-23
REGISTER FOR COMPILING THE COMPLAINTS CLASSIFICATIONWISE Q-I 2022-23
Performa SoP 003 B: |  |  |  | APPENDIX-B (already in the SoP regulation)
Classification | Nature of Complaints | Pending complaints of previous qtr. | Complaints received during the qtr. | Total Complaints =2+3 | No. of Complaints redressed during the quarter. |  |  |  |  | Balance Complaints to be redressed. (4) – (9)
[5 empty] | In stipulated time |  | Beyond stipulated time |  | Total (5) to (8)
[5 empty] | Within 50% of stipulated time. | Within stipulated time. | Up to double the stipulated time | More than double the stipulated time
| 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10
A(i) | Loose Connection | 0 | 66421.4544 | 66421.4544 | 32485.3374 | 33936.117 | 0 | 0 | 66421.4544 | 0
A(ii) | Intruption due to line Break down | 0 | 44122.9769 | 44122.9769 | 23249.2125 | 20873.7643 | 0 | 0 | 44122.9769 | 0
A(iii) | Intruption due to T/C Fail | 0 | 8573.1338 | 8573.1338 | 5985.1003 | 2588.0334 | 0 | 0 | 8573.1338 | 0
B(i) | Quality of power supply,ordinary case which require no Augmentation | 0 | 6451.1369 | 6451.1369 | 4049.3996 | 2401.7372 | 0 | 0 | 6451.1369 | 0
B(ii) | Quality of power supply,ordinary case which require Augmentation | 0 | 4232.3256 | 4232.3256 | 2520.2324 | 1712.0931 | 0 | 0 | 4232.3256 | 0
C(i) | Meters- Stoped/Defective meter | 0 | 10470.4944 | 10470.4944 | 5824.5621 | 4645.9323 | 0 | 0 | 10470.4944 | 0
C(ii) | Meters- Billing on average basis for > two bills | 0 | 5661.8965 | 5661.8965 | 3445.6019 | 2216.2946 | 0 | 0 | 5661.8965 | 0
D(i) | Over head lines - loose wires | 0 | 4932.4394 | 4932.4394 | 2722.7826 | 2209.6568 | 0 | 0 | 4932.4394 | 0
D(ii) | Over head lines - in adiquate ground clearance | 0 | 1793.4482 | 1793.4482 | 1311.254 | 482.1943 | 0 | 0 | 1793.4482 | 0
E(i) | Bills- for current bills where no addl information required | 0 | 5244.2523 | 5244.2523 | 3278.4396 | 1965.8127 | 0 | 0 | 5244.2523 | 0
E(ii) | Bills- for current bills where addl information required | 0 | 2960.5223 | 2960.5223 | 1683.8447 | 1276.6775 | 0 | 0 | 2960.5223 | 0
F(i) | Service connections- where extention of mains is not required | 0 | 9249.7539 | 9249.7539 | 6237.9832 | 3011.7707 | 0 | 0 | 9249.7539 | 0
F(ii) | Service connections- where extention of mains is required | 0 | 5253.2993 | 5253.2993 | 2594.7805 | 2658.5188 | 0 | 0 | 5253.2993 | 0
F(iii) | Service connections- Modification in connected load | 0 | 2701.6298 | 2701.6298 | 1157.3522 | 1544.2775 | 0 | 0 | 2701.6298 | 0
F(iv) | Service connections- Name change/reconnection | 0 | 3023.7969 | 3023.7969 | 1571.1329 | 1452.664 | 0 | 0 | 3023.7969 | 0
G | Refund of amount due inregard to temp conn | 0 | 556.3487 | 556.3487 | 324.8441 | 231.5046 | 0 | 0 | 556.3487 | 0
H | Others | 0 | 22218.0907 | 22218.0907 | 12306.4203 | 9911.6704 | 0 | 0 | 22218.0907 | 0
| TOTAL | 0 | 203867 | 203867 | 110748.2806 | 93118.7194 | 0 | 0 | 203867 | 0

## MG SoP 04
Name of Distribution Licensee: M G V C L
Quarter : Q-I (APRIL-MAY-JUNE 2022)
Year: 2022-23
Performa SoP 004 : Publicity carried out while displaying the contact details of consumer complaints centers
Particulars should also cover the details of consumer awareness program conducted, advertisement done through various media like TV, newspaper, radio, pamphlets & booklet distributions, Displays etc. The development of website and any medium through which public education is carried out can be included.
Sr. No | Actions or steps carried out by distribution licensee towards public awareness in the quarter | Likely number of consumers influenced
1 | RTI Officers Name is displayed at customer care centre on each office | 3415796
2 | Necessary information regarding time schedule for new connection and solving complaints is display on the board. | 3415796
3 | Contact nos. of various officers of the company for emergency contact is also displayed at customer care centre. | 3415796
4 | Displayed safety posters at various S/dn,Divisions | 4180
5 | Safety Meeting with Line Staff at various S/dn,Divisions on Every Monday (Line staff influenced) | 14200

## MG SoP 05
Name of Distribution Licensee: M G V C L
Quarter : Q-I (April-May-June- 2022)
Year: 2022-23
Performa – SoP 005 B: Action taken report by the Redressal Committee
Sr. No | Month | Date and Time Meeting conducted | No of complaints registered at the meeting | No. of complaints pending at the end of the meeting
1 | 1st Month of the quarter (April'22) | NIL | NIL | NIL
2 | 2nd Month of the quarter (May'22) | NIL | NIL | NIL
3 | 3rd Month of the quarter (June'22) | 28.06.2022 11:30 Corporate mgvcl | 1 | 0

## MG SoP 06
Name of Distribution Licensee: M G V C L
Quarter : Q-I (April-May-June- 2022)
Year: 2022-23
Performa SoP 006: Failure of Distribution Transformer
Sr. No. | Name of Circle | Nos. of existing Distribution Transformers at the start of the quarter / year | Nos. of Distribution Transformers added during 1st quarter / year (2022-23) | Total number of Distribution Transformers on June'22 | Total number of Distribution transformer failed | % failure rate of Distribution transformer
|  | A | B | C=A+B | D | H = (D)*100/C
1 | Baroda OM | 51746 | 719 | 52465 | 541 | 1.0312
2 | Baroda City | 8998 | 90 | 9088 | 13 | 0.14305
3 | Anand | 24140 | 289 | 24429 | 166 | 0.67952
4 | Nadiad | 32037 | 305 | 32342 | 298 | 0.9214
5 | Godhra | 57710 | 861 | 58571 | 818 | 1.3966
| MGVCL | 174631 | 2264 | 176895 | 1836 | 1.0379

## SoP008
Name of Distribution Licensee: M G V C L
Quarter : Q-I (April-May-June- 2022)
Year: 2022-23
Performa SoP 008: Sample Test result for Neutral Voltage
Compliance Sample Test Report for Neutral Voltage
-1 | -2 | -3 | -4 | -5 | -6
Sr. No | Category of consumers | Sample Size | Standard specified in regulation | Deviation of results from the sample test (Numbers) | % age compliance
|  | (Numbers) |  |  | (6) = (5)*100/(3)
| LT consumers | 1441 | 2% | 0 | 0
1 | Domestic | 1023 | 2% | 0 | 0
2 | Commercial | 242 | 2% | 0 | 0
3 | Industrial | 23 | 2% | 0 | 0
4 | Agricultural | 143 | 2% | 0 | 0
5 | Public water works | 10 | 2% | 0 | 0
| HT consumers |  | 2%
6 | HT industrial | 5 | 2% | 0 | 0

## SoP009
Name of Distribution Licensee: M G V C L
Quarter : Q-I (April-May-June- 2022)
Year: 2022-23
Performa SoP 009: Sample Test result for Voltage variations
Compliance Sample Test Report for voltage variations
-1 | -2 | -3 | -4 | -5
Voltage Level | Sample Size (numbers) | Limit or prescribed standard | Deviation of results from the sample test (Numbers) | % age compliance
(5) = (4)*100/(2)
Low Voltage | 56 | +6% to -6% | 0 | 0
High Voltage | 24 | +6% to -9% | 0 | 0
Extra High Voltage | 1 | +10% to -12.50% | 0 | 0

## SoP010
Name of Distribution Licensee: M G V C L
Quarter : Q-I (April-May-June- 2022)
Year: 2022-23
Performa SoP 010: Sample Test result for Harmonics
Compliance Sample Test Report for Harmonics
-1 | -2 | -3 | -4 | -5 | -6
Sr. No | Category of consumers | Sample size (Numbers) | Limit or standard prescribed | Deviation of results from the sample test (Numbers) | %age compliance
(6) = (5)*100/(3)
1 | LT consumers | 33 | 3.5% | 0 | 0
2 | HT consumers | 4 | 3% | 0 | 0
3 | EHT consumers | 1 | 3% | 0 | 0
Note: The licensee shall also submit along with the above harmonic data, the records of customer wise drawls of harmonic currents measured at various strategic points.
The formats SoP 008, SoP 009 and SoP 010 have to be sent annually.
For the purpose of annual submissions, the year end has to be considered as the end of December month of a particular year.

## MG SoP 11A
Quarter : 1 (Apr-May-Jun '22)
SoP 011 –A: System Average Interruption Frequency Index (SAIFI)
Sr. No | Month | Ni - Total no of customers for each momentary interruptions | NT - Total no of customers served |  |  | Past year corrosponding Month
1 | 2 | 3 | 4 | 5 | 6=5/4 | 7
1 | April' 22 | 3098473 | 3418613 | 7942450 | 2.3233 | 2.27
2 | May' 22 | 3237978 | 3408691 | 12756829 | 3.7424 | 4.98
3 | June' 22 | 3248282 | 3415796 | 16622137 | 4.8663 | 5.39
|  |  | 10243100 | 37321416 | 3.6436 | 4.21

## MG SoP 11B
Quarter : 1 (Apr-May-Jun '22)
SoP 011 – B System Average Interruption Duration Index (SAIDI)
Sr. No | Month | ri = Restoration Time for each interruption event | Ni - no of interrupted customers for each sustained interruption event | ri * Ni – Total customer interruption Duration | ri=Restoration Time for each interruption event | Ni= No of Interrupted customers for each sustained Interruption | NT - Total no of customers served | Customer Interruption Duration |  |  | Past year corrosponding Months
[9 empty] | MINS. | HRS. | MINS. | HRS.
1 | 2 | 3 | 4 | 5= 3 X 4 | 3 | 4 | 5 | 6 | 7=6/5 | 8 | 9 | 10
1 | April' 22 |  |  |  | 554228 | 3098473 | 3418613 | 618866497 | 181.0285 | 0.12569 | 193 | 0.13403
2 | May' 22 |  |  |  | 1009918 | 3237978 | 3408691 | 1312394964 | 385.0144 | 0.26736 | 339 | 0.23542
3 | June' 22 |  |  |  | 1139499 | 3248282 | 3415796 | 1410431598 | 412.9145 | 0.28681 | 512 | 0.35556
[7 empty] | 10243100 | 3341693059 | 326.2384 | 5:26 | 348 | 5:48

## MG SoP 011C
Quarter : 1 (Apr-May-Jun '22)
SoP 011 – C: Momentary Average Interruption Frequency Index (MAIFI)
Sr. No | Month | Number of Momentary interruptions Imi | Nmi - Total no of customers for each momentary interruptions | NT - Total no of customers served |  |  | Past year corrosponding Month
1 | 2 | 3 | 4 | 5 | 6 | 7=6/5 | 8
1 | April' 22 | 16845 | 2874872 | 3418613 | 27716394 | 8.1075 | 8.22
2 | May' 22 | 18504 | 2945607 | 3408691 | 30229964 | 8.8685 | 10.85
3 | June' 22 | 20746 | 3028421 | 3415796 | 33334182 | 9.7588 | 10.74
|  |  |  | 10243100 | 91280540 | 8.9114 | 9.94

## MG SoP - 13
Name of Distribution Licensee: M G V C L
Financial Year: 2022-23
Quarter : Q-I (Apr-May-Jun-2022 )
Performa SoP 013: Faulty Meters Replacement
Consumer Category | No. of faulty meters at the start of the quarter | No. of faulty meters added during the quarter | Total no. of defective / faulty Meter | No. of faulty Meters repaired and replaced | No of faulty meters pending at the end of the quarter | Remark
| 1 | 2 | (3)=(2)+(1) | 4 | (5)=(3)-(4)
1 PHASE
MGVCL | 9127 | 30163 | 39290 | 32821 | 6469
3 PHASE
MGVCL | 1947 | 4429 | 6376 | 4756 | 1620

## MG SoP 16
Name of Distribution Licensee: M G V C L
Quarter : Q-I (April-May-June- 2022)
Year: 2022-23
Performa SoP 016: Compensation details
COMPENSATION DETAILS
Sr.No. | Event | Compensation | No of cases where compensation was given (in numbers) | Amt of compensation paid (in Rs.)
1 | Duty to provide supply | Rs. 50 per day of delay from the limit specified in the performance regulations | 0 | 0
| a) New Connection |  | 0 | 0
| b) Additional Load |  | 0 | 0
| c) Temporary supply |  | 0 | 0
| d) Shifting service connection |  | 0 | 0
| e)Transfer of service connection |  | 0 | 0
| f) Change in tariff category of consumer |  | 0 | 0
2 | Complaints in billing | Rs. 50 for non reply within the period prescribed in Regulations | 0 | 0
3 | Replacement of meters | LT- Rs. 25 per day of delay - maximum Rs.2,500 and HT - Rs. 250 per day of delay - maximum of Rs.5,000 | 0 | 0
4 | Interruption of supply | LT- Rs. 25 for every 6 hrs of delay- maximum of Rs. 500 and HT- Rs. 50 for every 6 hrs delay- maximum Rs. 1000/- | 0 | 0
5 | Voltage fluctuations and complaints | Rs. 50 for failure to visit or convey findings within the stipulated period | 0 | 0
6 | Responding to consumer's complaints | Rs. 25 for each day of delay- maximum Rs. 500 | 0 | 0
7 | Grievance Handling | Rs.25 for failure in handling grievance | 0 | 0
TOTAL |  |  | 0 | 0

## MG_SoP 012
Performa SoP 012 : System Losses at EHT/ 11 KV |  |  |  | APR-22 TO JUN-22
CALCULATION OF SYSTEM LOSSES AT EHT/ 11 KV
1 | Losses in 11 KV System and Connected Equipment
| i. | Energy Delivered into EHT/ 11 KV and LT Distribution System from EHT/ 11 KV SS (MUs) | A | 4071.7779 | Cum Total Sent incl EHT
| ii. | Energy Sold (Billed). EHT direct sales (MUs) | B | 704.4458 | Cum EHT Sold
| iii. | Energy Sold (Billed) in the 11 KV LT system (MUs) | C | 2917.5087 | Cum TTL Excl EHT-Sold
| iv. | Total Sales (MUs) | (B+C) | 3621.9545
| v. | Losses (MUs) | {(A) - (B+C)} | 449.8234
| vi. | % Losses | {(A) - (B+C)} X 100 / (A) | 11.0473

## MG_SoP 014
| Performa SoP 014: Statement Showing the ATC losses, collection efficiency and Billing Efficiency | [8 empty] | F.Y. 2022-23
| Quarter | Month | Units Input (MUs) | Units Billed (MUs) | Billing Efficiency % | Revenue Billed (Rs. Crs) | Revenue Collected (Rs. Crs) | Collection Efficiency % | Business Efficiency % | ATC Loss%
Sr No |  |  | A | B | C = (B/A)*100 | D | E | F = (E/D)*100 | G = (C*F)/100 | H = 100 - G
Q-I | Q-I | Apr'22 | 1355.6148 | 1145.597 | 84.5076 | 754.69 | 711.85 | 94.3235 | 79.7105 | 20.2895 | 210.0178 | 15.4924
Q-I |  | May'22 | 1416.0157 | 1225.6663 | 86.5574 | 819.46 | 794.07 | 96.9016 | 83.8755 | 16.1245 | 190.3495 | 13.4426
Q-I |  | Jun'22 | 1300.1474 | 1250.6913 | 96.1961 | 913.31 | 893.53 | 97.8343 | 94.1127 | 5.8873 | 49.4561 | 3.8039
Q-I |  | Q-I | 4071.7779 | 3621.9545 | 88.9527 | 2487.46 | 2399.45 | 96.4619 | 85.8054 | 14.1946 | 449.8234 | 11.0473
Q-II | Q-II | Jul'22 | 0 | 0 | #DIV/0! |  |  | #DIV/0! | #DIV/0! | #DIV/0! | 0 | #DIV/0!
Q-II |  | Aug'22 | 0 | 0 | #DIV/0! |  |  | #DIV/0! | #DIV/0! | #DIV/0! | 0 | #DIV/0!
Q-II |  | Sep'22 | 0 | 0 | #DIV/0! |  |  | #DIV/0! | #DIV/0! | #DIV/0! | 0 | #DIV/0!
Q-II |  | Q-II | 0 | 0 | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | 0 | #DIV/0!
Half Year | 2022-23 | Half Year | 4071.7779 | 3621.9545 | 88.9527 | 2487.46 | 2399.45 | 96.4619 | 85.8054 | 14.1946 | 449.8234 | 11.0473
Q-III | Q-III | Oct'22 | 0 | 0 | #DIV/0! |  |  | #DIV/0! | #DIV/0! | #DIV/0! | 0 | #DIV/0!
Q-III |  | Nov'22 | 0 | 0 | #DIV/0! |  |  | #DIV/0! | #DIV/0! | #DIV/0! | 0 | #DIV/0!
Q-III |  | Dec'22 | 0 | 0 | #DIV/0! |  |  | #DIV/0! | #DIV/0! | #DIV/0! | 0 | #DIV/0!
Q-III |  | Q-III | 0 | 0 | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | 0 | #DIV/0!
Q-IV | Q-IV | Jan'23 | 0 | 0 | #DIV/0! |  |  | #DIV/0! | #DIV/0! | #DIV/0! | 0 | #DIV/0!
Q-IV |  | Feb'23 | 0 | 0 | #DIV/0! |  |  | #DIV/0! | #DIV/0! | #DIV/0! | 0 | #DIV/0!
Q-IV |  | Mar'23 | 0 | 0 | #DIV/0! |  |  | #DIV/0! | #DIV/0! | #DIV/0! | 0 | #DIV/0!
Q-IV |  | Q-IV | 0 | 0 | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | 0 | #DIV/0!
Total | 2022-23 | Total | 4071.7779 | 3621.9545 | 88.9527 | 2487.46 | 2399.45 | 96.4619 | 85.8054 | 14.1946 | 449.8234 | 11.0473
Month | Cumm. Sent | Cumm. Sold | Month Sent | Month Sold
Apr'22 | 1355.6148 | 1145.597 | 1355.6148 | 1145.597
May'22 | 2771.6305 | 2371.2632 | 1416.0157 | 1225.6663
Jun'22 | 4071.7779 | 3621.9545 | 1300.1474 | 1250.6913
Jul'22
Aug'22 |  |  | 0 | 0
Sep'22 |  |  | 0 | 0
Oct'22 |  |  | 0 | 0
Nov'22 |  |  | 0 | 0
Dec'22 |  |  | 0 | 0
Jan'23 |  |  | 0 | 0
Feb'23 |  |  | 0 | 0
Mar'23 |  |  | 0 | 0