## INDEX
Uttar Gujarat Vij Company Limited, Mehsana
Performas for FY 2022-23
Performa No. | Particulars | Remarks/Report
SoP 001 | Fatal & Non Fatal Accident Report | Qtrly FY 2022-23
SoP 002 | Action taken report for safety measures complied for the accidents occurred | Half Yly. FY 2022-23
SoP 003 | Register for compiling the complaints classification wise | Qtrly FY 2022-23
SoP 004 | Actions or steps carried out by UGVCL towards public awareness in the year | Qtrly FY 2022-23
SoP 005 | Action taken report by the Redressal Committee | Qtrly FY 2022-23
SoP 006 | Failure of Distribution Transformer. | Qtrly FY 2022-23
SoP 011 A | System Average Interruption Frequency Index (SAIFI) | Qtrly FY 2022-23
SoP 011 B | System Average Interruption Duration Index (SAIDI) | Qtrly FY 2022-23
SoP 011 C | Momentary Average Interruption Frequency Index (MAIFI) | Qtrly FY 2022-23
SoP 012 | System Losses at EHT / 11 KV and below | Half Yly. FY 2022-23
SoP 013 | Meter Faults | Qtrly FY 2022-23
SoP 014 | Statement Showing the ATC losses, Collection efficiency and Billing Efficiency | Half Yly. FY 2022-23
SoP 015 | Release of New Connections | Half Yly. FY 2022-23
SoP 016 | Compensation Details | Qtrly FY 2022-23

## SoP001
Uttar Gujarat Vij Company Limited
QUARTER :- 2nd (July-22 to Sept.-22)
YEAR :- 2022-23
Performa - SOP 001 : Fatal and Non-fatal accident report for quarter ending
Sr. No. | Name of area | No.of accidents during the quarter |  |  |  |  | Cumulative since the first quarter of the current FY
|  | Departmental |  | Out side
|  | FH | NFH | FH | FA | NFH | FH | FA | NFH
1 | Sabarmati | 0 | 1 | 8 | 18 | 2 | 19 | 22 | 9
2 | Mehsana | 0 | 0 | 11 | 13 | 0 | 16 | 17 | 4
3 | Palanpur | 1 | 0 | 7 | 11 | 2 | 11 | 16 | 3
4 | Himatnagar | 0 | 0 | 13 | 15 | 2 | 16 | 23 | 4
| TOTAL | 1 | 1 | 39 | 57 | 6 | 62 | 78 | 20

## SoP002
SOP 002 Action taken report for safety measures complied for the accidents occurred Half yearly 2022-23 ( April-2022 to Sept-2022)
Sr. No. | Circle | Location of Accident | Name of Victim/Owner & Designation | Type of Accident NFH/FH /FA | Dept/ Outsider | Date | Name of supervisor & Designation | Detailed Reason of Accident | Finding of CEI/EI/ AEI | Remedies suggested by CEI / EI/ AEI in various cases | Whether the remedy suggested is complied | Action taken to avoid recurrence of such Accident. | Compensation Paid (in Rs)
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14
1 | HMT | Fudeda | R K Parmar E.A. | NFH | Dept. | 30.04.2022 | - | The work of tree cutting and AB Switch repairing was allotted to the line staff with tree cutting labours. Victim himself had got line clear from 66kv Babsar s.s. for 11kv mahor Ag feeder. After correct identification of feeder then after he had isolated AB switch loc no 150 for work of tree cutting and AB switch repairing. victim and co-worker reached at location no 185 for rejumpering of AB switch. after making local earthing victim climbed the pole with helmet and started to work. after completion of one jumper suddenly momentary power observed due to victim got electrocuted and fallen down from the pole, hence co-worker had shifted him CHC Vadali through 108 ambulance for primary treatment . after primary treatment victim shifted to parshva hospital Idar for further treatment. detail investigation under process.
2 | MSH | Kadi- Karanpur Area | (1)Goswami Nileshgiri Balvantgiri (ELE. AST.) (2)Sindha Ranjitsinh Ratansinh (J.E) | NFH(Elect) | Dept. | 04.04.2022 15:45 HRS | N/A | .: A non fatal human departmental electrical accident occurred to shri R R Sindha-JE Kadi city sdn & Shri N B Goswami while checking of LTMD connection of Ranchhodbha Bhikhabhai Patel at shriram ice factory located at karanpur area of kadi city.PTs of accucheck wiring was done on load side with RCCB installed by consumer & CTs of accucheck were connected in meter box.immidietly after wiring spark occurred at RCCB with loud sound & RCCB fired.Due to this spark N B Goswami E.A had burns on his face & his both hands.JE shri R R Sidndha also had burns on his left eye. And accucheck meter also seems to be damaged. .Accident occurred at about 15:45 hrs on dt 4/4/2022. After accident treatment was given to both victim at soham hospital and jiviba eye hospital at kadi and now both are Resting at their home. Health is good of both victims | CEI Report No:- 752/2022/30.05.2022 | As Per Cei Report Suggestion Consumer Should Use Isi Electrical Appliance With Use Of Rccb , Also From Discom Side Hand Glows & Face Shield Use While Checking | New RCCB and Fuse installed at consumer End | Private Premises NFH Ele. Dept Accident Occurred During Installation Checking Work
3 | MSH | Vithalapur | Rabari Bhagavanbhai Ramabhai | FA | Outsider | 05.04.2022 AT 10.45 AM | N/A | A shackle pole of 11 KV Sadatpura Ag Feeder whose two side 11 kV Line and one side stay set fitted and forth side opposite to outgoing line to the shackle pole a long stay set which is broken from bottom due to two Cows quarrel at there and by pressure of their or horns the long stay wire may broken and as a spring action on the top of pole touch with live conductor and thus the supply may came up to bottom side of stay wire where the two cows touched to the live stay wire and the both cow got electrocuted. This is primarily reason of accident but detail report is under investigation and it may submitted after DTR. | No |  |  | New 2 Pole Erected And Proper Stay Set Provided And Span Reduced After This 2 Pole Erection | 30000
4 | MSH | Kharasada,TA- Mehsana,Di-Mehsana | Solanki Jagdishbhai Devabhai,Age-47 years | FH | Outsider | 19.04.2022 17:30 Hrs. | NA | Victim was outsider who has climbed on LT pole near Hanuman temple of Kharasada village,without any prior permission of UGVCL. when, Victim was jointing a service cable of new connection on LT line and may have touched with open LT phase wire on LT pole and he was electrocuted.Then he fall down on the RCC wall below LT pole and got major injury on his head.Then after Victim was shifted to Mehsana civil hospital through 108 emergency.There after Hospital was declared the death of Victim. | CEI Report No:-1082/2022/25.07.2022 | Spread Awareness not to climb on HT/LT/TC by unauthorized person | Yes | People were educated to maintain safe distance from electrical network | 50000
5 | MSH | Dersana | Rajendrabhai Gangarambhai Vanmali | FH | Outsider | 28-03-2022 at 15-30 hrs to 16-00 hrs reported dated 20-04-2022 | NA | As per eye witness statement -A Fatal Human Out sider electrical accident occurred to Rajendrabhai Gangarambhai Vanmali , age 45 yrs, approx. ,near Rabari vas of Derasana village,Ta-Patan Di:- Patan on dtd 28-03-2022 at . 15:30 hrs. to 16.00 hrs. (Approx), while victim was fixing PVC made flexible at water out let side of single phase mono block motor was ON condition . Water may have spread on live motor/wiring and victim may be electrocuted and accident happened. | No |  |  | People were educated to install ELCB at their premises
6 | MSH | Boratwada,TA ;- HARIJ | THAKOR RAKESHJI KIRTIJI,19 Yrs | NFH(Elect) | Outsider | 26.04.2022 TIME APPROX. 09.45 | NA | A Non Fatal Human Out sider electrical accident occurred to Thakor Rakeshji Kirtiji , age 19 yrs , at Boratwada village,Ta Harij Di:- Patan on dt 26.04.2022 at . 09:45 am , while victim was removing marriage mandap structure his body part touch to 11 KV HT line and he get electrocuted from 11 KV Boratwada ag feeder emanating from 66 kv Harij s/s. | No |  |  | Peoples were educated to keep safe distance from distribution network and not to construct under line.
7 | PLN | Gangudara | Kalpeshsinh Shetansing Deval | FH | Outsider | 07.04.22 at 12.30 PM | N.A | A Fatal Human (Outsider) electrical accident occur to Shri Kalpeshsing Shetansing Deval While he was crossing the fencing of barbed wire which was done around farm of shri Thakor Anopsing Gangarsing,the victim came in with another steel fencing on which live current was passing. The victim came in contact with this live steel fencing and got electrocuted and died on the spot.The owner of farm shri Thakor Anopsing Gangarsing has used the power from his AG consumer number 70914/10096/3 on this steel fencing | CEI Approval pending
8 | SBT | Vastral | Rabari Ranchhodbhai Shartanbhai | NFH | Dept. | 2022-04-06 | NA | Program of village complaint and solar connection is given to Shri R S Rabari. So he went for installation of solar connection of Sharma Dharmendra Shrilal at Kalhar Developers, Plot no.B-01,02, Vastral , con. No.26412106014. While installing solar meter somehow due to two phase touch with each other, short circuit happened at incoming side and flash happened and dueto flash, face and right side hand of victim burnt. | Yet not received |  |  | N A | 0
9 | SBT | Bakrol | Patel Yagnik Jyotindrabhai | NFH | Dept. | 2022-04-06 | NA | Program of installation checking of LTMD CT operated connections checking is given to Shri Patel yagnik Jyotindrabhai, ALM with JE. While checking at Sahitya Ind estate, Polt no.12L, 12J, 12K consumer no.26426105830, accucheck is installed at consumer wiring, after taking test of meter approx at 11 a.m. while removing accucheck somehow blast happened due to electric short circuit and thus victim burnt on both hands. | Yet not received |  |  | N A | 0
10 | SBT | Kanipur | Parita Prabhubhai Katara | NFH | Outsider | 2022-04-07 | NA | As per intimation, the accused is trying to fetch fruits from tree, near bore and HT line passing . Victim use aluminium rod to fetch fruit from tree and unfortunately this rod contact with HT line and victim got electrocuted. | Yet not received |  |  | UGVCL not at fault | 0
11 | SBT | Aniyari | Kamshubhai Trikambhai Patel | FA | Outsider | 2022-04-08 | NA | As buffalo came in contact with the earthing wire as leakage current was passing GI wire got electrocuted and died. | Yet not received |  |  | PORBLEM RECTIFIED & NEW EARTHING PIPE PROVIDED | 15000
12 | SBT | Viramgam | Vishnubhai Madhavbhai Patel (E.A.VS) | NFH | Dept. | 2022-04-09 | K.L.Sadhu, ALM | As per site visit, it is found that the DO fuse of 11 kv Thori Ag fdr was disconnected which was appx. 1 km away from accident location. At site tail end is the 63 kva TC of consumer name Sindhi Haunbhai Jivabhai. From this TC to coming side fdr between 4th pole to 5th pole near 4th pole the earthing has been done by gethring three conductor through chain and other end of this earthing wire is connected to shackle pole stay wire at bottom side. The victim climbed on first pole near TC to take stringing of loose span conductors, On pole he removed binding wire from pin insulator to conductor at that time he may be got electrical junk and fallen down to ground. He is under treatment , DR said no any burns or shock symptoms on victim body. By taking record at 66 kv Fulwadi SS there was one tripping of 11 kv Thori Ag fdr recorded from 11:25 to 11:30 a.m. | Yet not received |  |  | MAINTENANCE WORK OF HT LINE WAS CARRIED OUT AND ACTION TAKEN AGAINST DEFAULTERS | 0
13 | SBT | Devdi | Chauhan Natvarsinh NarvatSingh | FH | Outsider | 2022-04-10 | NA | Due to Ceiling fan inside victim's house found sorted and the victim after taking bath came in contact with the sainting wire and got victim electrocution which was tie with the roof of metal sheets. Metal sheet was in contact with ceiling fan through metal hook. | Yet not received |  |  | ELCB SWITCH REPLACED BY CONSUMER AND SAME VERIFIED | 0
14 | SBT | Sarkhej | Chandrikaben Mansukhbhai Sonara | FH | Outsider | 2022-04-13 | NA | Victim was washing clothes at her home. At that time victim came in contact with electric motor and electrocuted. | Yet not received |  |  | No any fault from UGVCL side | 0
15 | SBT | Kantha | Bhajanlal Baluram Jat | FH | Outsider | 2022-04-27 | NA | Victim was fitting angle standing over the truck loaded with tiles which was parked under the line. At that time angle touched to live line of 11 kv Ambaji JGY which is on sufficient distance and victim electrocuted. | DUE TO ILLEGAL CONSTRUCTION AND CARELESSNESS OF VICTIM | To remove illegal construction | yes | 11 KV AMBAJI FDR MAINTANED & NOTICE GIVEN FOR REMOVE CONSTRUCTION UNDER LINE | 0
16 | MSH | MEDA ADRAJ | MUKESHKUMAR MANGALARAM POTLIYA | FH | Outsider | 12.05.2022 | N/A | A truck with Tanker was parked under line 11kv Jetpura JGY feeder. Victim climb on the top of truck and may be touched or get inducted by 11kv Jetpura JGY feeder's conductor and may be got electric shock. He fell on truck tank and died at spot. THE DETAIL REPORT UNDER INVESTIGATION. | No |  |  | People were educated to maintain safe distance from electrical network
17 | MSH | GERITA | VAGHELA SAVITABEN SURESHBHAI(victim) | FH | Outsider | 13.05.2022 | N/A | WHEN VICTIM SMT. VAGHELA SAVITABEN SURESHBHAI WAS HANGING WASHED WET CLOTHS ON VARAGANI WIRE WHICH WAS TIED BETWEEN ROOF IRON SHEET WOODEN SUPPORT INSIDE HOME,AT THAT TIME SHE WAS CAME IN CONTACT WITH VARAGANI WIRE AND GOT ELECTRIC SHOCK. | No |  |  | Service Joint is replaced by new and leackage problem is resolved | 50000
18 | MSH | Nagalpur ( Rabari vas village tc) | Desai Rameshbhai Nagajibhai | FA | Outsider | 19.05.2022 at 9:00 to 9:30hrs. | N/A | On date 19.05.2022,a buffalo passing nearer to transformer center of rabarivas village tc and came in contact with fencing of said tc and got electrocuted. Detailed cause of an accident is under investigation. | CEI Report No:-1070/2022/25.07.2022 | Regular maintenance of HT/LT/TC to be carried out | Yes | LT cable is replaced at tranformer | 30000
19 | MSH | Nadasa | Thakor Dashrathji Nathaji | NFH | Outsider | 21.05.22 | N/A | A marriage ceremony was going on in farm of Nadasa village and people were taking their food meanwhile heavy wind was flowing and a supporting iron pipe of porch inclined so victim was holding it. At that time due to heavy wind the iron pipe came in contact with live electric line (11kv Ajabpura Ag feeder) and electrocuted. The victim immediately admitted to Lions Hospital, Mehsana. | CEI Report No:- 978/2022/05.07.2022 | Aware Pepole to keep construction away from UGVCL network | Yes | People were educated to maintain safe distance from electrical network
20 | MSH | Mandotri (Khodiyar nagar area) Ta-Patan Dist-Patan | PARMAR ADITYA JIGNESHKUMAR (Out Sider) Resident of Vill-Sunok Ta-Unjha Dis-Mehsana | FH | Outsider | 27.05.2022 | N/A | On date 27.05.22, a marriage ceremony was going on at Mandotri village khodiyar nagar area and victim was dancing in the marriage cermony and he felt perspirated so to get cool air he tried to turn the pedestal fan to his side and after touching the pedestal fan he got electrocuted. The victim immediately admiitted to Dharpur Civil Hospital Patan and he was declared dead. | No |  |  | Pepole were educated to install ELCB for protection for leakage current and use of standard wiring to avoid this type of accident
21 | MSH | Ramapura | Thakor Ranjitji Shankarji | NFH | Outsider | 30.05.2022 | N/A | Today On 30/05/2022 at arround 7:15 in the morning, An electrical non fatal human outsider accident occurred to Thakor Ranjitji Shankarji at below 11 KV line new shop of Mahamadbhai near Ambika Soc TC, Bus stand road of village Ramapura of Detroj sdn. Accident occurred due to victim climbed on steel roof of shop to take materials of shop construction work where 11 KV line passes above shop which conductor touched with victim head and neck and passed from body to left leg knee with thrown to steel roof and burnt on neck, normal at head, left pair knee and right chick of face. After accident victim is admitted at Ramapura Champa Vijya Hospital by Villagers and victim is discharged after primary treatment. | No |  |  | People were educated to maintain safe distance from electrical network
22 | SBT | Kujad | Bharada Maheshkumar Makshibhai | FH | Dept. | 17.05.2022 | NA | Program of tree cutting of 11 kv Gopalcharan & 11 Kv Kujad ag is given to Shri Bharada Maheshkumar makshibhai, EA with 2 no. of apprentice LM. As per primary conversation with apprentice, early morning they have started tree cutting of 11 kv Gopalcharan feeder. At around 9.00 Shri M M Bharada told them, he is going for dismantling wire of dead line of 11 kv Kujad ag feeder. But at that time apprentice has denied to work without him and they all went for dismantling work. After reaching at location victim climbed on 11 kv Kujad ag feeder pole for dismantling the conductor. At that time 11 kv Kujad Ag feeder power is 1Q. After climbing on pole he has cut the side wire, but due to ACSR, one turn of conductor is not cutted, after that while cutting the top conductor he got electrocuted and fell down on ground. As per primery visit on the location, it is found that the line is not dead and LC is also not taken by him. He immediatly shifted to hospital and primary treatment is given but he expired on dtd.19.5.22 at 8.59 a.m. | Yet not received |  |  | N A | 0
23 | SBT | Tragad | Valjibhai Hirajibha Patidar | FH | Outsider | 17.05.2022 | NA | Information received through Sabarmati Police as on dtd.17.5.22 time 5.20 pm, A fatal human elect. Accd. Occurred as on 16.5.22 approx time 23.30 hrs of victim Shri Valjibhai Hirjibhai Patidar, as per eye witness statement that victim was turn on the tube light which was with the MS angle of shed and got electrocuted, primary investigation found that the live wire of tube light supply insulation got damaged and touched with the MS angle and leakage current passes through angle and ground, immediately refer to Sola civil hospital for treatment but doctor has declared dead. | Yet not received |  |  | since accident occurred in consumer's internal premise,so internal wiring of consumer's premise was rectified. | 0
24 | SBT | Chharodi | Pathan Sirajkhan Rahimkhan | FA | Outsider | 22.05.2022 | NA | on dtd..22.5.22, in morning hours almost 9.30a.m. there when buffaloes were passing from the farm of Mirkhan Valikhan Pathan at vill. Chharodi and at same time the conductor of 11 kv Iyava JGY feeder was broken due to heavy wind and fallen on the 2 nos of buffaloes passing below this HT line and came in direct contact with the live wire, got electrocuted and died. Feeder was in PF from 9.35 to 10.00 am. First tripping at 9.30 am. | Yet not received |  |  | NEW POLE ERECTED & RE STRINGING DONE | 30000
25 | SBT | Nandasan | Gamar Govindbhai Hirabhai | NFH | Outsider | 27.05.2022 | NA | Victim tried to step down from metal shed near his resident, constructed illegally under 11 kv line clearance from shed to line is approximately 1.5 meter and got in touch of 11 kv line passing above the shed and got shock and fell down from shed to ground. victim got injured and shifted to hospital after giving primary tratment | Yet not received |  |  | ILLEGAL CONSTRUCTION REMOVED NEARBY NETWORK | 0
26 | PLN | Bhildi | Siddhantbhai Narendrabhai Patel | FH | Outsider (Private Premises) | 13-05-22 @18:45 | NA | Victim was doing work of submersible motor winding in his shop name Shreeji Electric work. During this work victim got sock and fell down on floor. Then after shop neighbour shifted him at referal hospital and Doctor declare a dead. | CEI Approval pending
27 | PLN | Aseda | Harijan Kuberbhai Maghabhai | FA | Outsider | 16-05-22 @15:00 | NA | When Owner's cow grazing grass in owner's land (Vada), suddenly top outgoing conductor of 11KV Vadhaniya-AG from 66KV Rasana Sub Station broken and fall down on ground and touch to the cows leg and got electric shock and died | CEI Approval pending
28 | HMT | Savgadh (Dhandha) , Near bharat trading oxygen plant | Bharvad Lalabhai Malabhai | FA(BUFFALO) | Outsider | 05.05.2022 | NA | During site inspection , A Buffalo was found died below said JGY transformer center . At the time of inspection there was no any symptoms of leakage current found at incident location . Also all the earthings of transformer center was earthed through PVC Rigid pipe . | EARTHING WIRE WITHOUT EARTHING PIPE | PROVIDING EATHING | EARTHING PIPE PROVIDED | TC MAINTANANCE DONE AND EARTHING PROVIDED WITH INSULATED PIPE | 30000
29 | HMT | Modasa | ASARI VISHRAMBHAI SALUBHAI | FH | Outsider | 28.05.2022 | NA | On Dtd 28-05-22, Electrical Accident occurred to victim while ,he tried for sprinkling water on new C.C. block for masonary use. During that time, 1-ph 0.5 HP motor not started kept on water tank , so he tried to catch 2 wire(used in submesible motor winding) which was comming from his house wiring plug point, took in his right hand and hang to check power supply in motor, at that time open wire whose insulation of wire deteriorated part of wire came in contact with his hand and other side, his lag were directly in contact wet ground near water tank , so he got shock and died. Electrical accident occured in consumer's premises by his private wire. Hence, UGVCL is not responsible for this accident. | CEI PENDING
30 | HMT | UBHARAN | VAGHRI KISHANBHAI DINESHBHAI & VAGHRI BHALABHAI RAMESHBHAI | FH | Outsider | 25.05.2022 | NA | There is HT line of 11 kV Bhempoda AG feeder supplying power on group TC. Today, both victims came to the sight for MANDAP work for marriage function at Vaghri Maheshbhai Kalabhai house. Mandap was placed under HT line. Both victims were erecting 20 feet Iron Pipe for decoration work below HT line and touched to HT line. So, both got electric shock and electrocuted Nearby people took them to Hospital for treatment , but both were died. PM Report and police punchnama awaited. | VICTIM FAULT | VICTIM FAULT | VICTIM FAULT | MAINTENANCE CARRIED OUT HT LT RESTRINGING | FIRST-100000
31 | HMT | ZANHARIYA | SOLANKI MAHENDRASINH VIRAMSINH | NFH | Outsider | 30.05.2022 | NA | TThere is special AG connection of Solanki Vaghsinh Krishnasinh. Beside his connection, there was farm of Solanki Viramsinh Himmatsinh where construction was done under AG HT Line. While spraying water on under construction house, he came in contact with 11 KV Zankhariya AG fdr and his left shoulder touched and get shock. He is admitted to SHivalik Hospital, Bayad under Treatment. | CEI PENDING | CEI PENDING | CEI PENDING | MAINTENANCE CARRIED OUT HT LT RESTRINGING | NOT APPLICABLE DUE TO NFH
32 | MSH | Sunshi | Chamar Karshanbhai Kanabhai | FA | Outsider | 17.06.2022 | N/A | As on Dtd.17.06.2022,at 3.00 pm ,at Chamarvas village-Sunshi ta-Visnagar a buffalo of Chamar Karshanbhai Kanabhai tide near to LT line girder pole got electrocuted and died.a 4sqmm LT PVC cable along with GI wire was incoming from near by pole to LT girder pole.this cable was punctred and neautral of this cable was in contact with GI wire and gireder pole.at the same time in same LT line service cable of patel Amrutbhai Ganeshbhai was punctured and neutral became live, due to this leakage current was flowing on GI wire and Gireder pole.Buffalo was tied near gireder pole got electrocuted and died.The detail investigation is under progress. | CEI Report No:- 1143/2022/26.08.2022 | Maintenenace of Serivce to be done | Yes | LT line maintanance is done on 18.6.2022 and faulty cable were replaced.
33 | MSH | Limbodara | Owner Of Cow Gosmani Bachugiri Anandgiri | FA | Outsider | 13.06.2022 | N/A | When cow is going near the water tank (havada) for drinking water , the cow is touched with cage of transformer which is located near the water tank and cage of transformer is already touched with distribution box which is located on transformer center and leakage current found on distribution box and due to that the same leakage current found on cage of transformer and cow is touched with cage of transformer and got electrocuted and died on the spot. | No |  |  | For the Safety purpose and future accident prevention , transformer center shifting proposal is under process. | 15000
34 | HMT | KHODAMBA | COW OF PATEL HASMUKHBHAI VALABHAI | FA(COW) | Outsider | 12.06.2022 | NA | Fatal Electrcal Accident Occured to Cow (Owner -Patel Hasmukhbhai Valabhai) Under UGVCL Line 11KV Shamalaji AG Feeder pole No-41 During heavy rain on dtd.12.6.22 at 20:05 P.M. Accident occurred to Cow While heavy raining with wind , that time kite wooden stick touched with live 11 kv line conductor to lower part of G.I.Pin and V-cross arm and leakage Current passed through G.I.earthing wire which is deteroiated and disconnect from ground and bounded with pole,so leakage current passes through it and at that time cow came in contact with live wire,so Cow got Shock and died. | pole earthing not maintained properly | provide GI wire earthing with pvc pipe | yes |  | 30000
35 | HMT | Udepur | Gauswami Shardaben Mangalgiri | FH ELECTRICAL | Outsider | 13.06.2022 | Na | On dated 13.06.2022 around 4.00 pm victim was cutting grass in farm.4 wire Ag LT line passing to AG Connection of Goswami Keshavgiri Hirgiri,in such LT line spacers are provided.Due to heavy wind and heavy rain,one phase of conductor broken due heavy wind,as neem tree branches fallen on top LT Conductor and fallen on temporary private self made fencing of approx 1 to 2 feet for protecting forest animals (pig,blue cow)surrounding farm.At that time approx 100 mtr away victim got electric shocked while touched to this fencing.Then after victim was taken to private Navjivan hospital Bayad and after then to Bayad CHC for further treatment where doctor declared death. | CEI PENDING | CEI PENDING | CEI PENDING | MAINTENANCE CARRIED OUT HT LT RESTRINGING | 50000
36 | HMT | SIKA KAMPA | PAGI RAJUBHAI PUNABHAI | FA(BUFFALO) | Outsider | 13.06.2022 | Na | 5 BUFFALO AND 12 GOAT WERE GAZING NEAR FIELD OF SIKA KAMPA VILLAGE.DUE TO HEAVY WIND AND RAIN ONE PHASE WIRE OF LT AG 4 WIRE LINE CONDUCTOR BROKE DOWN AND FELL ON ONE BUFFALO .BUFFALO GOT ELECTODUCT AND DIED ON SPOT. | COMPANY FAULT | TO CARRIED OUT MAINTENANCE | YES | LT WIRE RE STRINGING & SPACER PROVIDED | NOT APPLICABLE,PM NOT DONE.
37 | HMT | DOLPUR | KHANT RASIKBHAI NATUBHAI | FA(BUFFALO) | Outsider | 13.06.2022 | Na | APPROX. 2.30 PM DURING HEAVY RAIN BUFFALO TIED WITH CHAIN NEAR PSC POLE.DUE TO RUST STAY WIRE PSC POLE WAS BROKEN BY SOME PERSON AND TIED WITH EARTHING WIRE.STREET LIGHT OF SUCH POLE NO ANY CONNECTOR PROVIDED BY GRAM PANCHAYAT AND DIRECTLY JOINT WITH STREET LIGHT CONDUCTOR THROUGH INSULATION JUMPAR WITHOUT ANY INSULATION TAPE.SAME TIME DUE TO HEAVY WIND LOOSE JUMPAR OF STREET LIGHT CONTACT WITH STAY WIRE AND HENCE LEAKAGE CURRENT PASSING THROUGH GI WIRE TO EARTH AND SAME TIME BUFFALO NEAR PSC POLE GOT ELECTOCUTED AND DIE ON SPOT. | COMPANY FAULT | TO CARRIED OUT MAINTENANCE | YES | LT WIRE RE STRINGING & SPACER PROVIDED | NOT APPLICABLE,PM NOT DONE.
38 | HMT | Salal(Near Salal Highway to Salal village road) | Bharvad Nagjibhai Chakubhai | FA(BUFFALO) | Outsider | 17.06.2022 | NA | On Dtd.17/06/2022,Time: 10=30 AM at the Time of Site Inspection,there was LT two wire 1 Phase wire Electric line pass through farm.LT long span One phase of LT Line Conductor were snapped from LT Shackle due to conductor was detoriated and due to pressure of wind the conductor was snapped.The Buffalo was Depasture Under LT Line conductor,The Broken Live Conductor was Falled on Buffalo.Due to the Buffalo was contacted with Live LT Line Conductor,Buffalo died on the spot.The Owner of Buffalo is Bharvad Nagjibhai ChakubhaiVillage:Salal,Ta:Prantij,Distict:Sabarkantha. | CEI PENDING
39 | HMT | SATIPUR | BUFFALO OF RATHOD SABABHAI HIRABHAI | FA (BUFFALO) | Outsider | 19.06.2022 | NA | Fatal Animal Accident occurred to Buffalo of Rathod Sababhai Hirabhai at Satipur Village,Ta. Meghraj Di. Arvalli during 5.45 am as per information getting by owner. The Animal fatal electrical accident occurred Buffalo while rain was running sparking occur on pole due to consumer service wire touch with LT D clamp(service wire insulation damaged at a time) so current pass through pole to *ground* and Buffalo was tie near LT pole (i.e approx 6 feet) and Buffalo coming under electric stress so Buffalo die on the spot | CEI PENDING
40 | HMT | Vatda Bayad | 2 Buffalow of Parmar Bharatbhai Chhababhai | FA (BUFFALO) | Outsider | 23.06.2022 | Na | The Animal Fatal electrical Accident occurred to owner shri Parmar Bharatbhai Chhababhai of vi-Vatda Bayad,Ta-Bayad,Dist-Arvalli under Bayad sdn on dt-23.06.2022 at approximately 12.00 am.Visit at site on dt-23.06.2022,Time-9.30 am.After site investigation,due to heavy wind and rain from end pole,one number of LT Copper wire out of four wires snapping from LT shackle insulator and came in contact with exact below tied two numbers of buffaloes where at night rain and wet land both buffaloes got socked and death. | COMPANY FAULT | TO CARRIED OUT MAINTENANCE | TO CARRIED OUT MAINTENANCE | LT WIRE RE STRINGING & SPACER PROVIDED | 16500+16500=33000
41 | HMT | Farm of Patel vithalbhai karshanbhai at Pural, | Bharwad Karsanbhai Bachubhai | FA(COW) | Outsider | 24.06.2022 | NA | Due to heavy wind & cyclone; Pural Ag feeder LT pole was broken with 4 wire LT line falling down on ground.Meanwhile A cow (approximate 7 years old) was passing & came in contact to that LT wire.So cow got shocked & died.PM Report and police panchnama awaited | CEI PENDING
42 | SBT | Kalol | Rakeshkumar Natwarsinh Chavda | FH | Outsider | 05.06.2022 | NA | On dtd.5.6.22 time: 17.30, news report of Divya Bhaskar & the police staff came at office for intimate the accident and staff of sdn office immediately went to the site. After site verification, concluded that there is victim first climb on pole nearest to TC, then after with help of yellow cable he climb on transformer structure. then after victim touched the DO structure and fell down. During this incident there is no any tripping occured. | Yet not received |  |  | no UGVCL fault,TC maintanance done | 0
43 | SBT | Kerala | Nevabhai Ditabhai Damor | NFH | Dept. | 07.06.2022 |  | Victim has taken LC of 11 kv Yogi feeder at 18.45 and he was attending phase sequence reversal on feeder, he got electrocuted at gantry of Yogi feeder in SS itself. Yogi feeder is HT express feeder having 2 HT connection on it, and checking them both, primary conclusion is that, due to DG set running at matlax company with GOD switch connected with ugvcl grid, power may returned in line and the victim got electrocuted. | Yet not received |  |  | GOD Switch is double-checked to avoid any electrocution | 0
44 | SBT | Bhangadh | Jagdishbhai Punabhai Kalasva | FH | Dept. | 09.06.2022 | B A Bhoi | On date:-09-06-2022 , 11 KV Zankhi JGY feeder emanating from 66 KV Dholera ss was gone In Permanent fault at :-5:30am. So, GETCO staff Informed to BA BHOI (LM) that the 11 kv zankhi Jgy feeder In PF. Thus Shrl BA BHOl(LM) as a supervisor and J P KALASVA (EA) as well as J .R PARMAR (EA) went for attending the line, after line patrolling they were found 01 ht pole broken and 01 pole tilted In Mingalpur tapeline, so after cut off shackle pole jumper and other necessary rectification done and they charged the feeder on 7:10 am. After that they Informed for damage in 11 KV Zankhi JGY feeder about 8:00 am and DE arranged contractor gang with supervisor Shri B R PARMAR for rectification work of damaged pole and also give additional help of SHRI K N GOHIL(EA) and SHRI M G KANZARIYA (EA) to B A BHOI (LM) for restoring power as early as possible. So, as per schedule SHRI C J Rathod contractor gang reached at location with supervisor about 2:45 pm for rectification work. As per statement of SHRI B R PARMAR gang supervisor that after conforming with B A BHOI (LM) for all line was isolated they started work of rectification at that time shackle pole jumper already disconnected from line and B A BHOI, J P KALASVA, MG KANZARIYA and KN GOHIL gone for Mingalpur tapeline patrolling and they also done rectification of one location where one conductor fallen in V- cross arm was rectified and they all were come at location where contractor gang working after whole line patrolling done. As per statement of SHRI B A BHOI and other staff at that time contractor gang work almost completed (i.e. only one wire pending to restringing). So they all BA BHOI (LM), J P KALASVA, M G KANZARIYA and KN GOHIL went to next location where double structure shackle pole jumper cutted at that point SHRI BA BHOl (LM) instructed to JP KALASVA and MG KANZARIYA for doing re-jumpering on shackle pole. After that SHRI B A BHOI and K N GOHIL went at Bhangadh village (Dashama switch ) for cut off the power of line from this location Mahadevpura , Mingalpur and Zankhi village get power or isolated. After cut off the said switch as per instruction given by shri B.A.Bhoi, LM shri K N Gohil, EA informed to M G Kanjariya, EA for starting rejumper work without doing earthing on line. As call received on M G Kanjariya cell phone for starting work they both J.P.Kalasva and M.G.Kanjariya climbing on pole and started rejumpering work during this work M.G.Kanjariya completed one Jumper and J.P.Kalasva work In progress at that time conductor and binding wire in hand of J.P.Kalasva and M.G.Kanjarlya observed that whole body of shri Kalasva vibrate and immediately fallen down from pole. So, he quickly came down and informed to K N Gohil as he assume that Kalasva may got electrocuted from return current In line. From site visit and line network in Mahadevpura tapline 02 nos. of DG set is there In 220 KV Mahadevpura ss and there is also 02 nos. connection one for Control room 1) Executive Engineer, GETCO con.no:-273so/10041/6 and other is temporary connection for construction purpose 2) TRANSRAIL LIGHTING LTD. 220 KV SS having con.no:-27300/00117/3 respectively , So, we take both connection MRI data of said connection and also functioning of DG set checked on dt:- 10 06 2022 In presence of DE Tech-1, DE Tech-2 and DE LAB of Bavla division office. From above Executive Engineer, GETCO con.no:-27380/10041/6 connection DG connected with change over switch and work properly while TRANSRAIL LIGHTING LTD. 220 KV SS having con.no:-27300/00117/3 connection DG without change over switch. So, as per MRI data and functioning of DG there is only one possibility for return power from this temporary connection only. Thus, said connection was disconnected and informed to consumer for installing change over switch and submission fresh test report. Executive Engineer of Bavla Do and Add. Chief Engg. Of Sabarmati circle done site visit on dt:- 13.06.2022. | Yet not received |  |  | CHARGSHEET ISSUED TO ON SITE LINE MAN FOR POOR SUPERVISION VIDE LETTER NO:- UGVCL/BAVLA DO/EST/DA/157, DATED:- 13-07-2022 | 0
45 | SBT | Jagatpur | 1) Archanaben Dineshbhai Gupta 2) Bipin Pintubhai Kori | FH | Outsider | 11.06.2022 | NA | On dtd.11.6.22 at 7.30 PM apprx. Phone call received at Ognaj Sdn complain centre regarding leakage current at Sifron society, immediately line staff visited location. Afte reaching at location, present local persons informed that while it was raining, one child touched his house gate which was connected to AMC streetlight iron pole (pole number SSK/54411) through iron wire, since streetlight pole whosw terminal box was placed adjacent to victim's house, leakage current flew through iron wire and thus child got electrocuted. Seeing the chile one lady tried to save the chile and she also got electrocuted at the same place. After that both victims were admitted to nearest hospital by local persons where doctor declared them dead. | Yet not received |  |  | new section provided,lt spacers installed & service replacement done of the needful. | 0
46 | SBT | NAVAPURA | RABARI BHARATBHAI HARJIBHAI | FA | Outsider | 13.06.2022 | NA | On date 13.06.2022 at around 06:00 pm Shri Bharatbhai Rabari was returning back with his 30 camels, one of his female camel ran to eat neem tree branch and came in contact with 11 kV Laxmipura AG feeder passing nearby and got electrocuted and die. The span of the line is approx 90 mtrs and one of the conductor got loose from pin binding due to tree branch fallen on it during Sunday evening storm, the same loose conductor came in contact with camel. | fault of UGVCL network | regular maintanance of feeder | yes | 11 kV Laxmipura AG feeder tree cutting and other maintanance done and all the conductor sraightened | 25000
47 | SBT | Ambali | Mahavirkumar Surendra Bhola | FH | Outsider | 16.06.2022 | NA | On dtd.16.6.22, time:18.30, the police staff came at office for intimate the accident and office staff immediately went to the site. After site verification and discussed with there with available labour, concluded that victim was touched the defective moter and got elctrocuted whilw lift the water from under ground tank. | Yet not received |  |  | Informed to install ELCB and submit the Test Report ; TR is received after ELCB Installation | 0
48 | SBT | Shilaj | Nilesh Gomaram Parmar | FH | Outsider | 26.06.2022 | NA | On dtd.27.6.22, at 18:00, the police staff came at office for intimate the accident and staff of Sdn immediately went to the site. After site verification, we concluded that there is some leakage current at bunglow 50. There is common shed between bunglow 50 and 47. The victim was touched the metal wire of common metal shed of bunglow 47 & 50 and got electrocuted. | Yet not received |  |  | Informed to install ELCB and submit the Test Report ; TR is received after ELCB Installation | 0
49 | SBT | Popatpara(Juval) | Solanki Lavjibhai Ranchhodbhai | FA | Outsider | 27.06.2022 | NA | Due to heavy wind and rain LT conductor binding breakup from LT shackle insulator and touch to earthing wire. A Buffalo came in contact with the earthing wire and as leakage current was passing from the GI wire got electrocuted and died. | Yet not received |  |  | Rectified earthing during Maintenance | 15000
50 | SBT | Dhandhuka | Nareshbhai Dahyabhai Bharvad | FH | Outsider | 29.06.2022 | NA | As per press note of sandesh news paper on dated 30.6.2022,victim have got electric shock when touch to the single phase motor during water lifting in his home on dt. 29.6.22 | Yet not received |  |  | IT IS NOT UGVCL FAULT ACCIDENT OCCURED IN WITHIN PREMISES DUE TO MISTAKE OF VICTIM HIMSELF. | 0
51 | PLN | KHALI | THAKOR VISHNUJI SHANKUJI | FA | Outsider | 12.6.22 (7.30HRS) | NA | In khali village Umiya para road near Transformer cetnre of 11 kv Kamli(khali) Ag feeder Loc no.20,Shri Thakor Virsangji Shankuji'S buffalo came to drink water in artificial reservoir at near Transformer cetnre,at that time buffalo might came in contact with Leakage current flowing from Agricultural consumer shri Umatiya Abdul Rehman Nurmohammad's motor cable shot.During drinking water in reservoir buffalo might got shocked and died in the Resevoir. | CEI Approval pending
52 | PLN | Odhava | Thakor Kiran (Urfe-Hochi) Balvantaji (Urfe-Kacharaji) | FH | Outsider (Private Premises) | 12-06-22 @13:00 | NA | As per eye witnessstatement victm was doing tree cutting work in farm of Shri Ishvarbhai sendhabhai Rabari in Odhava Village. During this work suddenly Victim shri Kiran urfe (Hochi) Balvantaji Urfe(Kacharaji) Thakor came in contact with cable which is used for tree cutter machine and got electric sock and died. | CEI Approval pending
53 | PLN | Deesa | Un Known | FA | Outsider | 12-06-22 @21:15 | NA | on dt.-12.06.22 evening due to heavy wind and rain treebranch fallen on LT line near chandralok road. Due to this LT line conductor snapped and fall on ground at that time 2 nos. stray cows passes nearby and touched the conductor and got electrocuted and died. | CEI Approval pending
54 | PLN | Deesa | Un Known | FA | Outsider | 12-06-22 @21:30 | NA | on dt.-12.06.22 evening heavy wind and rain fall in deesa. May be due to this one insulated wire was hanging between DO Pin insulator and DO Angle. Due to rainy atmosphere current leacked through insulated conductor. At that time 1 no. stray cow passed nearby and due to leackage current cow got electrocuted and died. | CEI Approval pending
55 | PLN | Vajegadh, Ta. Tharad | SHRI NAVINBHAI JIVABHAI MAGARWADIYA (EMP NO.17599) (ELECTRICAL ASSISTANT (VS),Tharad-2 Sdn) | NFH | (Private Premises), Dept Employee of Tharad -2 | 14.06.22 at 20.35 PM | NA | On dtd-14.06.2022, Approx. Time 20:35 , Shri Navinbhai J Magarwadiya (EA-VS) was trying to start single phase electric motor at his home to fill the water in sintex tank at that time one male pin plug connected to switch board and at same time switch was in "ON" position at the other end there was a male pin plug which came in contact to right hand finger of victim hence Non-Fatal Electrical Accident occured. After he was referred at private Hospital and he was under treatment. | CEI Approval pending
56 | PLN | Unn | DESAI MADHABHAI VIRAMBHAI | FA | Outsider | 27.6.22 | NA | on dated 27.6.22 heavy wind is there ,11 kv khengarpura fdr,s conductor snapped and the buffaloe came in contact of live wire and got shock and died on the spot | CEI Approval pending
57 | MSH | Melusan | Pravinbhai Bhemabhai Suthar | FH | Outsider | 02-07-2022 at 07.30 hrs approx. | N/A | The victim was came to his parlour shop in morning. He was parking his bike near other shop located nearby , of which iron shutter was already closed. At that time he slipped and touched to the shutter. As per primary visit done at site power of that closed shop was coming by their private cable from outgoing fuse board of 3 phase meter located in other nearby diamond cutting industrial 3 phase service connection named Suthar Jemalbhai NaranBhai Virabhai-28703/10157/6. Thus the victim came in touch with shutter which was electrocuted due to insulation breaking of their private cable touching to shutter and thus victim also electrocuted and died. | No |  |  | Pepole were educated to install ELCB for protection for leakage current and use of standard wiring to avoid this type of accident
58 | MSH | Manund | THAKOR RAMBAIBEN JIVANBHAI | FA | Outsider | 06.07.2022 @08:00 HRS | N/A | As on Date 06.07.2022 @08:00 Hrs Aprox. Thakor Rambaiben has leave their buffalo from Shed for Drinking of Water. At that time buffalo goes to nearby electric pole near the residence of Amin Pravinbhai Manilal and came in contact to Earthing Wire (G.I) of electric pole and electrocuted and buffalo die. During detail investigation it is found that There are four servic wire looped together with the sectioin cable from LT Network. The insulation tape at the looping found open due to rain and touched to stay wire (upper part above Stay Insulator) of the electric pole. Due to that leakage current flows to Earthing wire (G.I) of the electric Poles and same time buffalo came in contact with the Earthing Wire of same pole and hence electrical accident occurs. | No |  |  | Serivce joints are insulated with tap and regular maintenance activities is done | 15000
59 | MSH | Dharpur Ta-Patan Dist-Patan | Mare (female horse) of owner Shri Bachubhai Punjabhai Bhangi Vill-Dharpur Ta- Dis-Patan | FA | Outsider | 07.07.2022 @ 0:15 hrs Appox. | N/A | As on date 06.07.2022 approx 00:15 hrs, Shri Bachubhai Punjabhai Bhangi's Mare(female horse) was grazing in private premise and got electrocuted near private premise's streetlight pole. The matter is under investigation. | No |  |  | Consumer and owner of victims is instructed to use ELCB in their premises for protection.
60 | MSH | Bapaiyara | Rabari Jagmalbhai Mafatbhai | FH | Outsider | 10.07.2022 AT APRROX 09:00 AM | N/A | A Electrical Fatal Human Accident Occurred To Outsider Rabari Jagmalbhai Mafatbhai ,Village-Bapaiyara,As Per Eye Witness Statement U.G.V.C.L. L.T.Line Passing In Front Of Victim House And While Cutting Neem Tree Branch Standing On Ground With Dhariya By Victim , He Was Electrocuted And Died,By Observing At Site Tree Branches Near Lt Line Were Cut Down Which Was Touched To Same Lt Line Stated By Eye Witness. | No |  |  | People were educated to maintain safe distance from electrical network
61 | MSH | Gerita | Owner Name:-Chauhan Manuji Pratapji | FA | Outsider | 11.07.2022 | N/A | Buffalo Touched To Waterwork Tc Center G.I.Wire & Got Electrocuted Due To Leakge Current Found In Waterwork Connection. | No |  |  | Instruction Given to water work operator to rectify faulty motor and winding also fencing provision will be done | 15000
62 | MSH | Modhera | Thakor Mukeshji Hiraji | FH | Outsider | 11.07.2022 AT APRROX 09:00 AM | N/A | A Fatal Human Electrical Accident Occurred To Shree Thakor Mukeshji Hiraji.Village-Modhera,Ta:Bechraji, Dist:Mehsana , A Victim Was Standing On Terrace & Removing Wooden Support( Wood Used For Terrace Work-Patti) Which Was Used For Construction Work Of New Shop & At That Time Victim Was Came In Live Contact With 11 Kv P & T Jgy Fdr & Got Electrocuted & Died On Site. | No |  |  | People were educated to maintain safe distance from electrical network, Line shifting work completed | 50000
63 | MSH | Sampra | Shah Kiritbhai Ramniklal | FH | Outsider | 09.07.2022 @ 14:30 hrs Appox. (message received from Divya Bhaskar news dtd 11.07.2022) | N/A | The Victim was fitting a GI string inside his rental house room for drying clothes as it was rainy season.At one side of the wall, he fitted the starting portion of GI string while the other end he tried to fit on opposite wall through hole during which the house wiring which was haphazard and whose insulation was broken and it was bare, came in contact with GI string and victim got electric shock and fall on stone infront of his house door. He was hospitalized and declared dead. | No |  |  | Consumer were educated to install ELCB in their premises for protection. Not to use conducting material for drying cloth.
64 | MSH | Kheralu | OWNER OF COW RABARI BHAGVANBHAI KURSHIBHAI | FA | Outsider | 19.07.2022 AT 7.00 PM | N/A | Due to rainy season, LT line jumper was burnt on PSC pole and this jumper was touched with turn-buckle and angle of guarding. As guarding was provided from PSC pole (which having proper earthing wrapped to all fabrication) to girder pole due to road crossing. Hence leakage current was passing from angle to guarding to opposite girder pole. The victim cow was returning to home after grazing, Mean while it was passing through this charged girder pole and came in contact with said girder pole. Due to that the cow was electrocuted and died on the spot. | No |  |  | Line Maintenance done and Burnt jumper was replaced | 15000
65 | MSH | Sametra | Thakor Manuji Bhavanaji, Thakor Vas, Village Sametra, Tal. & Distt. Mehsna. | FA | Outsider | 25.07.2022 at 13.30 hrs.(Approx) | N/A | A twin core cable of private installation was laid on the ground in industrial Polt of Shri Mehulkumar Vinodray Sompura, Consumer No. 20904/10309/9, The iron chain tied on buffalo's neck rubbed with the open private cable and the insulation got damaged and thus the buffalo got electrocuted. Detailed cause of an accident is under investigation. | No |  |  | People were educated to install high quality cables and ELCB at their premises to avoid such accident
66 | MSH | Gorad,TA- Mehsana,Di-Mehsana | Owner Name-Rabari Umangbhai Jayrambhai,Age-21 years | FA | Outsider | 25.07.2022 08:00 AM Hrs. | N/A | On Dated-25.07.22 3.ph -4 wire LT line of Indiranagar TC (JGY) whiches passes through near Shitla Mata Mandir,One Phase of out going conductor (between 4 & 5 no pole) is broken due to sparking & rain and also which power is ON .In the morning appr.8:00 AM the both cows(Female) came in the contact with the live broken conductor of LT line(JGY) and got electrocuted and the both cows occurred FATAL Electrical accident. | No |  |  | LT line maintenance is done accordingly and out going phase conductor is completed
67 | MSH | Padla | Cow Bharvad Babubhai Bodhabhai | FA | Outsider | 26.07.2022 AT08:00 AM | N/A | A Fatal Animal Accidant Occured At Padla Vill Ta-Shankheswar Dis-Patan Near Padla W Tc During Cow Of Bharvad Babubhai Bodhabhai Going For Eating Grass And Going Near Tc Fancing Arear During This Period Cow Weas Electrocuted And Died Due To Leakage Current Of Tc This Is Primary Reason Which Is Told By Victim But During Investigation Of Site By Ugvcl Empyoes There Is No Any Lekage Current Presnt On Padla Ww Tc Also It Fancing Area And Also Tc Earthing Was Full Of Satisfactor And Plastic Cotted Pipe Coverd On G.I 8 No Earthing Wire So During Site Visit We Dined That Cow Died Due To Leakage Current Of Padla Ww Tc So After All Site Verification We Will Conclud That Final Jugment Taken On The Bais Of Post Martom Report Submitted By Victim Owner. | No |  |  | People were eductaed to keep their Animals away from UGVCL Network
68 | MSH | Dabu | Owner of Cow Thakor Viramji Manaji | FA | Outsider | 26.07.2022 @ 07:00AM | N/A | Due To Heavy Rain And Wind Near By One Smaller Size Tree Branch Of Neem Tree Touch And Break On Lt Line Of Loc-43/45/2 Tc And 3 Wire May Be Gatherd And Broken And Fallen On Ground.There Is 11 Kv Sagthala Fdr And Said Lt Line Crossed.This Victim Cow Seperated From Owner And Enter In Other Near By Person Field Where 3 Wire Fallen This Cow-Zota Grazing And In Touched With Broken 3 Wires And Eloctroduced. | No |  |  | tree cuting was done and line maint. Done
69 | MSH | Mandali | Vaghari Prakashbhai Punabhai | FH | Outsider | 28.07.22 | N/A | While fitting the water pipe in running motor for pulling water from water tap,at that time he got electric shock in his premises. | No |  |  | Disconnected Electric Water Motor from Power supply where leakage current found. Notice given to consumer for installation of Consumer side Protection device like ELCB Switch to avoid this type of accident in future.
70 | HMT | Anjani(Jaleri fali) | Gamar Anitaben Lasabhai | FH | Outsider | 02.07.2022 | - | The G.I. wire of service line was ther laid from LT pole to roof of the house. Due to repairing purpose of house roof, the G.I. wire was dismantled from the roof but was tide at LT pole side.During the site visit the residual part of the wire used for lunger found touched with fabrication of the pole making whole metal parts live as its contact with live as its contact with live wire and metal part on the LT pole.The victim came in contact with GI wire lying in the yard of her house and she was electrocuted and unfortunately died on the spot.further investigation is under progress. | CEI PENDING
71 | HMT | Khadol | He-Buffalow of Bharvad Bachubhai Hirabhai | FA | Outsider | 02.07.2022 | Na | The Animal Fatal electrical Accident occurred to owner shri Bharvad Bachubhai Hirabhai of Vi-Khadol,Ta-Dhansura,Dist-Aravalli under Bayad sdn on dt-2.07.22 approx 1.30 pm due to heavy wind and rain,Bharvad Kalabhai Khatubhai connection 23674/00016/4,RGPR,which non use since long time,its service wire snapped from meter side tap roll binded joint and laid down on road where water 0.5 to 1 feet approx filled due to heavy rain,at that time due to heavy rain with wind,owner return and came at own village house with his all small big 13 nos Cows,buffaloes animals from grassing them approx away 1 km river side for tied them,out of them 1 he-buffalow age approx 4 to 5 year grassing nearby road side and this LT pole where service wire snapped in water,came in contact with leakage current in water and He-buffalow got electrocuted and death at sight.PM report and police panchnama awaited. | CEI PENDING | CEI PENDING | CEI PENDING | MAINTENANCE CARRIED OUT HT LT RESTRINGING | FIRST-8000
72 | HMT | VAKHATPURA | MAKVANA RAJUSINH DIPSINH | FA | Outsider | 05.07.2022 | Na | ON DATE:05.07.22 AT APPROX. 1.00 AM ONE BUFFALO TIED WITH CHAIN BELOW LT LINE.DUE TO HEAVY WIND AND RAIN TWO PHASE WIRE OUT OF LT 4 WIRE LINE CONDUCTOR BROKE DOWN AND FELL ON BUFFALO GOT ELECTRODUCT AND DIED ON SPOT. | CEI PENDING | CEI PENDING | CEI PENDING | MAINTENANCE CARRIED OUT HT LT RESTRINGING | FIRST-15000
73 | HMT | ZANHARIYA | PARMAR AMITBHAI MANUBHAI | NFH | Outsider | 08.07.2022 |  | In Fataji Na Muvada, Zankhariya Village, construction of building of owner Shri Solanki Kanaksinh Prabhatsinh is undergoing and reached upto ceiling level. Victim was working there. While installing 8 FEET LONG iron rod on the Terrace, acidentally iron rod came in induction zone of 11 KV Zankhariya AG passing nearby and as he was holding that bar get electrocuted and fell down. He is admitted to Shivalik Hospital, Bayad under treatment. | CEI PENDING | CEI PENDING | CEI PENDING | MAINTENANCE CARRIED OUT HT LT RESTRINGING | NOT APPLICABLE DUE TO NFH
74 | HMT | Kajavas | Parmar Singabhai Sangrambhai | FA | Outsider | 14.07.2022 | - | On dtd. 14.07.2022 at 08:00 aprrox. Due to heavy rain and wind 11KV Poshina JGY LT wire broken and fallen on the ground, a bullock came in contact with LT wire & electrocuted & died on the spot…. | CEI PENDING
75 | HMT | ANJANA | RAMESHBHAI CHHANABHAI VANKAR | FH | Outsider | 15.07.2022 | Na | ON DATE:15.07.22 AT APPROX. 10.30 AM VICTIM CLIMB HIMSELF ON NEEM TREE TO CUT BRANCHES OF TREE UNDER 11 KV RUPAL JGY LINE WITHOUT INFORMATION UGVCL OR ANY STAFF OF UGVCL DURING CUTTING OF BRANCHES, BRANCHES TOUCHED 11 KV LINE & HE ELECTROCUTED AND FALL DOWN AND DIED IN SITE. FEEDER WAS NOT TRIP DETAILS INESTIGATION REPORT AND POLICE PANCHANAMA AWAITED. | CEI PENDING | CEI PENDING | CEI PENDING | MAINTENANCE CARRIED OUT HT LT RESTRINGING | CONCENT FROM VICTIM RELATED TO NOT CLAIM COMPENSATION
76 | HMT | RAMOSH | RABARI BALDEVBHAI GANDABHAI | FA | Outsider | 19.07.2022 | NA | A cow was passing near transformer structure of Ramosh Ag feeder & rubbing his body to the earthing wire of that tc structure.Mean while leakage current might be came to cow due to water logging Around tc structure.So cow got shocked & died on the spot . | CEI PENDING
77 | HMT | AMARAPUR(Valani muvadi) | ZALA AMARSHIH JAVANSHIH | FA | Outsider | 22.07.2022 | Na | The Fatal Animal accident occured on dated 22.07.22 due to in last week heavy wind and rain the jumper of LT line on the jgy LT line on the JGY LT line pole stuck to D clamp got lose for some reason of said psc pole where having three circuits Lt line. The leakage power comming in to GI earthing wire through D clamp with which the LT line jumper was already stuck. minewhile the buffalo come for grazing grass near this LT line psc pole and that was rubbing body against that psc pole and came in the contact leakage power through GI earthing wire and buffalo got electrocuted and died on the spot at site .PM report and police panchnama awaited. The deatail report under investigation. | CEI PENDING | CEI PENDING | CEI PENDING | MAINTENANCE CARRIED OUT HT LT RESTRINGING | FIRST-15000
78 | HMT | Dakhneshvar | Parmar Narsinhbhai Jamabhai | FH | Outsider | 23.07.2022 | Na | As per eye witness and panchnama nivedan,on dt 23.07.2022 approx 9.00 pm,at that time rain with wind was going on and said victim was passing nearby PSC Pole,at that time suddenly anyhow one psc end pole 2 wire Arial bunch cable LT line was broken and fell down on victim,he souted for save him and his family members residing nearby this location came and take him out of from falling pole and went to vatrak Hospital where on dt 24.07.2022,1.00 pm approx doctor declared him death.Police Panchnama and PM report awaited.Reason for pole falling is suspected. | CEI PENDING | CEI PENDING | CEI PENDING | MAINTENANCE CARRIED OUT HT LT RESTRINGING | NOT APPLICABLE DUE TO F(Mechanical)
79 | HMT | NAVAPURA SITWADA | DESAI DINESHBHAI VIRAMBHAI | FA | Outsider | 26.07.2022 | NA | A COW WAS PASSING NEAR 2 WIRE LT POLE OF SITWADA AG FEEDER. ON THAT LT POLE 1 IRON WIRE TIGHTEN ON FORTH STAP FROM GROUND & OTHER SIDE OF TJAT WIRE WAS TOUGH WITH GROUND WHILE COW PASSING NEARER TO LT POLE ITS HORN CAME IN CONTACT WITH THAT IRON WIRE & THAT WIRE FIXED WITH ITS HORN & COW TRY TO REMOVE HORN FROM IRON WIRE WHILE IT WAS POSSIBLE THAT LT CONDUCTOR CAME IN CONTACT WITH ANGLE & CURRENT PASSED THROUH THAT IRON WIRE VIA GI EARTHING WIRE & COW GET SHOCKED & DIED ON THE SPOT. | CEI PENDING
80 | HMT | LOLASAN | RABARI SHAILESHBHAI BHAGVANBHAI | FA(COW) | Outsider | 27.07.2022 | NA | During site inspection , A Cow was found died below said AG transformer center . Its body was in contact with the earthing wire of transformer center. At the time of inspection there was no any symptoms of leakage current found at incident location . All the earthings of transformer center was not earthed through PVC Rigid pipe . So , there might be a instantaneous leakage current flowing at the time , when cow came in direct contact with live earthing wire. Thus cow died at spot. | CEI PENDING
81 | PLN | Palanpur | Sagar Dipakbhai Suryavanshi | FH | Outsider | 05-07-22 @11:00 A.M | NA | As per eye witnessstatement on Dtd 05.07.2022, around 10.30 hours,while victim was illegally working,Repairing and stringing of privet cable over 11kv City-4 feeder line,During this illegal work by any mistake,the fiber optic cable internal support wire touch with 11kv City-4 feeder live line,So current passes from city-4 feeder to support wire to victim body.Thus,victim got electrocuted him self | CEI Approval pending
82 | PLN | UNAVA | THAKOR VANRAJI JAVANJI | FH | Outsider (Private Premises) | 5.7.22 (1:00PM) | NA | SHRI THAKOR VANRAJJI JAVANJI AT UNAVA ON DTD:5.07.2022 WAS DOING LUNCH WITH HIS FAMILY AROUND 1:00 PM.DURING LUNCH HIS HAND CAME IN CONTACT WITH TABLE FAN PLACED NEAR HIM AND HE GOT ELECTROCUTED AND FATAL ACCIDENT OCCURED.DETAIL INVESTIGATION IS UNDER PROCESS AND WILL BE SUBMITTED ON THE RECEIPT OF THE SAME. | CEI Approval pending
83 | PLN | MANPURA(UN) | BHARWAD RAMESHBHAI DANABHAI | FA | Outsider | 11.7.22 | NA | ON 11.07.22 APPROX 17:00 HRS WHILE RETURNING FROM BOR WELL TOWARDS VILLAGE A BUFFELOW OF SHRI BHARWAD RAMESHBHAI DANABHAI MET WITH A FATAL ACCIDENT DUE TO LEAKAGE CURRENT FROM LV LINE AS DUE TO SERVICE CABLE FROM TRANSFORMER TO LT POLE INSULATION GOT BURNT AND AS RAINY SEASON RAIN IS CONTINUE WHILE THE ACCIDENT TOOK PLACE. HENCE A BUFFELOW MAY GOT ELECTROCUTED WHILE CAME IN TOUCH WITH LT LINE POLE & DIED ON THE SPOT. INFORMED TO POLICE DEPARTMENT FOR POLICE PANCHNAMA & VATERINARY OFFICE FOR P.M. REPORT | CEI Approval pending
84 | PLN | BAVALCHUDI | TAHKOR CHATURJI MANGAJI | FA | Outsider | 13.7.22 | NA | As per Eye witness, cow getting electrocuted while grazing near transformer center of 11KV Nalasar AG fdr and came in contact with PSC Pole of TC. | CEI Approval pending
85 | PLN | Kantivas | Makwana Punkiben Fulabhai | FH | Outsider | 19.07.2022 13.21 hrs | NA | Victim Smt. Makwana Punkiben Fulabhai was go for latrine at open place at that time due to rain & wind one conductor broken of 2 wire LT line which is JGY LT on ground at that time X'mer power supply is live victim's right hand came in contact with live broken conductor and got electric shock and death on the spot and fatal electrical accident occured. | CEI Approval pending
86 | PLN | Kantivas | Makwana Jagabhai Kehrabhai | FA | Outsider | 19.07.2022 13.21 hrs | NA | As per owner statement,on dated 19.07.2022 around 13.21 hrs owner's Buffalo grassing at open place at that time due to rain & wind one conductor broken of 2 wire LT line which is JGY LT on ground at that time X'mer power supply is live grassing buffalo came in contact with live broken conductor and got electric shock and death on the spot and fatal electrical accident occured. | CEI Approval pending
87 | PLN | Ashiya | Animal (Cow) owner shri Rabari Mafabhai Bhikhabhi | FA | Outsider | 19.07.2022 @ 17:00 | NA | Fatal animal (Cow) electrical accident occurred as on dtd. 19.07.2022 at village: Ashiya, Ta: Dhanera under Dhanera-1 sdn. A Cow (Approx. 8 Years old) of shri Rabari Mafabhi Bhikhabhai, Due to rain and wind atmosphere on that day, While cow was tied below LT line of 11 KV Sunthiya Ag feeder at that time power supply schedule is 3-phase of the feeder, Existing TC-100 KVA and existing LT 3Q4W line passing from service pole, two numbers of conductor broken due to rain and wind from LT shackle pole insulator and conductor fall down Cow and cow came into live conductor contact and Cow got electrocuted and died on the spot. | CEI Approval pending
88 | PLN | ABASANA | Sureshkumar Karshanji Solanki (EA) | FH | Dept. | 27.7.22 | A S LIMBAT (ALM) | on dated 27.7.22 as per eye witness A.S.Limbat(ALM) and M.D.Parmar (E.A),victim Sureshkumar Karshanji Solanki(E.A) climbed on 11 kv pole of Shriram JGY feeder of balodhan SS to tie the 6 mm PVC LT cable, during hanging of LT cable near to supporting angle stay pair on PSC pole unfortunatelly his hand touched the 11 kv line wire hence he got electric shock and fell down from pole and fatal accident occured | CEI Approval pending
89 | PLN | Gangapura | PATEL INESHKUMAR PRAKASHBHAI | FH | Outsider (Private Premises) | 28.07.2022(7:30AM APPROX) | NA | SHRI PATEL INESHKUMAR PRAKASHBHAI WAS CONNECTING THE PIN OF MOTOR WITH THE SWITCHBOARD SITUATED ON THE WALL ON DTD 28.07.2022 AROUND 7:30AM.WHEN HE WAS DOING CONNECTION HE CAME IN CONTACT WITH THE LIVE SWITCHBOARD AND HE GOT ELECTROCUTED.DETAILED INVESTIGATION IS UNDER PROGRESS AND WILL BE SUBMITTED ON THE RECEIPT OF SAME. | CEI Approval pending
90 | PLN | Vaghrol | Rabari Ishwarbhai Hamirbhai | FA | Outsider | 30.07.22 (5.30 P.M.) | NA | During site visit and as per eye witness statement,at about 5.30 p.m., the Buffalo was grazing near 11 kv pole of Vaghrol Feeder and at time buffalo started scratching on stay wire and the extra wire which was bind with this stay came in horn of buffalo and it fix with and suddenly unbind from stay and this wire touch with live conductor of 11kv vaghrol feeder.So,live current flow on this wire to buffalo and got electrocuted and died on spot. | CEI Approval pending
91 | SBT | Lavarpur | Patel Govindbhai Haribhai | FH | Outsider | 03.07.2022 | NA | Victim was used single phase 0.5 HP motor for sprinkle water on his new constructed house, on 3.7.22 at 7.00 P.M. He was connected wire in plug, made switch on of that plug & other side of such wire where connected male connector, while he entering this connector with female connector of motor accidentally he contected with live male connector & accident occurred as fatal. | Yet not received |  |  | UGVCL not at fault | 0
92 | SBT | Zezara | Hadgara Rajubhai Meghabhai | FA | Outsider | 04.07.2022 | NA | A Buffalo came in contact with the G I wire and at the momentory leakage current was passing from the G I wire due to disk puncture and buffalo got electrocuted and died. | Yet not received |  |  | DISC REPLACED AND MAINTENANCE DONE | 0
93 | SBT | Khoraj | 1) Balwantji Dipuji Dabhi 2) Bhikhaji Kaluji Dabhi | FA | Outsider | 05.07.2022 | NA | On 5.7.22 at around 22:30 service cable fire at end termination with LT conductor which is suppling (through 3ph 4w LT line) Ag, A1 tariff connection of Shri Dabhi Dipuji Takhuji village Khoraj. So due spark, two conductor of 4 wire LT line snap on the she buffalow and he buffalo's calf which was tighted with chain under the LT, got electrocuted. | Yet not received |  |  | 11 kv khoraj feeder , maintanance done | 0
94 | SBT | Ganol | 1) Gokalbhai Dhulabhai Algotar 2) Sureshbhai Velabhai Algotar | FA | Outsider | 05.07.2022 | NA | At Ganol near bharvad jok in para vistar, 1 no pole fallen down due to surrounding water, due to this another 2 pole and LT wire also fallen down, Live LT line conductor fallen down, live LT line conductor snapped between two piles and conductor fallen down on two nos. of cows move below this LT line, cows get electric shock and died on the spot. | Yet not received |  |  | NEW LT POLE ERECTED & RE-STRINGING DONE. | 30000
95 | SBT | Kavitha | Pravinsinh Devisinh Vaghela | FA | Outsider | 08.07.2022 | NA | on 8.7.22 at around 16.30 area around RSJ LT pole in front of floor mill in village Kavitha was flooded with rain water due to heavy wind blew, IT wire from the LT shackle insulator snapped and touched to RSJ LT pole and leakage current was flowing in pole and water at this time victim buffalo was passing through water and died due to leakage current passing through water. So got electrocuted. | Yet not received |  |  | NEW LT ABC PROVIDED AND EARTHING RECTIFIED | 15000
96 | SBT | Kadiyapura | Babubhai Keshabhai Devipujak | FA | Outsider | 10.07.2022 | NA | On dtd.10.7.22, in village Kaliyapura, nr. Kanal 11 KV Dadusar Ag feeder HT line conductor broken down due to wind and rainy atmosphere. Broken conductor of 11 kv Dadusar Ag feeder HT line live conductor hangging below from the pole. At that time one buffalo grazing below this HT line might have came in contact with hangging HT line live conductor and might have been electrocuted. Buffalo got electric shock and died on the spot. | Yet not received |  |  | RE STRINGING OF HT LINE DONE & PROBLEM RECTIFIED | 15000
97 | SBT | Palwada | Varshaben Chetanbhai Ko.Patel | NFH | Outsider | 11.07.2022 | NA | While victim was on way to her home the pole broken from ground due to heavy rain, pole accidently fallen on pit of sand & as the victim was passing from the location, she got injured due to falling down of pole and she got injury on her head, waist and legs. | Yet not received |  |  | Pole Muffing is re-applied | 0
98 | SBT | SANAND | Sachin Rajendra Sahani | FH | Outsider | 11.07.2022 | NA | As statement of company owner and at the early morning on dtd.11.7.22 while the victim came outside from his room he touched to iron wire used for hanging clothes and there was rainfall on that day. Due to some how leakage current passed on iron wire and he came in contact with iron wire and electrocuted. No any leakage current found in iron wire at the time of visit by UGVCL. | Yet not received |  |  | No any fault from UGVCL side | 0
99 | SBT | Kalol | Dantaniya Baldevbhai Shivabhai | FH | Outsider | 12.07.2022 | NA | On dtd.12.7.22 at around 16:00 during the fitting work for ladded of iron at premises of Shri Rajkumar Jamalbhai Nat and her wife Savitaben Rajkumar Nat at- Natnagar, nr. Krishnanagar (where there is no service connection from UGVCL exist) and for fitting of ladder electric power used from nearby source from private network during this work 5 nos. of persons were working with victim and got electrocute | Yet not received |  |  | AS THERE IS NO UGVCL NETWORK OR CONNECTION EXISTING AT SITE OF ACCIDENT OCCURE,VICTIM ARE INFORMED TO GET CONNECTION. | 0
100 | SBT | Khoraj | Takhiben Baldevbhai rabari | FA | Outsider | 14.07.2022 | NA | on dtd 14.07.2022 a message received on telephone at around 5.30pm about fatal buffalo accident. While site visited by staff on dtd 14.07.2022 at around 6.15 pm, we observed that, minor leakge current observed near TC center. On dtd 15.7.2022 when official went to site for site panchnama in the presence of Shri Baldevbhai R Rabari and Shri Karamshi D Rabari,we checked near TC Center(11KV KHORAG AG FEEDER, 66KV ADALAJ SS) where buffelo met accident , but there was no any leakge current found at site. so at the time of accident due to monsoon weather , and water loging near TC center may minor leakge current came in contact to buffalo, and it got electrocuted on spot. | Yet not received |  |  | TC earthing done where accident occurred | 15000
101 | SBT | Bakrol | Pravinkumar Ravindraram | FH | Outsider | 16.07.2022 | NA | A report for fatal accident received on 22.7.22 from kanbha Police station. As per eye witness statement on dtd.16.7.22 at around 16:45 hrs Victim and his colleague was working in consumer premises in big milk storage tank, which was placed nr. Pollar of the shed. After work completion inside milk storage tank, while coming outside victim take support of pillar of shed and got elctrocuted. His colleague pull him during electrocution and after that the victim slept on the milk storage tank. The person who pull him didn't felt any electric shock as per eye witness statement. After that other workers took him to Shiv Hospital, Bakrol for tratment. During treatment said accident converted in to fatal. At the time of site visit and also as per eye witness statement no any leakage current or loose wiring is observed however actual cause of death will bw derermined after receiving of PM report. | Yet not received |  |  | N A | 0
102 | SBT | Geratpur | Vinodbhai Sampatrav Davadkar | NFH | Outsider | 20.07.2022 | NA | Victim going to operate society bore well and while repairing fuse in out going side of meter at that timeshort circuit occurred and due to flash got electrocuted. Accident occurred in private network victim doing work without making power off. | Yet not received |  |  | NEW FUSE PROVIDED AND SEALING DONE. | 0
103 | SBT | Babajipura | Meniya Jayantibhai Dayarambhai | FA | Outsider | 22.07.2022 | NA | Due to wind (cyclone) LT conductor suddenly snapped and fall down on buffalo passing under the LT line and got electrocuted and died. | Yet not received |  |  | REPLACED COATED CONDUCTOR OF 3 SPAN | 15000
104 | SBT | Bavla | Chandubhai Mohanbhai Bharad | FA | Outsider | 22.07.2022 | NA | On 22.7.22 at around 17.10 17.10 at village Bavla near Sant Ashram vania Vas neutral wire of LT pole accidentally fell down and the cow was passing below LT line and got electrocuted and died.. | Yet not received |  |  | RE STRINGING OF LT LINE DONE & SPACERS PROVIDED ON LT SIDE PROBLEM RECTIFIED | 0
105 | SBT | Vavol | Sukhdev Mogilal Kharaniya | FH | Outsider | 24.07.2022 | NA | On dtd.24.7.22, around 9.22 a.m., phone call received at Kudasan complaint centre regarding Fatal accidnet at Sidhdharth Heaven site, Vavol. Staff who is present on duty at complaint centre had informed to Vavol SS, not to made ON the Tulsi feeder. HT line of Tulsi feeder is passes parallel to road. Office of construction site is under consttruction which is being constructed under HT line. Illegal construction is established by developers outside his premises just below the high tension line. Victim was working on under construction office (lintel level part of building), somehow he was got in contact/touched either directly or by any object, got electrocuted and died on site. | Yet not received |  |  | Issued notice for illegal construction to consumer and also later consumer did lineshifting and converted to under ground network. | 0
106 | SBT | Shethvas | Ramlal Ramprasad Sharma | FH | Outsider | 25.07.2022 | NA | On dtd.25.7.22, at 16.30, Police Office informed via letter no.3066/2022. After detail investigation the site on 25.7.22, as per eye witness of testimony victim used the motor for water pumping in own house from 3 pin plug with help of 2 core flexible wire. As per site seen it is concluded that during operation of motor, current is passing through body from nozzle pipe & victim got elecrocuted. There is no any protection device ELCB or RCCB connected at consumer premises. | Yet not received |  |  | accident occurred at consumer premise,so connection of consumer dis connected,after ELCB provided, re connection done | 0
107 | SBT | Kalol | Zaverbhai Harjibhai Rabari | FA | Outsider | 28.07.2022 | NA | On dtd.28.7.22, appx.at 10:40 A.M., Shree Chauhan Ishmuddin Registered a complaint of current & 2 cows are dead, near water tank, old town hall, kalol. Then after UGVCL emergency team arrived at location & see that 2 cows are dead near to Transformer's stay, which is located in water of construction site of nagarpalika. After that UGVCL team remove the fuse of water works & then after check the fencing & stay with the help of LT tester, there is no any leakage current flow in water or any transformer. So due to short of Nagarpalika WW motor, leakage current passing through the water & 2 cows are electrocuted & dead. | Yet not received |  |  | leakege current of Elect.motor of WWNP. | 0
108 | MSH | Chhaniyar | Bharvad Sartanbhai Gafurbhai | FA | Outsider | 05.08.22 03:45 PM | N/A | Due to heavy rain and wind big branch of neem tree fallen on LT line of village TC near Ramji mandir way due to this LT line live conductor broken and falldown and 1 nos cows touched with bthe live conductor and got electrocuted. At same time at the Detrojavas Rampura way existing LTline live conductor broken from jumper and binding due to broken the conductor of same LT line by fault occurancess and this other live conductor falldown which touched with 2 nos cow and 1 nos. calf got electrocuted.This is the primary reason is under investigation and it may submitted after DIR. | No |  |  | Tree Branched Cutting Work Completed & Lt Conductor Restringing Work Completed | 56000
109 | MSH | Opp- Vitthl Vila Society, Nr. Transformer, Matarvadi PATAN | COW of Shri. Thakor Kuvarsinh Udesinh | FA | Outsider | 11.08.2022 | N/A | Fatal Animal ( COW ) Electrical accident occurred nr. Vitthalvila Society Transformer, Op.. Vitthalvila Society located at rode side at Matarvadi area PATAN CITY Ta-Dist.Patan. Victim COW of Shri. Thakor Kuvarsinh Udesinh passing near the transformer centre fencing. At same time the fired(Damaged) out going LT cable of Transformer was in touch with fancing and same time cow came in contact with same fencing and geeting electroduce and died . The site is verified by DE Patan City-2 and necessary rectification done immidiately. Intimation received from Patan City power house complain centre on Dtd. 11.08.2022, 16:50PM. | No |  |  | LT cable is recitified and installed | 15000
110 | MSH | Kukarwada | OWNER NAME:-RABARI KARAMSHIBHAI SARTANBHAI | FA | Outsider | 17.08.22 | N/A | Due to collapse of old house of Mukundbhai Shah,debris of house is fallen on pole and hence pole has broken and fell at road side and at that time cow was passing under broken pole and came in contact with service & GI wire and died. | No |  |  | New Pole is erected and line stringing work completed
111 | MSH | Vamaj | OWNER OF Buffalo - RABARI PRINCE VISHNUBHAI | FA | Outsider | 23-08-2022 04:00 am | N/A | A buffalo was tied up with wooden peg on Vamaj-Fuletra road below the dead 11kv Vamaj Ag feeder's line. The same line is also passing from Vamaj-Ankhol road, from where approx 4.00 a.m today, a big truck was passed and broken the one conductor of several span of this line. Among that, approx 300 mtr far from that point, this dead broken wire came in contact with 2 wire LT live line near location pole no 108 of 11kv Vamaj Ag feeder and got charged also the same charged one wire came in touch with the Buffalo (near pole no 106), where tied up and got electrocuted. | No |  |  | Accident Occurred Due To Unknown Vehical Broken Conductor And By That Contact To Animal And Accident Occurred, Also Ht To Lt Line Crossing Removel Work Completed By K-2 Sd/N
112 | HMT | MAHUDI | Manat manilal mavjibhai | FA | Outsider | 08.08.2022 | NA | Fatal Animal Accident occurred to Buffalo of Manat manilal Mavjibhai at Mahudi Village,Ta. Meghraj Di. Arvalli during 4.00 pm as per information getting by owner. The Animal fatal electrical accident occurred to Buffalo while rain was running sparking occur on pole due to consumer service wire touch with service G. I. Wire (service wire insulation damaged at a time), whice came in contact with psc pole earthing wire.so current pass through pole to *ground* and Buffalo was passing near LT pole to drink water (i.e approx 3 feet) and Buffalo coming under electric stress so Buffalo die on the spot. | CEI PENDING
113 | HMT | BALAVANTPURA | DAMOR SACHINBHAI PRAVINBHAI | FH | Outsider | 09.08.2022 | NA | THE VICTIM'S FAMILY HAVE TAKEN POWER THROGH OUTGOING OF METER OF CONSUMER NO: 23103129858 IN R/S OF BHATT VIPULKUMAR UMIYASHANKAR BY LAYING 1/18 SIZE FLEXIBLE WIRE ON FIRST FLOOR OF THIS PREMISES,THE SAID WIRE INSULLATION IS DAMAGED AT TWO DIFFERENT SPOT AND LAYING ON OPEN TERRACE NEARIR ON PIPE COAT.DUE TO CONTINUOUS RAIN ON THAT DAY THE LEAKAGE CURRENTFROM DAMAGE LIVE WIRE FLOW TO IRON COAT AND IRON GRILL AND GET ELECTROCUTED AND DIED. | CEI PENDING
114 | HMT | NAVA JAVANPURA | BHARVAD BHARATBHAI KHODABHAI | FA | Outsider | 10.08.2022 | Na | ON DT:10.08.2022 ARROUND 2:15 PM BUFFALO WAS GAZING IN THE FIELD OF BHARVAD BHARATBHAI KHODABHAI.11 KV ITADI AG FEEDER IS PASSING THROUGH THE FIELD OF BHARVAD BHARATBHAI KHODABHAI ON SITE VISIT IT WAS OBSERVED THAT 11 KV CONDUCTOR OF ITADI AG FDR SLIPPED FEOM THE PIN INSULATOR AND FALL ON V-CROSS ARM,THE 11 KV FEEDER DIDNT TRIP AS THE POLE EARTHING WAS DETORIATED.SO WHEN BUFFALO TOUCHED THE BROKEN GI WIRE GOT SHOCK AND DIED ON SPOT. | CEI PENDING | CEI PENDING | CEI PENDING | MAINTENANCE CARRIED OUT HT LT RESTRINGING | ALL DOCUMENTS RECEIVED,PROCED FOR FIRST PAYMENT.
115 | HMT | KOLUNDRA | BHAMBHI BHIKHABHAI GOBARBHAI | FA | Outsider | 13.08.2022 | NA | FATAL ANIMAL ACCIDENT OCCURRED TO TODAY AT KOLUNDRA VILLAGE ON 13.08.2022.11 KV VAVKAMPA JGY LEAVING FROM 66 KV RELLAWADA SUB STATION PASSES THROUGH KOLUNDRA VILLAGE.OWNER OF SHRI BHAMBHI BHIKHABHAI GOBARBHAI NATIVE OF KOLUNDRA VILLAGE HAD TWO WETTER COWS FOR GRAZZING ON A FIELD ON THE OUTSKIRTS OF KOLUNDRA VILLAGE BUTTHE WIRE OF 11 KV VAVKAMPA JGY FEEDER SUDDENLY CONDUCTOR BROKEN DUE TO PIN FIRE & FELL DOWN ON THE GRAZZING COW ELECTROCUTING THE COW AT THAT PLACE KILLING IT ON THE SPOT AT TIME 2:15 PM APPROX. | CEI PENDING
116 | HMT | Modasa | Abrar Idrishbhai Sidhva | FH | Outsider | 13.08.2022 | NA | On date 13.08.2022 victim was unfurling national flag as a part of 'Har Ghar Tiranga' compaign. Incident occured on amin sign board near complex when the victim was fixing the flag with iron pipe , he may came in contact with 11KV line of Sahara feeder and may got shocked and suddenly fell down on the ground and got injuries on head. He was immediately dragged to Ganchi Aroghya Mandal for treatment and from there he was shifted to Unity Hospital and thenafter shifted to Ahmedabad Civil Hospital for treatment. And on dt. 20.08.2022 early morning he lost his life and was declared dead by the doctors. Detail cause of whether the accident is mechanical or electrical is under investigation. | CEI PENDING
117 | HMT | Oda | Makwana Milanji Jayantiji | FH | Outsider | 14.08.2022 | NA | The victim was going to his uncle's house at village Odaat night time approx. 22:00 hrs when he was passing through farm of Patel Gautambhai he came in contact of broken LT live conductor of 11KV Oda Ag and elctrocuted. He was shifted for further treatment by 108 ambulance but unfortunately he was declared dead by ambulance staff. | CEI PENDING
118 | HMT | KANADAR | SADAT KALPESHBHAI HARJIBHAI | FH | Outsider | 18.08.2022 | R D PATEL | A LINE STAFF GANG WITH LINEMAN WAS THERE FOR STRATIGHTEING LT TILTED POLE OF 11 KV VIRPUR JGY FEEDER , ALSO THE TOP CONDUCTOR OF 1P2W LINE WAS BROKEN AND FELL DOWN NEAR THIS TILTED POLE. DURING THE POLE STRATIGHTEING WORK, AS THE LOCATION IS NEAR TO THE VICTIM'S HOUSE , HE WAS ALSO CAME TO FOR HELP OF POLE STRATIGHTEING WORK. THE POLE STRATIGHTEING WORK WAS CARRIED OUT BY PULLING STAY WIRE. 11KV TRANSFORMER DO WAS REMOVED DURING THIS WORK. DURING THIS WORK THE LT LINE WAS TOUCHED TO THE HT LINE OF 11KV CHITHODA AG FEEDER EMANATING FROM 66KV DANTOD SS AND POWER CAME INLT LINE. THE VICTIM CAME IN CONTACT WITH BROKEN LT CONDUCTOR AND GET ELECTRIC SHOCK AND BECAME UNCONSCIOUS, VICTIM TRANSFERRED TO CIVIL HOSPITAL BHILODA WHERE HE WAS DECLARED DEAD BY DOCTORS. | CEI PENDING |  |  | MAITENANACE CARRIED OUT AND DISTANCE MAINTAIN WHERE LINE CROSSING
119 | HMT | VIRPUR | NINAMA SHANKARBHAI DHARMAJI | FA | Outsider | 22.08.2022 | NA | ON DATE 22.08.2022 TIME APPROX 09:55 AM, A TOP CONDUTOR OF 11 KV RAYSINGPUR AG FEEDER WAS BROKEN AND TOUCH TO EARTH SO DUE TO WET WEATHER NEAR BY SURFACE AREA IS ELECTROCUTED AND ONE BUFFALLOW AND ONE COW IS CONTACTED WITH THIS ELECTROCUTED SURFACE AND BOTH ANIMAL DIED ON THE SPOT. | CEI PENDING |  |  | MAITENANACE CARRIED OUT | first installment paid RS. 30000/-
120 | HMT | NATHA NA MUVADA (AMODARA) | RAVAL VIKRAMBHAI RAMESHBHAI | FH | Outsider | 24.08.2022 | NA | IN NATHANA MUVADA,AMODARA VILLAGE,VICTIM AND OTHER(RAVAL NARMADABEN NARSINHBHAI)WERE TRIYING TO LEVEL THE SHED OF RAVAL RAIJIBHAI GALABHAI'S HOUSE BY STANDING ON THE SHED.WHILE LEVELING,ACCIDENTALLY THE VICTIM GOT IN CONTACT WITH THE LIVE WIRE OF 4W LT OF AMODARA JGY PASSING ABOVE THE SHED AND FELL DOWN.WHILE MOVING TOWARD PHC,HE DIED. HIS PARENTS DENIED FOR POST MORTEM OR PUNCHANAMA OR POLICE COMPLAINT. | CEI PENDING | CEI PENDING | CEI PENDING | MAINTENANCE CARRIED OUT HT LT RESTRINGING | NOT APPLICABLE DUE TO PM NOT DONE CONCENT GIVEN BY VICTIMS FATHERS
121 | HMT | HATHIPURA | BARIYA KASHIBEN BHATHIBHAI | FH | Outsider | 24.08.2022 | NA | IN TEKRI FALI,HATHIPURA VILLAGE,THERE WAS THREE WIRE JGY LT POLE IN WHICH STREET LTG FIXTURE CAME IN CONTACT WITH JOINT OF STREET LIGHT SERVICE WIRE AND G.I WIRE WAS TOUCH WITH FIXTURE AND PRIVATE METAL WIRE FOR DRYING OF CLOTH WAS TIGHTED WITH G.I WIRE ON LT POLE BY PRIVATE PERSON. DUE TO JOINT SERVICE WIRE LEAKAGE CURRENT FLOW THROUGH G.I WIRE AND WHILE TAKING OFF CLOTHES FROM STRING,VICTIME GOT ELECTRIC SHOCK AND DIED. P.M REPORT AWAITED. | CEI PENDING | CEI PENDING | CEI PENDING | MAINTENANCE CARRIED OUT HT LT RESTRINGING | PM & POLICE PANCHNAMU & OTHERS DOCS.PENDING
122 | HMT | Kalyanpura | Rabari Jayrambhai Babarbhai | FA | Outsider | 25.08.2022 | NA | On dtd. 25.08.2022 at 10:00 aprrox. Due to heavy wind tree branch fallen on LT line cause snapping of conductor of LT line of 11KV Ravol ag feeder,2 cow were passing through wangha and came to contact of snapped conductor of LT line of 11KV Raol Ag and got electrocuted and died on the spot. | CEI PENDING
123 | HMT | KAU | KATARA SANJAYBHAI SHANKARBHAI | FH | Outsider | 26.08.2022 | NA | After come to know about the fatal accident of victim Katara Sanjaybhai Shankarbhai through social media that accident occured due to current providing on fencing of agriculture land. Accident was occured in agriculture land of Shanabhai Somabhai Khant as per satement of eye witness. As per eye witness statement, there was fencing of senting wire around the agricultural land Shanabhai Somabhai Khant. When witness saw the victim, there was no fencing around the land of Shanabhai khant. The dead body of victim was in the land of victim's agriculture land which is adjescent land of Shanabhai Somabhal Khant. As per eye witness statement, accident is occured due to the current providing on fencing of agriculture land of the Shanabhai Somabhai Khant. At the time of site visit, there was no fencing around the agriculture land, but small pits were obsereved around the land of Shanabhai Khant. Detailed investigation is under progress. | CEI PENDING
124 | HMT | Bayad | Buffalow of Baloch Nizamkhan Ahmedkhan | FA | Outsider | 31.08.2022 | Na | On Date 31.08.22, time approx 19.18 to 19.20 pm , 11KV Radodara AG feeder tripping came and feeder was in ON condition after test. But middle wire conductor snapping by reflection of line side tripping fault from first span from Bayad SS side cross boundry AB switch Pole location. During that time farmer buffalow nearby grassing there came in contact with that snapping conductor and buffalow got electrocuted and death at site. PM report and police panchnama awaited. | CEI PENDING | CEI PENDING | CEI PENDING | MAINTENANCE CARRIED OUT HT LT RESTRINGING | PM & POLICE PANCHNAMU & OTHERS DOCS.PENDING
125 | HMT | UBHRAN | BHARWAD PUNJABHAI BACHUBHAI | FA | Outsider | 31.08.2022 | Na | As per information received from local Village person at around 04:15 pm, DE Sathamba had visited the site. In Ubhran Village, there was 4W AG LT Line passes through raw road to existing AG consumer. After grazing grass, the cloud of approx 30 nos cows returning at home, one snapped conductor coming in contact with leg of one she cow and got electrocuted and died. | CEI PENDING | CEI PENDING | CEI PENDING | MAINTENANCE CARRIED OUT HT LT RESTRINGING | ALL DOCUMENTS RECEIVED,PROCED FOR FIRST PAYMENT.
126 | SBT | Zanzarka | Bhopabhai Ajubhai Jogarana | FA | Outsider | 06.08.2022 | NA | on dtd.6.8.22 around 8 a.m. at Zanzarka (Near Katakiya Welding Shop) cow was passing below TC and got electrocuted and died. No any tripping recoreded at that time as per confirmation given from Jaliya SS. As soon as complaint received , Zanzarka JGY feeder was shut down immediately to avoid any more unwanted accident. | Yet not received |  |  | OLD EARTHING REMOVED FROM TC CENTER & NEW EARTHING PROVIDED & PROBLEM RECTIFIED. | 15000
127 | SBT | Saij | Rabari Devjibhai Sakarbhai | FA | Outsider | 08.08.2022 | NA | On date Dt 08-08-2022 & at around 06:00 the cow of owner shri RABARI DEVJIBHAI SAKARBHAI went for grass feeding and passed nearby Rabari vas of village- saij was Came in contact with one broken LT wire so got to electrocuted, Detail invastigation is in progress. | Yet not received |  |  | CONDUCTOR REPLACED OF 1 SPAN AND LT SPACER PROVIDED | 0
128 | SBT | Bhadaj | Sunilkumar Harubhai Hathila | FH | Outsider | 09.08.2022 | NA | On dtd.10.8.22, Shilaj office received application for accident by police staff at 13.30 and immediately went to that site. There is LTMD connection in the name of Ganesh Infra con. No. 74812118484 (LTMD 20 kw for construction purpose for 2 years) village Bhadaj. the power was disconnected. As confirmed by eyewitness, the victim worked at basement road. the victim touched the Pvt cable and got electrocuted. Site checked but no any spots available on that cable and not found any technical proof for accident occurred or not. | Yet not received |  |  | Informed to install ELCB and submit the Test Report ; TR is received after ELCB Installation | 0
129 | SBT | Kanotar | Pravibhai Prahladbhai Rathod | FA | Outsider | 14.08.2022 | NA | On dtd.14.8.22 around 13.30 at village kanotar (nr. Farm of Chamanbhai Meghabhai Makwana) buffalo was passing below TC and got electrocuted and died. No any tripping recorded at that time as per confirmation given from Kesardi SS. | Yet not received |  |  | OLD EARTHING REMOVED FROM TC CENTER & NEW EARTHING PROVIDED & PROBLEM RECTIFIED. | 15000
130 | SBT | Jakhwada | Mahesh N Singada (E.A.VS) | NFH | Dept. | 22.08.2022 | NA | Victim and other 3 line staff were given program for creeper removal at Sokli Sachana Road meanwhile a complaint for no power at primary school of Jakhwada village was received. So Victim and other 3 linestaff were gone to attend the complaint. The primary school connection is connected to railway WW TC. Other 4 lgt connetions are also connected from this TC. For checking on TC centre, victim Shri MN Singada, touched the fencing of TC and got shocked and fallen down on RCC road. Other line staff immediatly called 108 ambulance and shifted him to shiv hospital Viramgam and then to SAL hospital Ahmedabad for surgery of fracture occurred at hip portion of victim. On investigation it is found that a twin core wire was connected on TC LT side bushing for purpose of unauthorized streetlight used by local residents. Insulation of twin core wire was found broken and touched to the fencing. So leakage current passed through fencing and victim got shocked. | Yet not received |  |  | REMOVED STREET LIGHT AT CONSUMER PREMISES | 0
131 | PLN | Dethali | Patel Ravjibhai Ramjibhai | FA | Outsider | 24.07.22 @16:10 hrs. | NA | In owner premises one outgoing wire from meter pass from iron shade pipe. A crake found in owner's wire and due to rainy season leackage current pass in shade and one no. buffalow got electrocuted and died. | CEI Approval pending
132 | PLN | Ganeshpura,Ta:-Tharad | Koli Tinabhai Danabhai | FA | Outsider | 22.7.2022 at 7 a.m. | NA | On dtd.22.7.2022 at 7 a.m. camle of Shri Koli Tinabhai Danabhai was grazing on hilly area and suddenly came in direct contact with 11 KV line of Ambadeshwar AG feeder passing right over the hill and got electrocuted and died on the spot. | CEI Approval pending
133 | PLN | Dabhachatra | Angari Mehlabhai Nanabhai | FA | Outsider | 02-08-2022 (9:00 AM) | NA | as per eye witness On dated 2-08-2022 in the morning due to rain and wind , one conductor of 2-wire LT line of Dabhchatra village was snapped from joint. At the saame time aprox. At 9:00 o'clock , the He -buffalo of owner shri Angari Mehlabhai Nanabhai , grassing at open place was came in contact with live conductore and got electric shok and died on the spot. | CEI Approval pending
134 | PLN | Sembalpani | Dungaisa Kavabhai Khimabhai | FA | Outsider | 11-08-2022 (04:00 pm) | NA | as per eye witness on dated 11-08-2022 due to heavy rain nd wind, the dry pipal tree was fallen on 11 KV padaliya AG feeder line so the line conductore was fall down near to ground. At the same time aprox. At 4:00 o'clock, the Cow of owner sh. Dungaisa Kavabhai Khimabhai, grassing at open place was came in contact with live conductore and got electric shok and dide on the spot. | CEI Approval pending
135 | PLN | Sherpura(M) | Suthar Jogaram Nanaram | FH | Outsider | 13-08-22 @10:00 A.M | NA | During working of making drilling in wall for fixing of Handle (Made by Stainless Steel S.S.) with help of hand drill machine in new constructed house by any reason,leakage current flow from handrill machine to victim.Thus,Victim got electrocuted himself and died on the spot. power taken from nearby house by jointing illegaly wiring connection for carpenter work | CEI Approval pending
136 | PLN | Arnivada | Rabari Chandubhai Jamabhai | FA | Outsider | 18.08.22 @16:30 hrs. | NA | Cow gazing grass under line of 11KV Gajnipur feeder, and at that time 11KV Gajnipur feeder conductor broken and in contact with Kartik feeder LT Line. After conductor broken cow in contact with live conductor and got electrocuted and died. | CEI Approval pending
137 | PLN | Kanodar | Ashishbhai Mukeshbhai Keshani (Vadi) | NFH | Outsider | 22-08-22 @10:15 A.M | NA | Without informing UGVCL ,the victim during tree cutting work,tree branch fallen on 11kv Kanodar JGY Feeder and victim Got Electrolyte of line via tree branch fallen on line and victim got injured | CEI Approval pending
138 | PLN | Nava Nesda | Laljibhai Devshibhai Kanbi | NFH | Outsider | 26.08.22 @11:15 hrs | NA | On dt.-26.08.22 Bhildi Sdn vigilance team went for check connection I/r. Shri Kanbi Devsibhai Narsungbhai, consumer No.-71716/00326/1. At that time victim was afraid to see vegilance team and reached in to electric room to remove cable of direct connection and got electric shock and fall down on earth and met with Non Fatal Accident. | CEI Approval pending
139 | MSH | Medha | Rahul Harmangalsinh | NFHMech) | Outsider | 07-09-2022, 08:00 a.m. | NA | As Per Eye Witness A Non Fatal Human Mechanical Accident Occurred To Shri Rahul Harmangalsinh,Village-Medha,Ta-Kadi,A Victim Was Standing Near By H.T.Consumer Ctpt And Ctpt Blast May Be Any Internal Abnormalities And Ctpt Fire And Very Hot Oil Spread On Victim Whole Body And At That Time Victim Body Was Burnt.And Victim Is Under Medical Treatment & Shifted At Gandhinagar S.V.M.S.Hospital | No |  |  | Mechanical Accident Ctpt Internal Technical Fault & Oil Spread On Victim
140 | MSH | INDRAD | Titabhai Bhurabhai Garval | FH | Outsider | 08.07.22 8:15 AM Reported on 08.09.2022 | NA | A victim was working on the newly construction work of new company office. As per the statement and police punchnama, a victim was removing the iron pharma of wall construction work and standing on palak by iron rod. While removing iron pharma by iron rod by mistake the victim came in contact with 11 kv line by iron rod and the victim got electrocuted and died at sight. This accident was occurred on dt. 08.07.2022 and UGVCL Kadi-2 sdn office was informed by Nandasan police station on dt. 05.09.2022. | No |  |  | K-2 Sdn Issued Notice To Consumer For Safe Clearance, Party Has Applied That Line Shifting Work By Providing U/G Work and is Under progress
141 | MSH | Ambod | Name Of Victim = (1) Bariya Anilbhai Kidiyabhai, (2) Bariya Shantaben Kidiyabhai. | FH | Outsider | 07.09.2022 | NA | In victim's house the supply wire of fan is touched with roof support iron pipe and Vice-verses iron roof sheet. The cloth drying iron wire is tied with roof which is used for drying wet cloths. Victims come in touch with cloth drying iron wire and got electrod. | No |  |  | People were educated to install ELCB at their premises
142 | MSH | MANSA GIDC MANSA | Saroj Ashokkumar Rambali | FH | Outsider | 14.09.2022 | NA | Due to internal fault of three phase fan leakage current found on body of three phase fan and Victim had come in touch with three phase fan’s body and got electrocuted. | No |  |  | People were educated to install ELCB at their premises
143 | MSH | PLOT NO. 40, ISCON INDUSTRIAL ESTATE, NUGAR | Parmar JIvarajbhai Nathubhai (Age Approx. 20 years ) | FH | Outsider | 19.09.2022 at 11:25 Hrs. | NA | As the wall construction work of first floor of plot no.40 at iscon industrial estate was going , The victim was going to handle the 6 feet long aluminum box pipe and accidently the pipe touched with the conductor of 11 KV line of Shivalik JGY feeder passing nearer to the plot.and got electric shock. The victim immediately admitted to Civil Hospital, Ahmedabad. | No |  |  | People were eductaed to keep safe distance from UGVCL Network
144 | MSH | Limbodara | Maheriya Gopalbhai Motibhai | FH | Outsider | 25.09.2022 | NA | The Victim was climbed illegally on existing two wire LT line pole to attach bulb holder and somehow he was felt down on RCC road and declared died by civil hospital Gandhinagar. (Actual reason of accident may be precisely decided after receiving PM report from hospital) | No |  |  | People were eductaed to keep safe distance from UGVCL Network
145 | MSH | Ambaghata | COW OF SHRI. THAKOR DALPUJI SHANKARJI(Approx 2 Years Old) | FA | Outsider | 27.09.2022 AT-5.30 PM | NA | The Said Accident Occurred On Dtd.27.09.2022 At About 5.30 Pm,This Accident Occured Due To One Conductor Of Lt Line Is Broken And Fallen On Cow And Cow Electroduced And Died On The Spot. | No |  |  | Due to water flow ,tree near lt line is tilted and tuched to LT line onductor are removed and rejoint broken conductor.
146 | PLN | sidhpur | Patani Sahil Bhaichandbhai | FH | Outsider | 7.9.22 (8:45AM) | NA | Victim was trying to climb on iron butteriness with the help of iron pipe on staning iron gate of house & he got electrocuted due to current & he die. Current was coming due to fan wire insulation was damaged & this damaged insulation wire was in touch with iron wire was touch with iron angle & this iron angle was in touch with iron pipe. | CEI Approval pending
147 | PLN | Rah | Parmar Hansabhai Hardasbhai | FA | Outsider | 12.9.2022 at 6:00 Hrs. | NA | On dtd.12.9.2022 at 6 a.m. buffalo of Shri Hansabhai Hardasbhai Parmar was grazing and suddenly came in direct contact with broken LT wire which was broken due to heavy wind on dt.11.9.2022 night and got electrocuted and died on the spot. | CEI Approval pending
148 | PLN | Bhopanagar, Deesa | Masharubhai Bhagabhai Majirana | FH | Outsider | 19.09.2022 @18:00Hrs | NA | Victim had trying to enter his own house, he came in contact with live electric wire of own house internal wiring, and he got sock and met with fatal human electrical accident. Intarnal wiring was deteriorated at many places. | CEI Approval pending
149 | HMT | Nana Bhachadiya | Shri Kalpeshkumar Malusinh Jadeja | FH | Outsider | 5.9.2022 | NA | AN INCIDENT WAS OCCURRED AT VILLAGE NANA BHACHADIYA IN AGRICULTURE LAND OF CHAUHAN BALUSINH CHHAGANSINH,WERE 11KV KUMAPUR AG FEEDER PASSES THROUGH AGRICULTURE LAND OF CHAUHAN BALUSINH CHHAGANSINH OF NANA BHACHADIYA VILLAGE, AT 09:15 AM VICTIM JADEJA KALPESHKUMAR MALUSINH OF VILLAGE NANA BHACHADIYA CLIMB ON 11KV KHUMAPUR AG FEEDER TAPPING SHACKLE POLE FOR SUICIDE AND FOR SUICIDE HE TOUCH TO LIVE 11KV KHUMAPUR AG LINE SHACKLE POLE CONDUCTOR AND GOT ELECTROCUTED AND DIED. DETAIL INVESTIGATION UNDER PROCESS. | CEI PENDING
150 | HMT | HELODAR | Pagi Jeshabhai ramtubhai | FH | Outsider | 10.9.2022 | NA | ACCIDENT OCCURRED AT VILLAGE HELODAR ON DATED 10-9-22 AT APROX TIME 15:00 IN THE FARM OF PAGI JESHAJI RAMTUJI NEAR A2 TERIFF AG CONNECTION WHEN VICTIM WAS TRYING TO SWITCH ON THE MOTOR WITH THE STARTER. THE INTERNAL WIRING IN STARTER IS DAMAGED AND SHOT. VICTIM WAS STARTED THE STARTER AND GOT ELECTROCUTED AND DIED ON THE SPOT THE ACCIDENT OCCURRED CONSUMER PREMISE SO UGVCL IS NOT RESPONSIBLE | CEI PENDING
151 | HMT | BHERUNDA | Shri Patel Kalpeshkumar Shamalbhai | FH | Outsider | 11.9.2022 | NA | ACCIDENT OCCURRED AT VILLAGE BHERUNDA ON DATE 11.09.2022 AT APPROX 5 PM IN THE FARM OF PATEL SHAMALBHAI VELABHAI NEAR A1 TARIFF AG CONNECTION WHEN THE VICTIM WAS TRYING TO SWITCH ON THE MOTOR WITH THE STARTER PLACED IN THE IRON BOX. THE SERVICE CABLE WAS VERY OLD AND WAS TIED TIGHTLY WITH IRON ANGLE UPON WHICH THE STARTER BOX WAS PLACED, AS THE SERVICE CABLE WAS OLD AND AGED SLIGHTLY CUT/PUNCUTURED FROM THE POINT WHERE IT WAS TIED DUE TO RUSTING OF IRON ANGLE. DUE TO RAINY WEATHER,HANDLE OF THE STARTER BOX WAS WET WHEN THE VICTIM TRIED TO OPEN THE BOX HE CAME IN CONTACT WITH LEAKAGE CURRENT THAT FLOWED FROM THE CUT PART OF THE SERVICE CABLE VIA IRON ANGLE AND HANDLE OF THE STARTER BOX AND GOT ELECTROCUTED AND DIED. MOREOVER, NO ANY COMPLAIN WAS RECIEVED EARLIER FROM THE CONSUMER FOR REPLACEMENT OF DETERIORATED/OLD CABLE. | CEI PENDING
152 | HMT | RADHIWAD | RABARI DASHRATHBHAI VIRABHAI | FA | Outsider | 13.9.2022 | NA | ON DATED 13-9-22 AT APROX TIME 10:30AM AT RADHIVAD GUNDEL ROAD BEHIND MAHAKALI MANDIR, THE BUFFALO PASS NEAR 11KV BORADI JGY TRANSFRMER FENCING AND CAME INTO CONTACT WITH FENCING IT MAY BE DUE TO FAULTY APPARTUS AND SUDDENLY FELL DOWN AND DIED ON THE SPOT. DURING SITE VISIT THERE WAS NO ANY LEKAGE CURRENT FOUND.THE DETAIL INVESTIGATION UNDER PROCESS. | CEI PENDING
153 | HMT | KHILODIYA | MAKVANA KETANSINH SHIVSINH | NFH | Outsider | 16.09.2022 | NA | ON DT:16.09.2022 TIME APPROX 11.30 AM AS PER INSTRUCTION FROM GRAM PANCHAYAT TO COLOUR WORK GIVEN TO VICTIM TO WHOSE HOUSE BUILT BY CEMENT SHEET ON TOP OF HOUSE.VICTIM CLIMB UP THE HOUSE OF ANVARSINH KUBERSINH AND DOING COLOUR WORK,SUCH TIME 11 KV JALARAM AG FDR LINE PASSING FROM TOP OF THE HOUSE VICTIM SOME HOW CONTACT WITH LIVE CONDUCTOR AND GOT ELECTROCUTED AT SITE.SAME TIME JALARAM AG FDR DRAWN 1 PH POWER AND NO ANT TT COME OUT AT SS END. | CEI PENDING
154 | SBT | Pethapur | Desai Babubhai Ranchhodbhai | FA | Outsider | 02.09.2022 | NA | A Crowd of cows were grassing & watering purpose nearer to owner's house after that all of it goes back to its owner's house while that one of cow & second cow whose calf was in its stomach might be in contact with JIO tower TC & got electrocuted due to that one nos of cow died on the spot & second cow's calf died in its stomach as owner said. | Yet not received |  |  | service wire rectified | 0
155 | SBT | Bakrol | Tapan Mahanto | FH | Outsider | 22.08.2022 | NA | AS PER EYE WITNESS STATEMENT ON DT: 03.09.2022 HYDRA DRIVER SHRI MAHESHKUMAR ARVINDKUMAR WAS PRESENT FOR WORK OF TRANSFERRING I-BIM TO OTHER SHED , AFTER BINDING APPROX 24 FT LONG I-BIM THROUGH SYNTHETIC BELT HE CAME OUTSID PLOT NO. E-1, SWAGAT IND. ESTATE, BAKROL. VICTIM AND OTHER ONE WAS THERE TO SUPPORT THE I-BIM EXTERNALLY. NEAR PLOT NO. E-1, 11 KV SHREEJI FEEDER LINE WAS PASSING THROUGH ROAD CROSS LINE, AT THAT TIME IT WAS RAINING . HYDRA REACH NEAR THE ROAD CROSS LINE, BOOM OF HYDRA TOUCH THE 11 KV LINE , AT THE SAME TIME VICTIM WAS IN CONTACT OF I-BIM AND GOT ELECTROCUTED. | Yet not received |  |  | MAINTENANCE DONE | 0
156 | SBT | KHATRAJ | A Cow of Shri Rabari Rameshbhai Mehulbhai and A Cow of Shri Rabari Amaratbhai Ramjibhai | FA | Outsider | 10.9.2022 | NA | As per police station,Santej informed on Dt.12.09.2022,Site visited by SDO on 13.09.2022 and got detail about Fatal Accident occurred to two nos. of cow, on Dt.10.09.2022 at Vill.Khatraj.On Dt.10.09.2022 due to heavy rain with tremendous thunderstorm,LT wire of 11 KV Rama multitech fdr,was broken (at the time of panchnama new joints of wire are seen at site)and as per statement of owners of cow, the cows may came in contact with leakege of current and may got elctrocuted .As per PM report cause of both cow is electric shock. | Yet not received |  |  | CONDUCTOR REPLACED | 0
157 | SBT | Devdi | Dashrathbhai Ratilal Thakor | FA | Outsider | 11.09.2022 | NA | As per report 3Ph 4W LT conductor was snapped due to heavy wind and rainfall (cyclone) on gamdi ag near Mahadev Mandir Devdi on 11.9.22 as wire was snapped and lying on farm (open land) so, during that moment buffalo was grazing and came in contact with live wire got electrocuted and died. | Yet not received |  |  | LT SPACER PROVIDED | 0
158 | SBT | Dhanot | Jayram Karamsibhai Rabari | FA | Outsider | 12.09.2022 | NA | on dtd.12.9.22 at around 4.30PM buffalo and calf went for grass feeding and was came in contact with one broken LT wire so got electrocuted and died | Yet not received |  |  | 11 KV Dhanot ag fdr maintanance done | 0
159 | SBT | Kamalbandh Vasna | Solanki (Thakor) Ramtuji Budhaji | FA | Outsider | 12.09.2022 | NA | LT phase wire of 1ph LT line snap due to heavy tree branch fallen on LT line from nearby neem tree and buffalo was under this lt line. Due to that buffalo electocuted and died on the spot. | Yet not received |  |  | work done for restringing of conductor | 0
160 | SBT | Pinglaj | Dabhi Jayabhai Laljibhai | FA | Outsider | 12.09.2022 | NA | According to the report of the police station today, while inspecting the site of the 3ph 4w LT line of the 11 kv Radhu Ag fdr going into the Gauchar land was broken due to the cyclone and heavy wind and lying at ground of gauchar land, due to this 2 buffaloes grazing nearby came in contact with the conductor and both the buffaloes were electrocuted and died. | Yet not received |  |  | MAINTENANCE DONE | 0

## SoP 003
Uttar Gujarat Vij Company Limited
QUARTER :- 2nd (July- 22 to Sept. - 22)
Performa SoP 003 B:
APPENDIX - B
REGISTER FOR COMPILING THE COMPLAINTS CLASSIFICATION WISE
Classification | Pending complaint of previous quarter | Complaints received during the quarter | Total complaints | No.of complaints redressed during the month |  |  |  |  | Balance complaints to be redressed (4) - (9) | Classification of complaint
|  |  |  | In stipulated time |  | Beyond stipulated time |  | Total (5) to (8)
|  |  |  | Within 50% of stipulated time | Within stipulated time | Upto double the stipulated time | More than double the stipulated time
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11
A(i) | 0 | 44916 | 44916 | 35603 | 9313 | 0 | 0 | 44916 | 0 | Loose conn. from pole
A(ii) | 0 | 21304 | 21304 | 17662 | 3642 | 0 | 0 | 21304 | 0 | Int.due to line breakdown
A(iii) | 0 | 6008 | 6008 | 3079 | 2929 | 0 | 0 | 6008 | 0 | Interruption due to failure of transformer
B(i) | 0 | 2377 | 2377 | 912 | 1465 | 0 | 0 | 2377 | 0 | Ordinary case, which requires no augmentation
B(ii) | 0 | 2455 | 2455 | 761 | 1694 | 0 | 0 | 2455 | 0 | Where augmentation is required
C(i) | 0 | 9832 | 9832 | 5560 | 4272 | 0 | 0 | 9832 | 0 | Stopped/Defective Meters
C(ii) | 0 | 4816 | 4816 | 3625 | 1191 | 0 | 0 | 4816 | 0 | Billing on average basis for more than two bills
D(i) | 0 | 4161 | 4161 | 2807 | 1354 | 0 | 0 | 4161 | 0 | Loose Wires
D(ii) | 0 | 814 | 814 | 485 | 329 | 0 | 0 | 814 | 0 | Inadequate ground clearance
E(i) | 0 | 2368 | 2368 | 1724 | 644 | 0 | 0 | 2368 | 0 | For current bills where no additional information is required
E(ii) | 0 | 2826 | 2826 | 1525 | 1301 | 0 | 0 | 2826 | 0 | Where additional information relating to correctness of reading etc. is required
F(i) | 0 | 1548 | 1548 | 636 | 912 | 0 | 0 | 1548 | 0 | Where extension of mains is not required
F(ii) | 0 | 503 | 503 | 312 | 191 | 0 | 0 | 503 | 0 | Where extension of mains is required
F(iii) | 0 | 2129 | 2129 | 1429 | 700 | 0 | 0 | 2129 | 0 | Modification in connected load
F(iv) | 0 | 4614 | 4614 | 3395 | 1219 | 0 | 0 | 4614 | 0 | Name change/reconnection
G | 0 | 1012 | 1012 | 806 | 206 | 0 | 0 | 1012 | 0 | Refund of amount due in regard to temporary connection
H | 0 | 14129 | 14129 | 11388 | 2741 | 0 | 0 | 14129 | 0 | Others
Total | 0 | 125812 | 125812 | 91709 | 34103 | 0 | 0 | 125812 | 0

## SoP 004
Uttar Gujarat Vij Company Limited
QUARTER :- 2nd (July - 22 to Sept.- 22)
Performa SoP 004
Sr. No. | Actions or steps carried out by UGVCL towards public awareness in the quarter | Likely number of consumers influenced | Details about media
1 | Display board of SOP at circle, Division & S/Dn | 127548 | Notice Board
2 | Display board of Name of information officers under RTI Act 2005 at Circle,Division,Sub- division offices. | 120177 | Notice Board
3 | Consumer care centers at various places | 146996 | Verbal & Notice Board at CCC
4 | Advertisement through Daily News papers | 238840 | Daily News papers
5 | Pamphlets distributed among public | 232463 | Pamphlets
6 | Advertisement through slide in TV / Banners | 169012 | T V Channels
7 | On Web site of Uttar Gujarat Vij Company Limited | 188030 | Internet
8 | Through Regular Energy Bills | 3166968 | Energy Bill
9 | Others | 441 | CD

## SoP 005
Uttar Gujarat Vij Company Limited
QUARTER :- 2nd (July - 22 to Sept.- 22)
YEAR :- 2022-23
Performa SoP 005 B: Action taken report by the Redressal Committee
Sr. No. | Month | Date and time meeting conducted | No. of complaints registered at the meeting | No. of complaints pending at the end of the meeting | Nos of cases Disposed | Location of Hearing
1 | July.22 | 08.07.2022 | 4 | 1 | 3 | Circle office Sabarmati
|  | 22.07.2022 | 3 | 0 | 3 | Circle office Sabarmati
|  | 28.07.2022 | 3 | 0 | 3 | Corporate Office, Mehsana
2 | Aug.22 | 06.08.2022 | 2 | 1 | 1 | Circle office Sabarmati
|  | 26.08.2022 | 5 | 2 | 3 | Circle office Sabarmati
3 | Sept.22 | 02.09.2022 | 4 | 2 | 2 | Circle office Sabarmati
|  | 13.09.2022 | 5 | 2 | 3 | Circle office Sabarmati
|  | 17.09.2022 | 2 | 0 | 2 | Corporate Office, Mehsana
|  | 23.09.2022 | 3 | 0 | 3 | Circle office Sabarmati
|  | 30.09.2022 | 1 | 1 | 0 | Circle office Sabarmati

## SoP 006
Uttar Gujarat Vij Company Limited
QUARTER :- 2nd (July- 22 to Sept.- 22)
Performa SoP 006 : Failure of Distribution Transformer.
Sr. No. | Class | No. of existing Distribution transformer at the start of the quarter | No.of Distribution transformers added during the quarter | Total number of Distribution transformers | Total number of Distribution transformer failed during the quarter | % failure rate of Distribution transformer
|  | A | B | C=A+B | D | H= (D) * 100/C
1 | 11KV | 366276 | 4333 | 370609 | 11357 | 3.0644
Total |  | 366276 | 4333 | 370609 | 11357 | 3.0644

## SOP011-(AG)
Uttar Gujarat Vij Company Limited
QUARTER :- 2nd (July-22 to Sept.-22)
YEAR :- 2022-23
SoP 011 - A : System Average Interruption Frequency Index (SAIFI) for AG. Dominant Category
Sr. No | Month | Ni - Number of Customers for each sustained interruptions (in numbers) | NT - Total No of customers served (in Numbers) | CI=∑ Ni | SAIFI = ∑ Ni/Nt (Monthly SAIFI)
1 | 2 | 3 | 4 | 5 | 6=5/4
1 | 2022-07-01 | 534520 | 612210 | 2537157 | 4.1443
2 | 2022-08-01 | 509810 | 613590 | 2177113 | 3.5482
3 | 2022-09-01 | 487698 | 614295 | 1971474 | 3.2093
SoP 011 - B : System Average Interruption Duration Index (SAIDI) for AG. Dominant Category
Sr. No | Month | Ri = Restoration Time for each sustained interruption event (in hours) | Ni - Number of interrupted Customers for each sustained interruption event (in numbers) | Ri* Ni - Total customer interruption Duration | NT - Total No of customers served (in Numbers) | Customer Intt. Duration CMI = ΣRi*Ni | SAIDI = ΣRi*Ni/Nt (Monthly SAIDI)
1 | 2 | 3 | 4 | 5 = 3 * 4 | 6 | 7 | 8=7/6
1 | 2022-07-01 | 1902-02-21 06:14 | 534520 |  | 612210 | 2337-11-16 04:16 | 0.26124
2 | 2022-08-01 | 1901-08-02 17:26 | 509810 |  | 613590 | 2248-07-27 05:21 | 0.20749
3 | 2022-09-01 | 1901-06-11 10:40 | 487698 |  | 614295 | 2211-06-24 08:45 | 0.1852
SoP 011 - C : Momentary Average Interruption Frequency Index (MAIFI) for AG. Dominant Category
Sr. No | Month | IMi = Number of Momentary interruptions for the month (in numbers) | Nmi = Total no of customers for each momentary interruptions (in numbers) | Imi =Nmi Number of customer Momentary interruptions (in numbers) | Nt - Total no of customers served (in numbers) | Customer Intt. ΣImi*Nmi | MAIFI=ΣImi*Nmi/Nt
1 | 2 | 3 | 4 | 5 = 3 * 4 | 6 | 7 | 8=7/6
1 | 2022-07-01 | 18133 | 577793 |  | 612210 | 4156671 | 6.7896
2 | 2022-08-01 | 15873 | 569789 |  | 613590 | 3731263 | 6.081
3 | 2022-09-01 | 13945 | 567438 |  | 614295 | 3238988 | 5.2727

## SOP011-(JGY)
Uttar Gujarat Vij Company Limited
QUARTER :- 2nd (July-22 to Sept.-22)
YEAR :- 2022-23
SoP 011 - A : System Average Interruption Frequency Index (SAIFI) for JGY category
Sr. No | Month | Ni - Number of Customers for each sustained interruptions (in numbers) | NT - Total No of customers served (in Numbers) | CI=∑ Ni | SAIFI = ∑ Ni/Nt (Monthly SAIFI)
1 | 2 | 3 | 4 | 5 | 6=5/4
1 | 2022-07-01 | 1785080 | 2125931 | 7880122 | 3.7067
2 | 2022-08-01 | 1737312 | 2129488 | 6717544 | 3.1545
3 | 2022-09-01 | 1729734 | 2131428 | 6113446 | 2.8682
SoP 011 - B : System Average Interruption Duration Index (SAIDI) for JGY category
Sr. No | Month | Ri = Restoration Time for each sustained interruption event (in hours) | Ni - Number of interrupted Customers for each sustained interruption event (in numbers) | Ri* Ni - Total customer interruption Duration | NT - Total No of customers served (in Numbers) | Customer Intt. Duration CMI = ΣRi*Ni | SAIDI = ΣRi*Ni/Nt (Monthly SAIDI)
1 | 2 | 3 | 4 | 5 = 3 * 4 | 6 | 7 | 8=7/6
1 | 2022-07-01 | 1900-06-19 02:02 | 1785080 |  | 2125931 | 334522.6701 | 0.15735
2 | 2022-08-01 | 1900-05-16 17:41 | 1737312 |  | 2129488 | 260071.7562 | 0.12213
3 | 2022-09-01 | 1900-05-16 19:39 | 1729734 |  | 2131428 | 274481.6375 | 0.12878
SoP 011 - C : Momentary Average Interruption Frequency Index (MAIFI) for JGY category
Sr. No | Month | IMi = Number of Momentary interruptions for the month (in numbers) | Nmi = Total no of customers for each momentary interruptions (in numbers) | Imi =Nmi Number of customer Momentary interruptions (in numbers) | Nt - Total no of customers served (in numbers) | Customer Intt. ΣImi*Nmi | MAIFI=ΣImi*Nmi/Nt
1 | 2 | 3 | 4 | 5 = 3 * 4 | 6 | 7 | 8=7/6
1 | 2022-07-01 | 6871 | 2059519 |  | 2125931 | 15478305 | 7.2807
2 | 2022-08-01 | 6080 | 2067941 |  | 2129488 | 13630761 | 6.401
3 | 2022-09-01 | 5266 | 2051346 |  | 2131428 | 11875034 | 5.5714

## SOP011-(OTHER THAN AG-JGY)
Uttar Gujarat Vij Company Limited
QUARTER :- 2nd (July-22 to Sept.-22)
YEAR :- 2022-23
SoP 011 - A : System Average Interruption Frequency Index (SAIFI) for Other than AG & JGY category
Sr. No | Month | Ni - Number of Customers for each sustained interruptions (in numbers) | NT - Total No of customers served (in Numbers) | CI=∑ Ni | SAIFI = ∑ Ni/Nt (Monthly SAIFI)
1 | 2 | 3 | 4 | 5 | 6=5/4
1 | 2022-07-01 | 927147 | 1233584 | 3004983 | 2.436
2 | 2022-08-01 | 800550 | 1237365 | 2325307 | 1.8792
3 | 2022-09-01 | 865772 | 1243033 | 2590235 | 2.0838
SoP 011 - B : System Average Interruption Duration Index (SAIDI) for Other than AG & JGY category
Sr. No | Month | Ri = Restoration Time for each sustained interruption event (in hours) | Ni - Number of interrupted Customers for each sustained interruption event (in numbers) | Ri* Ni - Total customer interruption Duration | NT - Total No of customers served (in Numbers) | Customer Intt. Duration CMI = ΣRi*Ni | SAIDI = ΣRi*Ni/Nt (Monthly SAIDI)
1 | 2 | 3 | 4 | 5 = 3 * 4 | 6 | 7 | 8=7/6
1 | 2022-07-01 | 1900-03-27 22:37 | 927147 |  | 1233584 | 2150-10-21 07:18 | 1:47
2 | 2022-08-01 | 1900-03-03 13:54 | 800550 |  | 1237365 | 2060-05-13 23:56 | 1:08
3 | 2022-09-01 | 1900-03-28 04:39 | 865772 |  | 1243033 | 2172-04-07 19:21 | 1:55
SoP 011 - C : Momentary Average Interruption Frequency Index (MAIFI) for Other than AG & JGY category
Sr. No | Month | IMi = Number of Momentary interruptions for the month (in numbers) | Nmi = Total no of customers for each momentary interruptions (in numbers) | Imi =Nmi Number of customer Momentary interruptions (in numbers) | Nt - Total no of customers served (in numbers) | Customer Intt. ΣImi*Nmi | MAIFI=ΣImi*Nmi/Nt
1 | 2 | 3 | 4 | 5 = 3 * 4 | 6 | 7 | 8=7/6
1 | 2022-07-01 | 2493 | 1041270 |  | 1233584 | 4061254 | 3.2922
2 | 2022-08-01 | 2220 | 963778 |  | 1237365 | 3605214 | 2.9136
3 | 2022-09-01 | 1891 | 926754 |  | 1243033 | 3167180 | 2.5479

## SOP011-(OVERALL)
Uttar Gujarat Vij Company Limited
QUARTER :- 2nd (July-22 to Sept.-22)
YEAR :- 2022-23
SoP 011 - A : System Average Interruption Frequency Index (SAIFI) for UGVCL as a whole
Sr. No | Month | Ni - Number of Customers for each sustained interruptions (in numbers) | NT - Total No of customers served (in Numbers) | CI=∑ Ni | SAIFI = ∑ Ni/Nt (Monthly SAIFI)
1 | 2 | 3 | 4 | 5 | 6=5/4
1 | 2022-07-01 | 3246747 | 3971725 | 13422262 | 3.3795
2 | 2022-08-01 | 3047672 | 3980443 | 11219964 | 2.8188
3 | 2022-09-01 | 3083204 | 3988756 | 10675155 | 2.6763
SoP 011 - B : System Average Interruption Duration Index (SAIDI) for UGVCL as a whole
Sr. No | Month | Ri = Restoration Time for each sustained interruption event (in hours) | Ni - Number of interrupted Customers for each sustained interruption event (in numbers) | Ri* Ni - Total customer interruption Duration | NT - Total No of customers served (in Numbers) | Customer Intt. Duration CMI = ΣRi*Ni | SAIDI = ΣRi*Ni/Nt (Monthly SAIDI)
1 | 2 | 3 | 4 | 5 = 3 * 4 | 6 | 7 | 8=7/6
1 | 2022-07-01 | 1902-11-07 06:53 | 3246747 |  | 3971725 | 586061.1521 | 3:32
2 | 2022-08-01 | 1902-02-20 01:01 | 3047672 |  | 3980443 | 445960.9764 | 2:41
3 | 2022-09-01 | 1902-01-23 10:58 | 3083204 |  | 3988756 | 487693.8083 | 2:56
SoP 011 - C : Momentary Average Interruption Frequency Index (MAIFI) for UGVCL as a whole
Sr. No | Month | IMi = Number of Momentary interruptions for the month (in numbers) | Nmi = Total no of customers for each momentary interruptions (in numbers) | Imi =Nmi Number of customer Momentary interruptions (in numbers) | Nt - Total no of customers served (in numbers) | Customer Intt. ΣImi*Nmi | MAIFI=ΣImi*Nmi/Nt
1 | 2 | 3 | 4 | 5 = 3 * 4 | 6 | 7 | 8=7/6
1 | 2022-07-01 | 27497 | 3678582 |  | 3971725 | 23696230 | 5.9662
2 | 2022-08-01 | 24173 | 3601508 |  | 3980443 | 20967238 | 5.2676
3 | 2022-09-01 | 21102 | 3545538 |  | 3988756 | 18281202 | 4.5832

## SoP 012
Uttar Gujarat Vij Company Limited
Year 2022-23 (April - 22 to Sept. - 22)
Performance SoP 012 - System Losses at EHT / 11 KV and below
SoP 012 - CALCULATION OF SYSTEM LOSSES AT EHT / 11 KV
Losses in 11 KV System and Connected Equipment |  |  |  | Cummulative
i | Energy Delivered into EHT / 11 KV and LT Distribution System from EHT / 11 KV SS (Mus) | A | 14340.3115 | Sent Total
ii | Energy Sold (Billed) EHT direct sales (Mus) | B | 1418.4179 | Sold EHT
iii | Energy Sold (Billed) in the 11 KV LT system (Mus) | C | 11926.6253 | Sold Exl. EHT
iv | Total Sales (Mus) | (B+C) | 13345.0432 | Sold Total
v | Losses (Mus) | {(A) - (B+C)} | 995.2683
vi | % Losses | {(A) - (B+C)} X 100 / (A) | 6.9404

## SoP013
Uttar Gujarat Vij Company Limited
QUARTER :- 2nd (July - 22 to Sept.- 22)
Performa SoP 013 : Meter faults
Consumer Category | No. of faulty meters at the start of the quarter | No. of faulty meters added during the quarter | Total No. of defective / faulty meter | No. of faulty Meters repaired and replaced | No. of faulty meters pending at the end of the quarter
| 1 | 2 | 3=2+1 | 4 | 5=3-4
Single Phase | 1410 | 27059 | 28469 | 26822 | 1647
Three Phase | 630 | 4879 | 5509 | 5069 | 440
Total | 2040 | 31938 | 33978 | 31891 | 2087

## SoP 014
Uttar Gujarat Vij Company Ltd ,Mehsana
QUARTER : April-22 to Sept-22
YEAR: 2022-23
Performa SoP 014: Statement Showing the ATC losses, collection efficiency and Billing Efficiency
Qtr. | Months | Units input (Mus) | Units Billed (Mus) | Billing Efficiency | Revenue Billed (Rs. Crore) | Revenue Collected (Rs. Crore) | Collection Efficiency* % | Business Efficiency | AT & C Losses %
|  | A | B | C=(B/A)*100 | D | E | F=(E/D)*100 | G=(C*F)/100 | H=100-G
I | 2021-04-15 | 2848.4828 | 2393.0405 | 84.0111 | 1219.0163 | 1568.6993 | 100 | 84.0111 | 15.9889
| 2021-05-15 | 2967.9483 | 2476.5133 | 83.4419 | 1342.5643 | 1670.9682 | 100 | 83.4419 | 16.5581
| 2021-06-15 | 2652.8686 | 2487.0619 | 93.7499 | 1373.1568 | 1739.0284 | 100 | 93.7499 | 6.2501
| Sub Total | 8469.2998 | 7356.6157 | 86.8621 | 3934.7374 | 4978.6959 | 100 | 86.8621 | 13.1379
II | 2021-07-15 | 1866.4631 | 2092.4559 | 112.1081 | 1365.7602 | 1628.3586 | 100 | 112.1081 | -12.1081
| 2021-08-15 | 1739.0587 | 1899.6325 | 109.2334 | 1261.1749 | 1702.1184 | 100 | 109.2334 | -9.2334
| 2021-09-15 | 2265.49 | 1996.3391 | 88.1195 | 1327.7796 | 1645.6019 | 100 | 88.1195 | 11.8805
| Sub Total | 5871.0117 | 5988.4275 | 101.9999 | 3954.7147 | 4976.079 | 100 | 101.9999 | -1.9999
Grand Total |  | 14340.3115 | 13345.0432 | 93.0596 | 7889.4521 | 9954.7749 | 100 | 93.0596 | 6.9404
| * | Collection Efficiency above 100% is taken as 100%

## SoP015
Uttar Gujarat Vij Company Limited
Year 2022-23 (Apr. - 22 to Sept. - 22)
Performa SoP 015 : Release of New connection : Status as on 30.09.22
Consumer Category | Total No. of consumers connected at the beginning of half year (i.e. as on Apr-22) | Pending at the beginning of the of the Half year (i.e. as on Apr.-22) | New Applications received during the half-year | No. of Connections released during the Half year | No. of Applications pending at the end of Half year | Total no. of consumers connected at the end of the half year (Sept.-22)
Domestic | 3002543 | 6471 | 74803 | 59514 | 14857 | 3062057
Commercial (GLP) | 26669 | 8 | 586 | 431 | 56 | 27100
Industrial LT (NRGP & LTMD) | 442580 | 2722 | 19313 | 18023 | 5176 | 460603
Agriculture (Total) | 409591 | 25417 | 10779 | 10863 | 22684 | 420454
Industrial HT | 5452 | 34 | 271 | 229 | 40 | 5681
Total | 3886835 | 34652 | 105752 | 89060 | 42813 | 3975895

## SoP016
Uttar Gujarat Vij Company Limited
QUARTER :- 2nd (July- 22 to Sept.- 22)
Performa SoP 016 : Compensation details
COMPENSATION DETAILS
Sr. No. | Event | Compensation | No. of cases where compensation was given (in numbers) | Amt.of compensation paid (in Rs.)
1 | Duty to provide supply | Rs.50 per day of delay from the limit specified in the performance regulations | …NIL… | …NIL…
a) New connection
b) Additional load
c) Temporary supply
d) Shifting service connection
e) Transfer of service connection
f) Change in tariff category of consumer
2 | Complaints in billing | Rs.50 for non reply within the period prescribed in Regulations
3 | Replacement of meters | LT Rs.25 per day of delay maximum Rs.2,500 and HT Rs. 250 per day of delay maximum of Rs. 5,000/-
4 | Interruption of supply | LT Rs.25 for every 6 hrs. of delay maximum of Rs.500 and HT Rs. 50 for every 6 hrs. delay maximum Rs. 1000
5 | Voltage fluctuations and complaints | Rs.50 for failure to visit or convey findings within the stipulated period
6 | Responding to consumers complaints | Rs. 25 for each day of delay maximum Rs. 500
7 | Grievance Handling | Rs. 25 for failure in handling grievance.
| TOTAL :- |  | …NIL… | ……NIL…..