## INDEX
Sr. No | Performa/ Sheet Name | Particulars | Frequency
1 | Sop 001 | Fatal and Non-fatal accident report | Quarterly | Safety | received
2 | Sop 002 | Action taken report for safety measures complied for the accidents occurred | Half Yearly | Safety | received
3 | Sop 003 | Register For Compiling The Complaints {As per Appendix B of the regulation} | Quarterly | Tech-2
4 | Sop 004 | Publicity carried out | Quarterly | Safety | received
5 | Sop 005 | Action taken report by the Redressal Committee II | Quarterly | GERC
6 | Sop 006 | Failure of Distribution Transformer | Quarterly | Tech-2
7 | Sop 007 | Failure of Power Transformer | Quarterly
11 | Sop 011 | Reliability Indices – SAIDI, SAIFI, MAIFI | Quarterly | Tech-2
12 | Sop 012 | System Losses at 66KV and Below | Half Yearly | T & D
13 | Sop 013 | Meter faults | Quarterly
14 | Sop 014 | Statement Showing the ATC losses, collection efficiency and Billing Efficiency | Half Yearly | T & D
15 | Sop 015 | Release of New Connection status | Half Yearly
16 | Sop 016 | Compensation details | Quarterly

## Banner
STANDARD OF PERFORMANCE COMPLIANCE REPORT YEAR : 2022-23
Reported By Pascim Gujarat Vij Company Limited
Submitted To : GUJARAT ELECTRICITY REGULATORY COMMISSION
Report Jul - 2022 to Sep-2022

## 001
Performa - SoP 001: Fatal and Non-fatal accident report
NUMBER OF ACCIDENTS FOR THE QUARTER
Sr.No | Name of Area/Circle | No of accidents in the quarter |  |  |  |  | Cumulative since the first quarter of the current FY year
|  | Departmental |  | Outside
|  | FH | NFH | FH | FA | NFH | FH | FA | NFH
1 | RJC | 1 | 0 | 1 | 0 | 0 | 3 | 0 | 2
2 | RJR | 0 | 1 | 0 | 7 | 2 | 3 | 11 | 4
3 | MRB | 0 | 1 | 3 | 4 | 1 | 5 | 6 | 3
4 | PBR | 0 | 0 | 2 | 11 | 1 | 3 | 15 | 2
5 | JMN | 0 | 1 | 0 | 11 | 1 | 4 | 21 | 10
6 | BHJ | 0 | 1 | 6 | 19 | 0 | 11 | 22 | 2
7 | ANJ | 0 | 0 | 2 | 6 | 2 | 3 | 7 | 3
8 | JND | 0 | 1 | 2 | 11 | 0 | 8 | 13 | 3
9 | BVN | 0 | 3 | 4 | 10 | 0 | 5 | 14 | 6
10 | BTD | 0 | 0 | 0 | 4 | 0 | 2 | 7 | 0
11 | AMR | 0 | 0 | 2 | 20 | 0 | 7 | 22 | 2
12 | SNR | 0 | 0 | 1 | 6 | 0 | 2 | 9 | 0
PGVCL |  | 1 | 8 | 23 | 109 | 7 | 56 | 147 | 37
up to JUN-17 | RJC | 1 | 0 | 2 | 0 | 0 | 3 | 0 | 0
| RJR | 0 | 3 | 5 | 3 | 2 | 5 | 3 | 5
| MRB | 0 | 0 | 3 | 0 | 0 | 3 | 0 | 0
| PBR | 0 | 2 | 0 | 3 | 0 | 0 | 3 | 2
| JMN | 1 | 0 | 3 | 5 | 4 | 4 | 5 | 4
| BHJ | 1 | 0 | 1 | 1 | 1 | 2 | 1 | 1
| ANJ | 0 | 1 | 1 | 6 | 1 | 1 | 6 | 2
| JND | 0 | 1 | 1 | 2 | 1 | 1 | 2 | 2
| BVN | 0 | 0 | 1 | 5 | 0 | 1 | 5 | 0
| BTD | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| AMR | 0 | 1 | 3 | 8 | 1 | 3 | 8 | 2
| SNR | 1 | 0 | 1 | 8 | 0 | 2 | 8 | 0
|  | 4 | 8 | 21 | 41 | 10 | 25 | 41 | 18
up to SEPT-17 | RJC | [5 empty] | 0 | 0 | 0
| RJR | [5 empty] | 0 | 0 | 0
| MRB | [5 empty] | 0 | 0 | 0
| PBR | [5 empty] | 0 | 0 | 0
| JMN | [5 empty] | 0 | 0 | 0
| BHJ | [5 empty] | 0 | 0 | 0
| ANJ | [5 empty] | 0 | 0 | 0
| JND | [5 empty] | 0 | 0 | 0
| BVN | [5 empty] | 0 | 0 | 0
| BTD | [5 empty] | 0 | 0 | 0
| AMR | [5 empty] | 0 | 0 | 0
| SNR | [5 empty] | 0 | 0 | 0
|  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
up to DEC-17 | RJC | [5 empty] | 0 | 0 | 0
| RJR | [5 empty] | 0 | 0 | 0
| MRB | [5 empty] | 0 | 0 | 0
| PBR | [5 empty] | 0 | 0 | 0
| JMN | [5 empty] | 0 | 0 | 0
| BHJ | [5 empty] | 0 | 0 | 0
| ANJ | [5 empty] | 0 | 0 | 0
| JND | [5 empty] | 0 | 0 | 0
| BVN | [5 empty] | 0 | 0 | 0
| BTD | [5 empty] | 0 | 0 | 0
| AMR | [5 empty] | 0 | 0 | 0
| SNR | [5 empty] | 0 | 0 | 0
|  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0

## 002
| Performa – SoP 002: Action taken report for safety measures complied for the accidents occurred | [10 empty] | CEI No. | Date |  |  | Outward No. | Outward Date
Sr | Circle | Location of Accident and details of the victim | Date of occurrence | Type of Accident | Cause of Accident | Findings of CEI / EI / AEI | Remedies suggested by CEI /EI / AEI in various cases | Whether the remedy suggested is complied | Action taken to avoid recurrence of such Accident | Circle Sr. No. | Regulation No. |  | DD | MM | YY |  | DD | MM | YY | UID
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21
1 | RJC | Rajkot , Parshottambhai Mithabhai Makvana | 04.06.22 | NFHOS | On date: 04.06.2022, 11 KV Tax feeder shutdown was pre notified and arranged, Accordingly staff of Bedinaka Sdn were assigned to carry out Tree cutting and other maintenance work on Press road in Tax feeder with Two no’s of contractor person. Shri S J Bheda ALM was supervising the work for tree cutting and creepers removing from DT Center along the press road. Another 11 KV Din Dayal feeder( Power feed from 11 KV Hospital feeder) is also running on the same road. Contractor person Shri Parshotambhai Mithabhai Makwana was removing creepers from TC and climbed on DT-12 of 11 KV Din Dayal feeder instead of 11 KV Tax feeder without seeing feeder name on pole and came in contact with line bottom jumper of TC. Thus he got electric shock and injured in right hand. Then admitted in private hospital for treatment. At present victim is under normal condition. Hence resulting into Human Non Fatal accident occurred in network. | CEI report awaited | NA | NA | Show Cause Notice has been issued to Supervisor Shri S J Bheda vide No RCD-2/HR/106 dt 29.06.22. 'Reply of show cause notice received 07.07.22. Charge sheet issued vide letter NO RCD2/HR/118 dt 25.07.22 . Inquiry proceeding under process. | 1 | [9 empty] | HRCC2223009151
2 | RJC | Rajkot , Vivekbhai Bhupatbhai Vadher | 08.08.22 | FHOS | Vivekbhai Bhupatbhai Vadher and Rajeshbhai Rathod were placing the banner Boards of Gopinathji industries , Industrial area-3, near Maldhari fatak and at that time while placing Banner board on first floor of shop using steel wire to tighten the board at that time that steel wire may come in induction zone of marvel fdr between pole location Mar/008/R001 and Mar/008/R002 and Vivekbhai Bhupatbhai vadher got electrocuted and Rajeshbhai Rathod got injured and both were admitted in Civil Hospital Rajkot for treatment and Vivekbhai Bhupatbhai Vadher was declared dead and Rajeshbhai Rathod is taking further treatment in hospital and on inspection at location site no sparking spot is observed on conductor wire between above location of Marvel feeder as well as no tripping is observed of Marvel feeder during the above accident. | CEI report awaited | NA | NA | Notice Given to Industry vide letter no. HT-3/Tech/Accident/739 Dt. 09.08.22 for unauthorised construction Nr. 11KV line of PGVCL. | 2 | [9 empty] | HRCC2223009334
3 | RJC | Rajkot , Rajeshbhai Bhupatbhai Rathod | 08.08.22 | NFHOS | Vivekbhai Bhupatbhai Vadher and Rajeshbhai Rathod were placing the banner Boards of Gopinathji industries , Industrial area-3, near Maldhari fatak and at that time while placing Banner board on first floor of shop using steel wire to tighten the board at that time that steel wire may come in induction zone of marvel fdr between pole location Mar/008/R001 and Mar/008/R002 and Vivekbhai Bhupatbhai vadher got electrocuted and Rajeshbhai Rathod got injured and both were admitted in Civil Hospital Rajkot for treatment and Vivekbhai Bhupatbhai Vadher was declared dead and Rajeshbhai Rathod is taking further treatment in hospital and on inspection at location site no sparking spot is observed on conductor wire between above location of Marvel feeder as well as no tripping is observed of Marvel feeder during the above accident. | CEI report awaited | NA | NA | Notice Given to Industry vide letter no. HT-3/Tech/Accident/739 Dt. 09.08.22 for unauthorised construction Nr. 11KV line of PGVCL. | 3 | [9 empty] | HRCC2223009334
4 | RJC | Rajkot , Vinod Kakwaji Baranda | 12.08.22 | FHD | On date 12.8.2022 11 KV Murlidhar feeder eminating from 66 KV GIDC SS was in PF so in order to attend feeder two teams of HT -3 sdn reached at location and found that conductors were snapped near SS. So Team-1(I A Makrani LI, R M Parmar LM, A I Veragi LM, G.N Donga ALM, V K Baranda EA) was engaged in work of conductor joint and simultaneously a message received of tree touching murlidhar feeder on Ramvan road. So Team-2 (A C Joshi LI, A B Tank ALM, A T Gohel ALM) went to that location and engaged in cutting the tree branches. At tree cutting location murlidhar urban feeder and sambhalpur Ag feeder were running in parallel. So while trimming of tree branches a big branch fall between Sambhalpur Ag and murlidhar feeder. As weather was rainy and tree branches are totally wet a returned leakage current might flow from sambhalpur ag to murlidhar feeder. Among Team-1 Sh V K Baranda EA who was doing jumper work at riverside and G N Donga ALM at roadside on same DP structure has experienced an electric shock. Sh V K Baranda became unconscious on pole and than after fall from DP structure. He was admitted to H J doshi and next to Civil hospital where he declared as dead. Actual cause of death can be know after PM report received. 11 KV sambhalpur AG feeder was tripped when incident occurred and black spots are observed on tree branches as well as on conductors of 11 KV Sambhalpur AG Feeder. | CEI report awaited | NA | NA | Explanation asked of Supervisors then Show Cause Notice Issue to Sh A C Joshi (LI-HT3 sdn) Wide Letter No. RCD-3/HR/Cofi./189 Dt.23.09.2022 and Warning Memo issue to I.A.Makrani (LI-HT-3) wide Letter No. RCD-3/HR/Cofi./190 Dt.23.09.2022 | 4 | [9 empty] | HRCC2223009344
5 | RJC | Rajkot , Gopal Narshibhai Donga | 12.08.22 | NFHD | On date 12.8.2022 11 KV Murlidhar feeder eminating from 66 KV GIDC SS was in PF so in order to attend feeder two teams of HT -3 sdn reached at location and found that conductors were snapped near SS. So Team-1(I A Makrani LI, R M Parmar LM, A I Veragi LM, G.N Donga ALM, V K Baranda EA) was engaged in work of conductor joint and simultaneously a message received of tree touching murlidhar feeder on Ramvan road. So Team-2 (A C Joshi LI, A B Tank ALM, A T Gohel ALM) went to that location and engaged in cutting the tree branches. At tree cutting location murlidhar urban feeder and sambhalpur Ag feeder were running in parallel. So while trimming of tree branches a big branch fall between Sambhalpur Ag and murlidhar feeder. As weather was rainy and tree branches are totally wet a returned leakage current might flow from sambhalpur ag to murlidhar feeder. Among Team-1 Sh V K Baranda EA who was doing jumper work at riverside and G N Donga ALM at roadside on same DP structure has experienced an electric shock. Sh V K Baranda became unconscious on pole and than after fall from DP structure. He was admitted to H J doshi and next to Civil hospital where he declared as dead. Actual cause of death can be know after PM report received. 11 KV sambhalpur AG feeder was tripped when incident occurred and black spots are observed on tree branches as well as on conductors of 11 KV Sambhalpur AG Feeder. | CEI report awaited | NA | NA | Explanation asked of Supervisors then Show Cause Notice Issue to Sh A C Joshi (LI-HT3 sdn) Wide Letter No. RCD-3/HR/Cofi./189 Dt.23.09.2022 and Warning Memo issue to I.A.Makrani (LI-HT-3) wide Letter No. RCD-3/HR/Cofi./190 Dt.23.09.2022 | 5 | [9 empty] | HRCC2223009344
6 | RJC | Rajkot , Mansukhbhai Lavjibhai Dholariya | 25.04.22 | FHOS | Today i.e.on Dted.25.04.2022 ,11 KV Vaniyavadi Feeder 's Notified shutdown carried by taking Line clear from 66 kv Lalpark(Nilkanth) S/s wide Line clear Number 139 Time - 07:00 by A V Solanki (Line Man - HT-1) then given peta line clear to Sitaram Enterprise supervisor Shri Dharmeshbhai Chamanbhai Nimavat for General maintenance & dismantle of Ideal 11 KV AB cable ( Dead over head Ab cable ) under Vaniyavadi feeder. By mistake to dismantle work of 11 KV over head AB cable victim climbed on nearby 11KV Veer savarkar Feeder pole and came in contact with live 11KV Veer savarkar line hence electrocuted and fell down , resulting in severe head injuries, During shifting him to Hospital the victim passed away Thus Fatal human contractor person's accident occurred. | CEI report awaited | NA | NA | Notice issued to contractor Sitaram Enterprise vice no.: HT-1/DE/Tech/227 dt: 25.04.2022. 'Reply Received wide inward no.: 194 Dt.:02.05.2022 | 6 | [9 empty] | HRCC2223009104
7 | RJC | Rajkot , Anishbhai Khodidasbhai Makwana | 26.04.22 | NFHOS | As per site visit it is came to reveal that,at the time of incident victim was trying to hang unauthorized advertisement Board on electric line pole. Banner is made with iron support. While doing this work addicentally iron part of banner might be came in contact with conductor of 11 KV gayatri Feeder on electric pole location no Mot/Gay/42. Victim experienced electric shock and fall on ground. There is tripping observed in 11 KV gayatri Feeder at 2.20 AM. Victim is admitted in Civil Hospital for further treatment. | CEI report awaited | NA | NA | Complain Registered against Victim in Police station vide letter no. DE/HT-3/Police Complain/452 Dt. 21.05.22 for unauthorised work on pole of 11KV line. | 7 | [9 empty] | HRCC2223009109
8 | RJR | Kathrota , Sureshbhai Bhagubhai Bavaliya | 01.07.22 | NFHOS | Both Victim were fixing iron pipe with Flag at the top of Mahakali Temple at village Kathrota. Approx. 17 feet long and heavy weight iron pipe tilted due to loss of balance of victims. The iron pipe touched the conductor of 11 KV Krupali JGY feeder two wire line passing on the other side of Village Street opposite temple. The Approx. distance between top of temple And 11 KV line is 10 feet. As the victims were holding the iron pipe with his hands, experienced electrical shock and fell on the terrace Of the Temple. Thus non-fatal electrical accident occurred. There was no tripping recorded in the feeder. Villagers gathered at temple immediately admitted both the victim at Sardhar hospital and then shifted to Civil Hospital Rajkot for further treatment. | CEI report awaited | NA | NA | Village meeting arrange on dated 02.07.2022 and Awareness among general public regarding electrical safety "Keep safe distance from Electrical line & Network of PGVCL" during khedut-shibir & village meeting regularly. | 1 | [9 empty] | HRRC2223009219
9 | RJR | Kathrota , Jayeshbhai Jayantibhai Kukadiya | 01.07.22 | NFHOS | Both Victim were fixing iron pipe with Flag at the top of Mahakali Temple at village Kathrota. Approx. 17 feet long and heavy weight iron pipe tilted due to loss of balance of victims. The iron pipe touched the conductor of 11 KV Krupali JGY feeder two wire line passing on the other side of Village Street opposite temple. The Approx. distance between top of temple And 11 KV line is 10 feet. As the victims were holding the iron pipe with his hands, experienced electrical shock and fell on the terrace Of the Temple. Thus non-fatal electrical accident occurred. There was no tripping recorded in the feeder. Villagers gathered at temple immediately admitted both the victim at Sardhar hospital and then shifted to Civil Hospital Rajkot for further treatment. | CEI report awaited | NA | NA | Village meeting arrange on dated 02.07.2022 and Awareness among general public regarding electrical safety "Keep safe distance from Electrical line & Network of PGVCL" during khedut-shibir & village meeting regularly. | 2 | [9 empty] | HRRC2223009219
10 | RJR | Metoda , Shri Rameshbhai Dafda | 09.04.22 | NFHOS | As per information received from Sh Dineshbhai Maiyatra regarding accident, DE/JE Metoda visited the site immediately. As per site visit, it was found that 11 KV Palace Jgy feeder passes through construction site of Ankurbhai Chandubhai Dangar. Victim Rameshbhai was working at construction site and by mistake touched the 11 KV line and got electric shock and was referred to Rajkot civil hospital. tripping was observed in 11 KV Palace JGY at 9:20 am | CEI report awaited | NA | NA | Estimate given for line shifting on dated 19.04.022,and paid on dated 20.04.2022 ,hence line shifting on dated 20.04.22 | 3 | [9 empty] | HRRC2223009087
11 | RJR | Rampar Beti , She Buffalo of Ghughabhai Khodabhai Bhalgamadiya | 11.07.22 | FA | As per information received and as per statement of Owner of Animal , it is came to know that ,the fatal animal accident occurred to 1 nos. of Buffalo of Sh.Ghughabhai Khodabhai Bhalgamadiya While passing nearby 63 KVA Village TC , Nr. Bus Stand area at Vill: Rampar Beti. On site visit, it is found that there is no leakage current at present. It might be due to rain water accumulated near TC area. Buffalo might experience an electric shock due to step potential or leakage current. | CEI report awaited | NA | NA | 05 nos of earthing reactive again ,earthing wire cover with PVC pipe | 4 | [9 empty] | ARRC2223009263
12 | RJR | Bedla , Buffalo of Gelabhai Gobarbhai Kihla | 13.06.22 | FA | As per information received and as per the statement of owner of victim animal, it is come to know that, fatal accident occurred to 2 nos of buffalo’s of Shri Gelabhai Gobarbhai Kihla, while passing nearby 5 KVA transformer centre at faddang road, Bedla village. On Site visit it is found that, there is no leakage current. But due to rain water accumulated near transformer center, due to leakage current or due to step potential the cow might got electrocuted. Detail cause of accident can be known only after findings and conclusion of PM report and police panchnama. | CEI report awaited | NA | NA | 05 nos of earthing reactive again ,earthing wire cover with PVC pipe | 5 | [9 empty] | ARRC2223009173
13 | RJR | Bedla , Buffalo of Gelabhai Gobarbhai Kihla | 13.06.22 | FA | As per information received and as per the statement of owner of victim animal, it is come to know that, fatal accident occurred to 2 nos of buffalo’s of Shri Gelabhai Gobarbhai Kihla, while passing nearby 5 KVA transformer centre at faddang road, Bedla village. On Site visit it is found that, there is no leakage current. But due to rain water accumulated near transformer center, due to leakage current or due to step potential the cow might got electrocuted. Detail cause of accident can be known only after findings and conclusion of PM report and police panchnama. | CEI report awaited | NA | NA | 05 nos of earthing reactive again ,earthing wire cover with PVC pipe | 6 | [9 empty] | ARRC2223009173
14 | RJR | Bedla , Cow of Khodabhai Mepabhai Kihla | 13.06.22 | FA | As per information received and as per the statement of owner of victim animal, fatal accident occurred to 1 Nos of cow Shri Khodabhai Mepabhao Kihla, while passing nearby 100KVA transformer centre at faddang road, near Ramapir Temple, Bedla Village. On site visit it is found that there is no leakage current or due to step potential the cow might got electrocuted. | CEI report awaited | NA | NA | 05 nos of earthing reactive again ,earthing wire cover with PVC pipe | 7 | [9 empty] | ARRC2223009172
15 | RJR | Motipaneli , Kamleshbhai Bhanjibhai Degama | 14.04.22 | FHOS | Victim Kamleshbhai Bhanjibhai Degama was a labour. At Accident place 3 phase AG connection named Rameshbhai Maganbhai Bhalodiya having 7.5HP, A1 Cat., exists. As per site observation he might climbed on transformer center and came in contact with live phase of 11kv line and got electrocuted and died. Dark spot found on TC Jumper above HT stud and tripping observed on 03:50AM and 04:25AM. | CEI report awaited | NA | NA | Letter written to police for FIR register vide letter no BHAYA/HR/2022/117516.04.22. | 8 | [9 empty] | HRRC2223009091
16 | RJR | Khirasara , Sanjaybhai Sureshbhai Gujarati | 14.06.22 | FHOS | As per information from D D Makwana contractor, DE Metoda immediately visited the accident site and as per statement of eye witness (co-worker) on date 14.06.2022, after removing the do fuse they were doing repairing work of earthing wire of transformer. During this joining of earthing GI wire with transformer channel, one of the thin wire touch the do fuse from live line to dead line and victim got electric shock. Immediately he was referred to civil hospital Rajkot and was declared dead by on duty officer. It was found that Govaliya AG feeder was in single phase power. No tripping was registered on this feeder at 66 KV Khirasara SS. | CEI report awaited | NA | NA | Notice issued to contractor for no provide super vision of labour at site vide letter no MSD/2548/28.06.22 | 9 | [9 empty] | HRRC2223009175
17 | RJR | Kothariya , He Buffalo of Rajesh Navghan Sindhav | 17.07.22 | FA | As per information received from sarpanch of village Kothariya, about said animal fatal accident occur to a buffalo of shri sindhav Rajeshbhai navghanbhai in PGVCL Network on dated 17.07.2022 at time 8:00 am (app) DE ronki sdn has visited accident site on dated 17.07.2022 at 5:00 pm for departmental procedure, investigation @ found that LT line conductor of village transformer DT-23 was broken due to heavy wind pressure and rain, while buffalo passing near to this location get electric shock and died. | CEI report awaited | NA | NA | New LT line conductor replace with old one which was broken due to heavy wind pressure and rain, | 10 | [9 empty] | ARRC2223009319
18 | RJR | Kotda Nayani , She Buffalo of Kanabhai Gigabhai Varu | 17.07.22 | FA | As per telephonic information received at fault centre Ronki about above fatal accident occur to a she buffalo of shri kanabhai gigabhai varu in PGVCL Network on dated 17.07.2022 at time 12:00 pm (apx). DE ronki sdn has visited accident site on dated 18.07.2022 at 11:30 am for departmental investigation and found that one of the LT line conductor of transformer no DT-220 (11 KV Kotda AG) was broken due to rainy and stormy atmosphere and snapped on the she buffalo who was grazing under the LT line. As contact with live conductor she buffalo got electric shock and died. | CEI report awaited | NA | NA | New LT line conductor replace with old one which was broken due to heavy wind pressure and rain, | 11 | [9 empty] | ARRC2223009320
19 | RJR | Hadamtala , Owner of Cow Sh.Khimjibhai Versibhai Ratadiya | 18.07.22 | FA | As information received, immediately a site visit was taken by SDO and observed that a dead body of a cow was found on site. At this location, 1 span of 1 LT wire (deteriorate) found broken due to heavy rain and wind. According to the statement of eye witness victim cow of Sh.Khimbhai vershibhai Ratadiya was grazing near to this location and it may came in contact with this broken LT wire and electrocuted. | CEI report awaited | NA | NA | New LT line conductor replace with old(deteriorated) one which was broken due to heavy wind pressure and rain, | 12 | [9 empty] | ARRC2223009286
20 | RJR | Amreli , Buffalo of Navghanbhai Sidhabhai Tariya | 24.07.22 | FA | As per information received telephonically at fault centre about said animal fatal accident occur to a buffalo of shri Navghanbhai sidhabhai tariya & Ashokbhai vaghjibhai vanahar in PGVCL Network on dated 24.07.2022 at time 11:00 am (app) JE ronki sdn has visited accident site and found that tree branch fallen on LT line conductor due to heavy wind and pressure while buffalos were passing near this location buffalos got electric shock and died. | CEI report awaited | NA | NA | Re-conductoring done of LT line and necessary tree cutting done. | 13 | [9 empty] | ARRC2223009308
21 | RJR | Amreli , Calf of Navghanbhai Sidhabhai Tariya | 24.07.22 | FA | As per information received telephonically at fault centre about said animal fatal accident occur to a buffalo of shri Navghanbhai sidhabhai tariya & Ashokbhai vaghjibhai vanahar in PGVCL Network on dated 24.07.2022 at time 11:00 am (app) JE ronki sdn has visited accident site and found that tree branch fallen on LT line conductor due to heavy wind and pressure while buffalos were passing near this location buffalos got electric shock and died. | CEI report awaited | NA | NA | Re-conductoring done of LT line and necessary tree cutting done. | 14 | [9 empty] | ARRC2223009308
22 | RJR | Amreli , Buffalo :of Ashokbhai Vaghjibhai Vanahar | 24.07.22 | FA | As per information received telephonically at fault centre about said animal fatal accident occur to a buffalo of shri Navghanbhai sidhabhai tariya & Ashokbhai vaghjibhai vanahar in PGVCL Network on dated 24.07.2022 at time 11:00 am (app) JE ronki sdn has visited accident site and found that tree branch fallen on LT line conductor due to heavy wind and pressure while buffalos were passing near this location buffalos got electric shock and died. | CEI report awaited | NA | NA | Re-conductoring done of LT line and necessary tree cutting done. | 15 | [9 empty] | ARRC2223009308
23 | RJR | Gomta , Cow of Raghubhai Jinkabhai Ghodasara | 26.06.22 | FA | As information received from Shri. Raghubhai Jinkabhai Ghodasara owner of Cow regarding the 1 no. Fatal Animal accident, JE Gondal Rural-2 visited the site and found that, LT line conductor was broken due to heavy rain and wind pressure, at that time the cow was passing near muddy area for water drinking and came in contact with broken live conductor and got electrocuted. | CEI report awaited | NA | NA | New LT line conductor provide ,which was broken due to heavy rain and wind pressure, | 16 | [9 empty] | ARRC2223009205
24 | RJR | Jasdan , Cow of Kalubhai Lakhabhai Sariya | 27.04.22 | FA | As per information received from cows owner JE of Jasdan SDn visited the site and found that due to electric shock to no 02 cows, near ramvadi selu gauchar land and 11 KV Ganjivada AG fdr was on live. As per site inspection, they have come to know that, the cows came in contact with broken conductor near to DP with AB switch structure, So two cows came in contact of broken conductor and got electric shock and both died. Feeder was on live. | CEI report awaited | NA | NA | New conductor provide ,which was broken due to heavy rain and wind pressure, | 17 | [9 empty] | ARRC2223009112
25 | RJR | Jasdan , Cow of Kalubhai Lakhabhai Sariya | 27.04.22 | FA | As per information received from cows owner JE of Jasdan SDn visited the site and found that due to electric shock to no 02 cows, near ramvadi selu gauchar land and 11 KV Ganjivada AG fdr was on live. As per site inspection, they have come to know that, the cows came in contact with broken conductor near to DP with AB switch structure, So two cows came in contact of broken conductor and got electric shock and both died. Feeder was on live. | CEI report awaited | NA | NA | New conductor provide ,which was broken due to overloading , | 18 | [9 empty] | ARRC2223009112
26 | RJR | Bakhalvad , Nitaben Ramjibhai Palaliya | 28.07.22 | NFHOS | As per Information received, both DE and JE of Atkot Sdn, Visited the accident site. As per site visit, it has come to know that, victim was going to home, with her husband in rickshaw (chhakado) filled with grass from farm. This rickshaw was fully loaded with grass and the victim was sitting on the grass while her husband was driving the rickshaw. During this journey, while approaching ganga jadi marg, 11KV Dungarpur AG feeder was in single phase, While rickshaw was crossing this line, at same time, one phase of conductor of 11KV Dungarpur AG broken from the tapping jumper and fall on the head of victim. Thus non-fatal electrical accident occurred. There was no tripping recorded in this feeder. Villagers gathered at Site and immediately admitted the victim at Virani Hospital Jasdan for further treatment. Conductor was broken from jumper point, which was weak due to sparking and weather effect. | CEI report awaited | NA | NA | D-type jumper provide and conductor replacement doe of top wire. Awareness among general public regarding electrical safety "Keep safe distance from Electrical line & Network of PGVCL" during khedut-shibir & village meeting regularly. | 19 | [9 empty] | HRRC2223009310
27 | RJR | Hadala , Shri Sureshbhai Mansukhbhai Kukadiya | 31.05.22 | FHOS | As per information received from Akila News Paper dt 01.06.2022 about said fata outsider network occurred to sh. Sureshbhai Mansukhbhai Kukadiya app 40. As per site visited by I/C DE Ronki V B Mera and JE Ronki J N Patel , as illegal construction of tea stall on road side under our existing 11 KV Shakti AG feeder, earth filling was done under 11 KV line and distance from ground was reduced and tea stall was constructed on that earth filling . During construction of stall roof, victim threw iron wire ti tighten the roof, the wire came in contact with 11 KV live line, due to which victim got electric shock and was referred to Rajkot civil hospital. TT was recorded in 11 KV Shakti AG at Vijaynagar SS at 19:00 to 19:05 | CEI report awaited | NA | NA | Letter written to police for fir of illegal construction near to pgvcl network RNSD/TECH/3195 DT-08.06.2022 | 20 | [9 empty] | HRRC2223009148
28 | RJR | MERVADAR,Buffalo of Sh Bhurabhai Surabhai Karamta | 15.09.22 | FA | After receiving telephonic information on dated 15.09.2022 at 09:20 from Line inspector that animal fatal accident occurred at Mervadar village Near Shamjibhai Parshotambhai Gediya TC. Immediately JE rush to the accident site. And observing the return leakage current might be flown through Transformer neutral wire to earth and due to that step potential was created near distribution transformer earthing at ground level. The water logging around the TC area due to the rainy season. When buffalo was passing near distribution transformer centre, It was caught up in step potential through front 2 legs, got electrocuted and died on site. | CEI report awaited | NA | NA | 05 nos of new earthing provide with PVC pipe | 21
29 | RJR | GONDAL,MUKESHBHAI MANSUKHBHAI MAKWANA | 14.09.22 | NFHD | On dated14.09.2022, 11KV Old kotda ag feeder was in fault from 19:20 hrs. In which feeder fault, faulty D.O. pin was found on transformer center location no.: KSS/OKT/102/R032/DT248-Cap: - 10 KVA, then after this faulty pin was replaced and feeder rectified at 22:25 hrs. by Sh.Mukeshbhai Makwana with other three night shift line staff with vehicle during heavy rain and wind. After power restored, victim found that D.O. fuse wire is blown on this transformer. Due to night time and heavy rain with wind, victim was unable to bind this D.O. wire from ground level due to bad geographical situation of ag land. Hence, victim climb on transformer pole, and try to bind D.O. fuse wire with used D.O. rod and with wearing hand glows. Anyhow victim lost his balance on pole and at that time he may be came in contact or live induction zone of transformer center D.O. fuse. Hence he got electrical shock and got non-fatal electrical accident. Immediately he was admitted at the Hospital-Gondal for primary treatment. Victims had carryout safety gadgets with him, also he had utilized hand glows and helmet, D.O. Rod during work execution. | CEI report awaited | NA | NA | Accidently came in contact ,victim at present hospitalised | 22
30 | RJR | PEDHALA,BUFFALO OF SH.BHIKHABHAI PUNJABHAI AAL | 28.09.22 | FA | when buffalo was passing on rough road of pedhla-jetalsar at that time buffalo’s horn stuck with the rod side guy of 'jagdish dying valu 25 KVA TC' and buffalo continue moving forward with stacked guy wire thus guy wire broke down from guy rod and this broken guy wire came in contact with live wire from DO fuse to 11 KV bushing of transformer it got electric shock and electrocuted, resulting into animal fatal accident. | CEI report awaited | NA | NA | New guy wire provided which was broke down due to buffalo’s horn stuck with the guy wire. | 23
31 | MRB | Valasan , Miss. Payal Shyambhai Kharadi | 02.06.22 | FHOS | As per site visited by DE Wankaner Rural 1 jointly with EE WKR DO , it is came to know that accident took place in the farm of AG consumer namely Shri Yunus Jiva Bhoraniya having Con.No :34747/00469/6, Load:7.5 HP. From site visit, it is seen that farmer Sh. Yunus Jiva Bhoraniya has newly constructed Room in his farm adjacent to 11KV line hence vertical distance from 11KV line to roof of room becomes 0.5 mtr only & which is not safe as per safety rules. On dated 02.06.2022 Time Approx. 12:15 HRS, both victims was playing on roof of that room with iron rod having length of 5 feet. Meanwhile, iron rod came in direct contact with 11KV live conductor and both victim got electrocuted and during preliminary treatment at Civil hospital, wankaner Miss Payal Shyambhai Kharadi declared dead by on duty doctor while Mr. Vishal Shyambhai Kharadi referred at civil hospital rajkot after primary treatment. Sparking spots on iron rod, 11KV conductor and on roof of room observed during site visit. However. As per record of 66KV Mitana SS, No tripping observed around accident time. | CEI report awaited | NA | NA | Notice Issue for remove illegal construction. Notice No-SDOWKR1/T/15698/03.06.2022 & Awareness among general public regarding electrical safety "Keep safe distance from Electrical line & Network of PGVCL" during khedut-shibir & village meeting regularly | 1 | [9 empty] | HMRB2223009150
32 | MRB | Valasan , Vishal Shyambhai Kharadi | 02.06.22 | NFHOS | As per site visited by DE Wankaner Rural 1 jointly with EE WKR DO , it is came to know that accident took place in the farm of AG consumer namely Shri Yunus Jiva Bhoraniya having Con.No :34747/00469/6, Load:7.5 HP. From site visit, it is seen that farmer Sh. Yunus Jiva Bhoraniya has newly constructed Room in his farm adjacent to 11KV line hence vertical distance from 11KV line to roof of room becomes 0.5 mtr only & which is not safe as per safety rules. On dated 02.06.2022 Time Approx. 12:15 HRS, both victims was playing on roof of that room with iron rod having length of 5 feet. Meanwhile, iron rod came in direct contact with 11KV live conductor and both victim got electrocuted and during preliminary treatment at Civil hospital, wankaner Miss Payal Shyambhai Kharadi declared dead by on duty doctor while Mr. Vishal Shyambhai Kharadi referred at civil hospital rajkot after primary treatment. Sparking spots on iron rod, 11KV conductor and on roof of room observed during site visit. However. As per record of 66KV Mitana SS, No tripping observed around accident time. | CEI report awaited | NA | NA | Notice Issue for remove illegal construction. Notice No-SDOWKR1/T/15698/03.06.2022 & Awareness among general public regarding electrical safety "Keep safe distance from Electrical line & Network of PGVCL" during khedut-shibir & village meeting regularly | 2 | [9 empty] | HMRB2223009150
33 | MRB | Jodhpar , Punamben Babubhai Surela | 02.07.22 | NFHOS | As per information received from Morbi Taluka police station on dated 03.07.2022 and site visited by DE Lalpar Sdn & it is found that on dtd 02.07.2022 about 12:30 hrs conductor of Jodhpar ag feeder is broken from shackle point & to fall on fencing of dry thrones. Due to that feeder was not tripped that time. When victim was passed from road and anyhow touched to the live conductor and she shocked & burned out by live conductor. Victim was taken hospital and she is under treatment in Krishna hospital. At the time of victim touched to conductor about 12.30 hrs feeder may be tripped which is observed in SS. | CEI report awaited | NA | NA | Conductor replaced at accident place & Awareness among general public regarding electrical safety "Keep safe distance from Electrical line & Network of PGVCL" during khedut-shibir & village meeting regularly | 3 | [9 empty] | HMRB2223009226
34 | MRB | Andarana , 1 nos Buffalo of Gopalbhai Vishabhai Bambhava | 03.07.22 | FA | As per Information received from Villager & Site visited By DE Ghuntu sdn, it came to know that, an accident was taken placed at Talavadi Vadi, Hanuman vadi area, In Last span LT line Of Transformer centre location AND/ASR/017/L-013/DT-23,63 KVA of 11kv Ashram Ag feeder. Due to heavy wind Somehow 2nos. of LT line conductors of LT line which is power supply to AG connection of sh. Shivabhai Popatbhai are broken and fall to the ground at accident site, at that time feeder was on in single phasing. Buffalo was passing at that location and came in contact with live LT Line wire of feeder, experienced an electric shock and electrocuted and got death at site. | CEI report awaited | NA | NA | Conductor replaced at accident place & Awareness among general public regarding electrical safety "Keep safe distance from Electrical line & Network of PGVCL" during khedut-shibir & village meeting regularly | 4 | [9 empty] | AMRB2223009225
35 | MRB | Thorala , Rahul Pappulal Bhil | 14.06.22 | FHOS | As per telephonic information received from Morbi Taluka police station on 15.06.2022 at 12.30 hrs. And Police station letter (inward no.55, 15.06.2022) this incident came to known. Site visit by D.E & J.E of Nani Vavdi Sdn on 15.06.2022 at 15.45 hours. As per statement of eye witness, while playing, Victim accidentally touched conductor of 11 kv line from parapet of staircase in between of first and second terrace of labour quarter in the premises of HT Consumer- Ms Prime microns (IND) LLP (Consumer No.34747) at Thorala patiya. Due to this, victim got electrocuted and fall down on staircase. There is black spot found on nearest conductor to building of 11kv Maruti JGY feeder which is covered with white PVC pipe. Moreover this pipe found cut straight so as to house on Conductor. Eye witness Pappulal Kishanlal Bhil (father of victim), Subodhkumar Sinh and Prakashbhai Shamjibhai Barasara rushed to him and took victim to Krishna hospital, Morbi by private vehicle for further treatment and from there shifted to civil hospital, Morbi and on duty doctor of civil hospital Morbi declared him as dead. There was no tripping observed on 11 KV Maruti JGY (66 KV Rajpar s/s) as per GETCO record. | CEI report awaited | NA | NA | Notice Issue for illegal construction. Notice No-DE/NV/399 15.06.2022 & Awareness among general public regarding electrical safety "Keep safe distance from Electrical line & Network of PGVCL" during khedut-shibir & village meeting regularly | 5 | [9 empty] | HMRB2223009174
36 | MRB | Gangiyavadar , Buffalo of sh. Matrabhai Kukabhai Lamka | 14.07.22 | FA | As per Site visit, it was came to know that, Accident site in agriculture area in Gangiyavadar village. Due to continuous heavy rain from last 4-5 days, land becomes wet so that PSC pole of 11KV Maha AG feeder fall down. Meanwhile, 3 no’s buffalos were passing below the line and live conductor fallen on the buffalos and got electrocuted and Fatal animal accident occurred. Site photo graphs taken. As per the record of 66KV Lunsar S/S, tripping was observed in SS at 14:45 hrs on accident date. | CEI report awaited | NA | NA | Damage poles/ Line rectified & Awareness among general public regarding electrical safety "Keep safe distance from Electrical line & Network of PGVCL" during khedut-shibir & village meeting regularly | 6 | [9 empty] | AMRB2223009273
37 | MRB | Gangiyavadar , Buffalo of sh. Matrabhai Kukabhai Lamka | 14.07.22 | FA | As per Site visit, it was came to know that, Accident site in agriculture area in Gangiyavadar village. Due to continuous heavy rain from last 4-5 days, land becomes wet so that PSC pole of 11KV Maha AG feeder fall down. Meanwhile, 3 no’s buffalos were passing below the line and live conductor fallen on the buffalos and got electrocuted and Fatal animal accident occurred. Site photo graphs taken. As per the record of 66KV Lunsar S/S, tripping was observed in SS at 14:45 hrs on accident date. | CEI report awaited | NA | NA | Damage poles/ Line rectified & Awareness among general public regarding electrical safety "Keep safe distance from Electrical line & Network of PGVCL" during khedut-shibir & village meeting regularly | 7 | [9 empty] | AMRB2223009273
38 | MRB | Gangiyavadar , Buffalo of sh. Matrabhai Kukabhai Lamka | 14.07.22 | FA | As per Site visit, it was came to know that, Accident site in agriculture area in Gangiyavadar village. Due to continuous heavy rain from last 4-5 days, land becomes wet so that PSC pole of 11KV Maha AG feeder fall down. Meanwhile, 3 no’s buffalos were passing below the line and live conductor fallen on the buffalos and got electrocuted and Fatal animal accident occurred. Site photo graphs taken. As per the record of 66KV Lunsar S/S, tripping was observed in SS at 14:45 hrs on accident date. | CEI report awaited | NA | NA | Damage poles/ Line rectified & Awareness among general public regarding electrical safety "Keep safe distance from Electrical line & Network of PGVCL" during khedut-shibir & village meeting regularly | 8 | [9 empty] | AMRB2223009273
39 | MRB | Lajai , Gajendrabhai Samatbhai Vala | 24.06.22 | NFHD | As per message received from 66 KV Lajai S/S, 11 KV Madhuvan JGY feeder was in PF at 11:30am. For attending the same, technical staff U M Jadeja, ALM with victim G S Vala, Electrical assistant (VS) were reached to location on the Morbi Rajkot highway, which was just outside 66 KV Lajai S/S. On site, it was found that there was jumper fault of 11 KV Madhuvan JGY feeder occurred on Girder pole located at road side. To carry out rectification work, ALM shri Jadeja taken Line Clear permit of 11 KV Madhuvan JGY along with 11 KV Ramdev AG and 11 KV Akshar JGY feeder, due to crossing, at 11:45 am. Victim shri Vala climbed upon this road side girder pole for repairing of jumper and he made it complete. Meantime, shri Jadeja call upon help of other staff as there was dry grass on the ground which got flammable due to sparking. And as two staff arrived on site, they three were engaged to extinguish this fire to prevent damage to other 11 KV XLPE cable at site. Meanwhile, on the very next DP towards S/S to this Girder Pole, there was also one jumper found isolated from line. Hence Shri Vala goes to attend the same on this PSC Pole DP Structure. He climbed on this DP and repaired Jumper. After completion of work, while coming downwards from DP Structure, unfortunately he got contacted with contacts of 11 KV XLPE Cable of 11 KV Rudra JGY feeder which was laid on this same DP Structure for road crossing. Hence Victim got electrocution and fall on the ground. Nearby staff shri Jadeja and other two run towards shri vala and get him to the nearby Sagar hospital, Morbi for emergency primary treatment. After wards as suggested by Sagar hospital, he referred to Salus hospital, Rajkot for further treatment. At now, as per opinion of doctor he got injury on forehead and out of danger. Although he is kept under observation for further course of period.During further course of primary investigation, it was found that 11 KV Madhuvan JGY feeder was shorted and earthed before carrying out jumper work. Victim wore hand gloves while working. Safety belt and helmet were not wore by him which was available in vehicle. LC of 11 kv Rudra JGY was not taken which was exist on same DP Structure. Hence accident occurred. | CEI report awaited | NA | NA | SCN issued to ALM-Sh. U M JADEJA (Supervisor) vide no. MDO2/HR/SCN/23, Dtd: 29-06-2022 & G S VALA wide no. MDO2/HR/SCN/24, Dtd: 29-06-2022Safety meeting arrange regularly with Line staff & Contractor. | 9 | [9 empty] | HMRB2223009197
40 | MRB | Tikar , Buffalo of Jagabhai/Jagdishbhai Hindubhai Manguda | 26.06.22 | FA | As per site visit verification by SDO shri. M N Ninama (Halvad Rural SDn), at site Location of Tikar village TC No. DT-18/L-26/R-13 No any type of leakage path of Current found at a time. As per Present Eye Witness shri.Lilaben Jagdishbhai Manguda's statement that On Dt:-26/06/2022, Approx. Time 18:30, Buffalo passes Nearby Transformer Centre. Due to Heavy Wind and Wet Land in rainy season, there may be leakage current flows, while Buffalo passed nearby TC center, it got an electrocuted. | CEI report awaited | NA | NA | TC earthing reactive & Awareness among general public regarding electrical safety "Keep safe distance from Electrical line & Network of PGVCL" during khedut-shibir & village meeting regularly | 10 | [9 empty] | AMRB2223009206
41 | MRB | Tankara , Cow of Rameshbhai Vishabhai Zapda | 27.06.22 | FA | As per complaint received at fault center of Tankara Sdn given by Sh Vijaybhai Bharwad regarding accident to a Cow, site visited and it came to know that, an accident was taken placed near Transformer centre situated near Kumar Taluka Shala - Tankara of 11KV Tankara Urban feeder. There is a 200 KVA distribution Transformer with plinth mounted X'mer centre at sufficient height. There was heavy wind and rain last night and due to that Soil of surrounding area was very wet. A Cow was passing near that X'mer at early morning experienced an electric shock and electrocuted. Step potential may have developed near area of X'mer centre due to minor leakage in earthing and got death at site. During preliminary investigation no leakage /shock was observed. | CEI report awaited | NA | NA | TC earthing reactive & Awareness among general public regarding electrical safety "Keep safe distance from Electrical line & Network of PGVCL" during khedut-shibir & village meeting regularly | 11 | [9 empty] | AMRB2223009203
42 | MRB | Dhuva , 1. nos baffelo of Ghanshyambhai Hathabhai Chauhan | 28.08.22 | FA | As per Site visited, it came to know that on dtd: 28.08.22, buffalos were grazing in agriculture area of dhuva village where GO switch exist of 11KV Himalaya AG feeder. At that time, one buffalo was rubbed her horn with guy wire of GO switch DP. Meanwhile, guy wire broken and lower part of guy wire from the guy insulator came in contact with live GO switch's jumper and buffalo was electrocuted and died. As per the record of 66KV Dhuva S/S, tripping was observed in Ss at 8:30 hrs on accident date. Further, Sparking spots on guy wire was seen clearly. | CEI report awaited | NA | NA | New guy and jumper provided & Awareness among general public regarding electrical safety "Keep safe distance from Electrical line & Network of PGVCL" during khedut-shibir & village meeting regularly | 12 | [9 empty] | AMRB2223009387
43 | MRB | Hadmatiya , Ajay Mukeshbhai Makwana | 29.08.22 | FHOS | As per information received through press cutting, site of said accident place visited by DE Virpar. It was found that Victim climbed up on TC DP while the power is On. Purpose of climbing up on TC DP was not found at this stage. TC was supplied by 11 kV Bansi AG feeder which was ON while the person climbed up. Accidentally he came in contact with DO fuse/Jumper and get electric shock and fallen on the ground. Nearby person came after happening of accident and take the victim to the hospital where he was declared dead by on duty doctor. | CEI report awaited | NA | NA | Victim himself responsible as he climbed on pole. Awareness among general public regarding electrical safety "keep safe distance from electrical line & network of pgvcl" during khedut-shibir & village meeting regularly. | 13 | [9 empty] | HMRB2223009390
44 | MRB | Halvad, Sanjaybhai Gordhanbhai Makawana | 13.09.22 | FHOS | As per information received from Social media on Dt.14.09.2022, 16:00hrs regarding accident to a Human. Site Visit taken by DE of Halvad Town SDn on Dt.14.09.2022, 17:30hrs and it is come to know that accident took place near Bhavaninagar Railway fatak. Victim was working as a labour in Umiya garage. One heavy vehicle TATA Dumper vehicle No- GJ36V3123 was parked under line of 11KV Halvad City-2 urban feeder. Victim was doing some repairing work on that Vehicle. For some reason Vehicle driver lifted hydraulic trolley of truck and trolley touched to live conductor of 11KV Line which is passing above vehicle. Victim was in contact with vehicle at the time of touching and got electrocuted. Then he was transfer to the Referral Hospital, Halvad and On duty Doctor declared him as Dead. Ground clearance of the 11KV Line at the point of accident is 5.1 mtr. 11KV Halvad City-2 Urban Feeder tripping occurred at that time of 12:10pm on Dt.13.09.2022. | CEI report awaited | NA | NA | Notice Issue to owner of garage vide No- DEHALT/T/10212 dt: 13.10.2022 & Awareness among general public regarding electrical safety "Keep safe distance from Electrical line & Network of PGVCL" during khedut-shibir & village meeting regularly | 14
45 | MRB | Ghuntu, Mohamad Ashrafbhai Iliyasbhai | 21.09.22 | FHOS | As per information received from Social media & site visited by DE Ghuntu, It is found that 11kv Silk Ind. Feeder passing along with Juna Ghuntu road at Poonam industries, village Ghuntu. Victim has parked truck between location numbers 109-110 of 11Kv Silk feeder for unloading of material. Victim climbed on panel which is lying in truck and try to throw iron pipe about 24feet 9inch length and iron pipe came in contact with lowest conductor of line and he got electrocuted and met with fatal accident. He fallen down in truck & primary treatment was given. While going towards Samrpan hospital Morbi, he dead on way. Victim was taken to Morbi Civil hospital for PM. Distance between lowest conductor of 11kv Silk Ind feeder and ground measured as 20feet 1inch. At the time of accident tripping was not recorded at substation. Dark spot observed on conductor. | CEI report awaited | NA | NA | Notice Issue to owner of factory vide No SDO/GNT/1965 dt: 13.10.2022 & Awareness among general public regarding electrical safety "Keep safe distance from Electrical line & Network of PGVCL" during khedut-shibir & village meeting regularly | 15
46 | MRB | Bela, Momjibhai Dhanabhai Karkta | 11.09.22 | FA | As per information received from 66 kv Bela SS Operator regarding accident and site visited by DE & JE Jetpar sdn the initial implications of accident are as narrated below A Buffalo was grazing grass in the open land situated besides 66 KV Bela SS. At that time accidentally, a single conductor got broken between DP structure location (11 KV Virat Nagar/IND/BEL/VRT/02/03 - 04/05) and conductor came in direct contact with the buffalo and being wet land due to rain it got electrocuted. Being a return conductor, no tripping is recorded in the 11 KV Virat Nagar JGY feeder at the time of accident. | CEI report awaited | NA | NA | Restringing with new Jumper and joint work carried out & Awareness among general public regarding electrical safety "Keep safe distance from Electrical line & Network of PGVCL" during khedut-shibir & village meeting regularly | 16
47 | MRB | Charadva, Rupeshbhai Laljibhai Shiyala | 09.09.22 | NFHD | As per telephonic information received on dtd:09.09.22, time:10:10 am hrs from Sh.J.T Kharadi, ALM,Chardava SDn regarding accident and Site visited by SDO, it came to know that accident was taken placed nr.Narmada canal,Charadva Village. On Dtd: 09.09.22,11KV Panchali AG feeder emanating from 66KV Charadva SS was in PF from 08:00 hrs. so,that team of Line staff 1)J.T Kharadi,ALM, 2)J.R Damor,EA and 3) R.L.Shiyala,EA on duty in 1st shift(8:00 to 16:00) conveyed by fault center to attend fault of 11KV Panchali AG. After patrolling of 11KV Line 11KV jumper found snapped between location No.CHR/PNC/009 & CHR/PNC/010 which was rectified by above team by observing all safety rules. Then after, they were reached at DP structure Location No.CHR/PNC/009 where Y-phase jumper found burnt. So, after observing all formalities of safety rules and wearing all safety gadgets, Sh.R.L.Shiyala, EA was starts climbing girder pole. While he was climbing up on said 11KV girder pole at about 15 feet from ground level his feet had slipped due to lost grip and wet mud shoes of his toes & lost his balance and fell down to the ground and Get injured at his sciatica disc. First of all, he took away at Govt. Hospital, Charadva after Krishna Hospital Morbi for primary treatment and then after he transferred at YASH Hospital, Rajkot for further treatment. As said by Doctor victim having fractures in Sciatica disc. | CEI report awaited | NA | NA | Showcause Notice Issue to victim No-CHD/Tech/14, 30.09.2022 Safety meeting arrange regularly with Line staff & Contractor. | 17
48 | PBR | CHORWAD , BUFFALO OF SHRI BHUPATBHAI VIKRAMBHAI CHAVDA | 01.07.22 | FA | As per site visit and information given by eye witness that owner of she buffalo was away ahead and nearly 8 to 10 group of she buffalo was behind and passing from KEDI which is about width of 6 feet merely. Also water was accumulated in kedi due to rain. At about 17.20 hrs. sudden wind pressure developed and coconut leaf was fallen on the conductor of 11 kv kanek ag feeder, resultant in to snapping of conductor, At that time she buffalo was passing in kedi and came in contact with snapped conductor and electrocuted. After getting information at fault center immediately 11 kv Kanek ag power was shut off. As per 66kv Chorwad ss record, no any tripping observed after 16.30 hrs. till shut off power at 17.30 hrs. | CEI report awaited | NA | NA | One span conductor replaced | 1 | [9 empty] | APBR 2223009218
49 | PBR | THALI , BUFFALO OF SHRI PUNJA MENSHI KESHWALA | 04.06.22 | FA | As per site visit and information given by buffalo owner, when At buffalo crowd passed near thali WW tc, at that time one buffalo rubbing it's back with the transformer dp pole.Due to this Earthing wire was stretched by buffalo and earthing wire pull out from ground, so that leakage current passed to earth wire and buffalo get electric shocked. | CEI report awaited | NA | NA | TC earthing reactivated | 2 | [9 empty] | APBR2223009154
50 | PBR | MOCHA , SHEEP OF SHRI RANABHAI VEJABHAI KODIYATAR | 05.07.22 | FA | As per site visit and information given by owner of sheep, when crowd of sheep's passes near to 63 KVA Ag. Group tc, at that time two nos. sheep passes very near to transformer dp pole and Due to monsoon season, the ground is fully wet. Both sheep’s may came in zone of leakage current of earthing of transformer center and get electric shocked. | CEI report awaited | NA | NA | TC earthing reactivated | 3 | [9 empty] | APBR2223009235
51 | PBR | MOCHA , SHEEP OF SHRI RANABHAI VEJABHAI KODIYATAR | 05.07.22 | FA | As per site visit and information given by owner of sheep, when crowd of sheep's passes near to 63 KVA Ag. Group tc, at that time two nos. sheep passes very near to transformer dp pole and Due to monsoon season, the ground is fully wet. Both sheep’s may came in zone of leakage current of earthing of transformer center and get electric shocked. | CEI report awaited | NA | NA | TC earthing reactivated | 4 | [9 empty] | APBR2223009235
52 | PBR | AJAB , SHRI VAJUBHAI NARANBHAI BHUVA | 06.04.22 | NFHOS | The top clamp inclined at location no.55 of 11 kv Prasali Ag feeder due to that phase to phase fault occurred which result in jumper fault at location no.40 & and also conductor snapped between location no.26 & 27 where guarding is already exist but due to side cross arm on pole location no.27,that snapped conductor fallen on tractor which was park under the span location no.26 & 27 , due to that tractor tyre catches fire at that time victim tried to extinguished the fire and came in contact with tractor and got electrocuted and met with non fatal accident. The tripping recorded in 66 KV Ajab s/s in 11KV Prasali Ag feeder at 1:20, 1:25 & 1:30 hrs. The size of conductor is 55mm2 and also condition of conductor is good. This accident occurred due to technical fault in line. | Snapped conductor fallen on tractor which was park under the HT Line , due to that tractor tyre catches fire at that time victim tried to extinguished the fire and came in contact with tractor and got electrocuted and met with non fatal accident. | Maintainance of HT line periodically and provide broken conductor relay. | YES | One span conductor replaced and guarding done | 5 | 12, 49 | 1082 | 18 | 8 | 22 | 6223 | 25 | 8 | 22 | HPBR2223009085
53 | PBR | AJAB , SHRI DINESHBHAI MEGHABHAI BABARIYA | 06.07.22 | NFHOS | As per statement of eyewitness the victim tried to bind a DO Fuse of T.C. using plastic pipe but due to rain pipe was wet and victim got electric shock and met with non-fatal accident. No any sparking/spot found on plastic pipe and also no tripping registered in 11kv Madhi Ag feeder at 66kv Ajab SS on dtd: 06.07.2022, Time:16:00. There is no any leakage current found at said location. And also No such fault/complain registered by victim at Keshod Rural-1 sdn fault office. Victim himself tries to do unauthorized work, so PGVCL is not responsible. There is a single transformer from 11kv madhi Ag feeder for agriculture connection, consumer name Sh. Meghabhai punjabhai, consumer no.80216/02295/9, Load 5HP, and also residential connection (AGRL), consumer name Meghabhai punjabhai Babariya, consumer no.80216/11104/8, Load 1kw is supplied form this transformer using single phase twin core service wire. | CEI report awaited | NA | NA | Awareness among general public regarding electrical safety during khedut-shibir & village meeting regularly | 6 | [9 empty] | HPBR2223009244
54 | PBR | KUTIYANA , CAMEL OF SHRI RANMAL MANAN NAGESH | 08.07.22 | FA | As per eye witness Shri Lagdhirbhai Nagesh camel were feeding grass by handler and by passing through gate and due to irresponsibility of owner one camel come near to transformer Centre near SM Jadeja collage gate and try to eat leaves of lemon tree near SM Jadeja college transformer , during eating of tree breaches ,tree branches moved toward bushing and come in induction zone of transformer bushing jumper and got electrocuted and fall on earth near transformer Centre . Also DO fuse wire of transformer got blown. | CEI report awaited | NA | NA | Awareness among general public regarding electrical safety during khedut-shibir & village meeting regularly | 7 | [9 empty] | APBR2223009249
55 | PBR | KADACHH , BUFFALO OF SHRI DINESHBHAI DAYABHAI KODIYATAR | 09.08.22 | FA | As per site visit and information given by buffalo owner, site was fully wet, when at buffalo crowd passed near tc centre, at that time one buffalo rubbing it's horn with the transformer centre guy wire and stretched and touched to DO and current passed to guy wire and buffalo get electric shocked. | CEI report awaited | NA | NA | TC new jumper done and tree cutting done. | 8 | [9 empty] | APBR2223009331
56 | PBR | CHHAYA (NAVAPARA) , BUFFALO OF SHRI RAMBHAI BHAGATBHAI KESHWALA | 12.06.22 | FA | As per telephonic information from an owner regarding electric shock to a she buffalo at above location and as per site visit, LT line conductor of 3 phase 4- wire LT line of Rajbha Jethva AG group of 11kv Ratanpar AG feeder one conductor snapped due to wind and nearby tree branches fallen on conductor and hence conductor snapped on she buffalo standing under that LT line near to AG connection of shri Rajesh Bhagat Keswala and due to this she buffalo got electrocuted & died. | CEI report awaited | NA | NA | One span conductor replaced | 9 | [9 empty] | APBR2223009165
57 | PBR | PALAKHADA , BULLOCK OF SHRI BHURABHAI RANCHHODBHAI JOSHI | 13.07.22 | FA | As per telephonic information from owner regarding electric shock to Bullock at above location and as per site visit, due to heavy Rain and wind, Neem Tree branches tilted on LT line, one conductor of 3-ph 4-wire LT line of Mehta Ag group snapped one conductor and fallen on Bullock standing under that LT line and due to this Bullock got electrocuted & died. Conductor is in good position and no any joint in that span of LT Line from which one conductor has been snapped. | CEI report awaited | NA | NA | One span LT conductor replaced and tree cutting done | 10 | [9 empty] | APBR2223009267
58 | PBR | MADHADA , BUFFALO SHRI GOVINDBHAI LAKHAMANBHAI CHHUCHAR | 15.08.22 | FA | As per site visit and Site observation it was found that Due to heavy wind and rain, one DO fuse wire burnt and fall on transformer LT stud and wire touches to B phase and TC body. So leakage current passing through TC body earthing wire & due to monsoon season, the nearby land is fully wet. The buffalo passes between the pole of DP and came contact of zone of leakage current and electrocuted. This transformer center is very old so there is no earth pipe in earth wire. | CEI report awaited | NA | NA | TC earthing reactivated | 11 | [9 empty] | APBR2223009353
59 | PBR | PORBANDAR (BOKHIRA) , COW SHRI MASHRIBHAI LAKHANSIBHAI ODEDARA | 16.06.22 | FA | As per telephonic information from owner regarding electric shock to a Gir cow at above location and as per site visit information, it is observed that LT ABC cable insulation got damaged/overheated and was touching LT Girder pole and due to rainfall surrounding land was wet and cow came in contact of LT pole while passing there and got electrocuted by flow of leakage current passed to cow and met with fatal accident. | CEI report awaited | NA | NA | One span LT ABC cable replaced and pole earthing reactivated | 12 | [9 empty] | APBR2223009176
60 | PBR | VANANA , COW OF SHRI KARA SARMAN KODIYATAR | 16.08.22 | FA | As per information given by first person visit. As he was passing where incident took a place he show that a cow was dead in wet surface due to monsoon season near corona center TC, at Vanana, of 11 KV Pipariya JGY feeder. Cow comes in contact with leakage induction area due to monsoon rain and wet surface and electrocuted. Condition of Transformer center, earthing is good hence pgvcl network is intact but due to faulty, damage and short circuit internal wiring of Consumer 35620006476,load 49kw ,Name Mukhya jilla aarogya adhikari, is improper RCCB & ELCB are not working so leakage current pass in earthing and wet Areas near TC. | CEI report awaited | NA | NA | Awareness among general public regarding electrical safety during khedut-shibir & village meeting regularly | 13 | [9 empty] | APBR 2223009355
61 | PBR | VANANA , COW OF SHRI KISHOR LAKHMAN MUCHHAR | 16.08.22 | FA | As per information given by first person visit. As he was passing where incident took a place he show that a cow was dead in wet surface due to monsoon season near corona center TC, at Vanana, of 11 KV Pipariya JGY feeder. Cow comes in contact with leakage induction area due to monsoon rain and wet surface and electrocuted. Condition of Transformer center, earthing is good hence pgvcl network is intact but due to faulty, damage and short circuit internal wiring of Consumer 35620006476,load 49kw ,Name Mukhya jilla aarogya adhikari, is improper RCCB & ELCB are not working so leakage current pass in earthing and wet Areas near TC. | CEI report awaited | NA | NA | Awareness among general public regarding electrical safety during khedut-shibir & village meeting regularly | 14 | [9 empty] | APBR 2223009355
62 | PBR | KATRASA , COW OF SHRI KALPESHBHAI RAGHUBHAI GONDALIYA | 17.07.22 | FA | As per site visit and information received from owner of cow, when cow passes near to 100 KVA transformer center, at that time cow passes to very near to transformer D.P. pole and Due to monsoon season, the nearby land is fully wet. The cow may come in zone of leakage current of earthing of transformer center and got electric shocked. The leakage current checked at the time of site visit but no leakage current found and also at the time of accident the feeder is in three phase power supply. | CEI report awaited | NA | NA | TC earthing reactivated | 15 | [9 empty] | APBR2223009279
63 | PBR | MESHVAN , SHRI ASHWINBHAI MOHANBHAI KAMARIYA | 24.04.22 | FHOS | As per information received from Gujarat samachar dt.25.04.2022 ,The victim climbed on pole of 11 KV Ashram ag feeder Pole no.-L-21 & he tied cloth with V cross arm & around his neck to commit suicide & also catch Y-phase conductor of 11kv line to commit suicide & electrocuted. The sparking spot found in Y-phase conductor of 11kv Ashram Ag feeder of said location. In 66 kV Koylana substation tripping recorded in 11KV Ashram Ag feeder at 9:50 to 9:55am.There is no any leakage power found in said location pole no. L-21. So PGVCL is not responsible for this accident. | CEI report awaited | NA | NA | Awareness among general public regarding electrical safety during khedut-shibir & village meeting regularly | 16 | [9 empty] | HPBR2223009105
64 | PBR | SONDARDA , BUFFALO OF SHRI PUNJABHAI RAJABHAI CHAVDA | 24.07.22 | FA | As per site visit and information received from owner of buffalo, when buffalo passes near to Ghanti valu 63KVA Transformer center and the buffalo came very near to DP and also LT AB cable of transformer to distribution box is found damaged and touches to earthing wire & due to monsoon season, the nearby land is fully wet. The Buffalo may came in contact of zone of leakage current of earthing of Transformer center and got electric shocked. | CEI report awaited | NA | NA | TC earthing reactivated | 17 | [9 empty] | APBR2223009303
65 | PBR | VIROL , BULLOCK OF SHRI KASAMKHA SHERKHA BELIM | 25.07.22 | FA | As per site visit and information received from owner of Bullock, when Bullock passes near to 10 KVA transformer centre, at that time accidentally due to wind pressure one DO blown and it's wire fall on LT stud between phase and Neutral and current may passes through the earthing and also nearby land is fully wet. Bullock may came in zone of leakage current of earthing of transformer centre and get electric shocked. At the time of accident, the feeder is in three phase power supply and no any interruption noted. | CEI report awaited | NA | NA | TC earthing reactivated | 18 | [9 empty] | APBR2223009306
66 | PBR | CHULADI , BULLOCK OF SHRI VEJANANDBHAI VARJANGBHAI NANDANIYA | 30.06.22 | FA | As per site visit and information given by bullock owner, when they were passing from pankva chuldi rajmarg accidently AAA 55mm2 conductor of 11 kv dudhala ag (loc: chld/dudhala/81) snapped and bullock came in contact with affected snapped load side conductor and electrocuted. After detailed investigation it was found that Y-phase 11 kV pin insulator (porcelain) was found punctured and due to that conductor was snapped. Also said feeder was tripped at 16.30 hrs. as per 66kv chuldi ss record. | CEI report awaited | NA | NA | One span conductor replaced and faulty pin insulator replaced | 19 | [9 empty] | APBR2223009215
67 | PBR | KESHOD, MAYABEN CHANDUBHAI DEVADIYA | 14..08.22 | FHOS | As per eye witness statement "Mayaben Chandubhai Devadiya try to pick bael fruit from the tree with the help of iron rod (approx. length of 10 ft) at that time due to heavy wind perhaps she may came in zone of HT live bare conductor which is nearby bael tree and as a result she may got electrocuted." Tripping not observed in 11 KV Gandhinagar urban feeder at 66kv Keshod Ss at a time of accident and also Vertical Distance From ground to conductor is Approx. 25 feet and Vertical Distance From slab of room to conductor is 15 feet and horizontal distance is approx. 4feet & 5 inch. No any sparking spot or other symptoms observed in iron rod and 11kv line. As per PM report victim came in induction zone and got electrocuted. | CEI report awaited | NA | NA | Awareness among general public regarding electrical safety during khedut-shibir & village meeting regularly | 20
68 | PBR | BUFFALO OF SHRI PARBATBHAI VIKRAMBHAI GORANIYA | 2022-09-03 | FA | As per information given by first person visit who himself owner of the Buffalo, he told that today at morning his mother taking his Buffalo out for feeding grass and out of his waranda there is water storage so Buffalo went there for drinking water at that time main line conductor of Y phase of 11 kv panchkoshi ag, shackle pole no 93 conductor departed from disc anchor and fallen down on that Buffalo. Due to that buffalo get electrocuted. Condition of conductor is good. | CEI report awaited | NA | NA | Conductor is in good condition. So conductor restringing of one span. | 21
69 | PBR | SHRI HARSUKHBHAI SARMANBHAI DABHI | 2022-09-10 | FHOS | As per site visit victim was doing un authorised work in valima vara Transformer LT network line by cut D. O fuse of transformer but as per site visit victim was unauthorised work at those place where also 11 kv Kankeswari ag line cross, at the time unauthorised work LT line contact with 11kv live line conductor and victim was directly contact with 11kv live line through LT line and got electrocuted. So Victim was responsible unauthorised in Pgvcl network and Pgvcl not responsibility for this Fatal accident, Further matter under investigation. | CEI report awaited | NA | NA | Awareness among general public regarding electrical safety during khedut-shibir & village meeting regularly | 22
70 | JMN | JAMBUSAR(VADI VISTAR) , NINAMA ALPESHBHAI SOMABHAI (Contractor Person) | 01.06.22 | NFHOS | As per site investigation report & statement of eyewitness, it came to know that on dtd : 01.06.2022, maintenance work of Bansidhar JGY feeder was allotted to contractor M/s. Madhuvan construction along with supervisor Shri. G.R. Parmar (EA-VS). He went with contractor team at Jambusar Vadi Vistar and took Line clear of Bansidhar JGY feeder. After getting line clear, he followed the safety norms by short & earth the said line at location no. JSP/BSD/155. Meanwhile, victim and two other labor were working for restringing of loose span at location no. JSP/BSD/156 to 159. After that victim went for tree cutting work. After completing restringing wok at given location in south side, he found one more span was loose at north side which was not allotted to do. In that span, Jambusar AG feeder is crossing. During restringing work middle conductor on north side accidently came in induction zone of Jambusar AG feeder which was live in single phase schedule. Due to that, temporarily electric flash occurred and victim got minor jerk. After that victim set on DP and other two labor took him to ground and admitted in hospital for primary treatment. At present, health of victim is normal and no any major injury occurred to him. | CEI report awaited | NA | NA | Notice issued to M/s. Madhuvan Construction for not following safety standards and started work without wearing safety gadgets by victim vide letter no. JJW/Tech/2022/18, Dtd : 1.6.22. All the contractor strictly instructed to educate to their labour for use safety gadgets and follow the all safety measures while working on line and insisted them to short & earth the line on both the sides of the working location as per standard procedure and Electrical Network must be properly isolated before starting work in the network. | 1 | [9 empty] | HJMN2223009143
71 | JMN | Bhanvad-Garas vadi vistar , M K Jogel Electrical Assistant (V.S.) | 01.06.22 | NFHD | As per site visit and observation, it came to know that victim Shri M. K. Jogel (Electrical Assistant - VS) and Shri Hiren Nakum (Apprentice lineman) went for attending complaints in agriculture area. For attending complaint no. 18964 in 11 KV Garas AG feeder, they took line clear of 11 KV Garas AG feeder. After taking line clear, they shorted and earthed the 11 KV line with chain link and complaint had been resolved by doing jumper work. After resolving the above complaint, they went to attend another complaint vide complaint no. 18994, dtd : 01.06.2022. This complait was registered for not getting power in one phase. So, there was required to check jumper and connection of transformer center. On the top of the said complaint receipt, 11 KV Garas AG was written. As the line clear already taken for Garas AG feeder, victim believed that this location also falls under 11 KV Garas Ag feeder and without further verification of power, he climbed blindly. Unfortunately, it was Morzar Ag feeder supplying power to the complaint location. Hence, in hurry without isolated DO fuse of transformer center, victim began climbing on transformer center and came in contact with R phase live LT bushing and got minor jerk and fall down on ground resulting in to non-fatal electrical accident. | CEI report awaited | NA | NA | This accident was occurred due to non-utilization of safety gadgets and not following safety standards by victim. Hence explanation asked to victim vide letter no. BSD/Tech/20, Dtd : 2.6.22. All the line staff instructed to use safety gadgets while working on line and insisted them to short & earth the line on both the sides of the working location as per standard procedure and Electrical Network must be properly isolated before starting work in the network. Also, work with due care during rainy atmosphere to avoid such accident. | 2 | [9 empty] | HJMN2223009144
72 | JMN | Korada , A buffalo of Sangrambhai Mekranbhai Nangesh | 03.08.22 | FA | As per information received From Dwarka PGVCL Fault centre wide complain no 102660 name of Ramesh Karshan Nakum on dt 03.08.2022.Sdo Dwarka has visited site, and as per statement of eyewitness it is came to know that it is found that nearest shackle pole jumper fault occurred and one jumper burnt and touched with pole fabrication and Guy fabrication and guy insulator not found and leakage current passed to earth through guy wire. As buffalo has come in contact with that guy wire got electric shock and died at place. | CEI report awaited | NA | NA | Faulty Jumper has been replaced and rectification work of guy wire has been carried out. Also necessary maintenance work has been carried out at accident site. | 3 | [9 empty] | AJMN2223009317
73 | JMN | Chandraga , Shri. Gaurav Bharatbhai Parmar (ALM) | 03.08.22 | NFHD | As per detail investigation during site visit and statement of victim & eyewitness, it came to know that this accident was occurred on dtd : 03.08.2022 while victim Shri Gaurav Bharatbhai Parmar (ALM) and Shri K. D. Bamniya (EA) went for attending complaint no. 41993 registered on dtd : 02.08.2022 of jumper burnt at DP of Shri. Sanjay babubhai Vasoya. Before starting the said complaint work, Shri K. D. Bamniya (EA) had asked line clear of Naghuna AG feeder (Harshadpur S/S) from Shri. D. D. Parmar (LM- Rural Sub division). After getting line clear, victim and his co-worker had shorted the 3 phase line and climbed on DP structure to repair jumper. While binding jumper, suddenly power came and victim got electric shock and fell down on earth. Vitim got injured and got fractured on his knee. On investigation of suddenly power came during above complaint work, it came to notice that Shri. D. D. Parmar (lineman) wanted to return line clear of Dhandha Ag feeder from 66 KV Pipartoda S/S and prepared message for the same. But by mistake, he sent the said prepared message to Harshadpur S/S. On duty operator at Harshadpur S/S had not read entire message sent mistakenly by Shri. D. D. Parmar (lineman) and returned line clear of Naghuna AG feeder where the complaint work was in process. Due to that victim got electric shock and met with non-fatal electrical accident. | CEI report awaited | NA | NA | This accident was occurred due to message for line clear was sent mistakenly to other substation by Shri. D. D. Parmar (lineman) hence show cause notice issued to Shri. D. D. Parmar (lineman) vide letter no. JCD-2/HR/DA/170, Dtd: 08.08.2022. Also, a letter written to Harshadpur S/S In charge for action taken against defaulter (on duty S/S Operation at the time of accident occurred) in this accident. All the line staff instructed to use safety gadgets while working on line and insisted them to short & earth the line on both the sides of the working location as per standard procedure and Electric Network must be properly isolated before starting work in the network. Also, work with due care during rainy atmosphere to avoid such accident | 4 | [9 empty] | HJMN2223009318
74 | JMN | Dhrafa , Shri Jayesh Rana Agath (EA- VS) | 05.05.22 | NFHD | As per detail investigation during site visit and statement of victim & eyewitness, it came to know that this accident was occurred while victim went for attending AG consumer complaint no. 200529, dtd : 05.05.2022. At accident site, there is a single transformer of HVDS feeder Deri AG. Co-worker Shri. H G Rathod EA (VS) took Line clear. After taking line clear, line was shorted and earthed with chain and victim climbed on Transformer Center to check jumper of TC. After completing middle jumper work, victim started work on right jumper of TC. Somehow power came from unknown source and victim got electrocuted. After that he was admitted to hospital at Upleta for primary treatment. At present, his health is good. | CEI report awaited | NA | NA | This accident was occurred even after all safety measures are followed by victim except isolate the network by disconnected power supply from nearby switch. Hence a showcause notice issued by Jamjodhpur East sub division to supervisor Shri. J. A. Saresa (ALM) vide letter no. JJE/12, Dtd : 09.05.2022. All the line staff instructed to use safety gadgets while working on line and insisted them to short & earth the line on both the sides of the working location as per standard procedure and Electric Network must be properly isolated before starting work in the network. Also, work with due care during rainy atmosphere to avoid such accident. | 5 | [9 empty] | HJMN2223009117
75 | JMN | Mota Thavariya , Buffalo of Shri AKSHAY KARAMSHI MAKVANA | 06.06.22 | FA | As per information received via phone call to hapa sub division fault center from punit karamshi makvana of vill: mota thavariya, buffalo of akshay karamshi makvana while grasing in ag field area, got in touch with broken conductor of 11kv mota thavriya jgy. So buffalo got electric shock and died due to electrocution resulting into fatal accident. Conductor was snapped due to pin insulator fault in 11KV mota thavariya JGY. | CEI report awaited | NA | NA | Pin insulator has been replaced and the said conductor re-joined. Also necessary maintenance work has been carried out at accident site. | 6 | [9 empty] | AJMN2223009156
76 | JMN | Navagam vadi vistar , Surpal Gumansinh Solanki | 06.06.22 | FHOS | As per site investigation report, it came to know that this accident was occurred while victim was doing tree cutting work carelessly near 11 KV live line of Morzar Ag feeder. Also, it is observed that said 11 KV line of Morzar Ag feeder is at distance of 10 feet from the transformer center and height of tree is more than the said 11 KV line. As per statement of eyewitness, a branch of tree was at near about 5 feet distance from conductor of 11 KV line and during heavy wind the due to that sparking noticed many times. Hence, owner of farm decided to cut the said tree branch. Victim climbed on tree and tried to cut that branch. During that time one end of the said tree branch touched to 11 Kv line and due to that victim got electrocuted. After above incident, his co-worker noticed that short circuit occurred and he immediately removed the said tree branch by using PVC water pipe and then victim and the said tree branch fell down on land. After above incident, his co-worker and farm owner shifted victim to hospital and he declared dead at hospital. | CEI report awaited | NA | NA | Necessary maintenance work has been carried out at accident location. Also, awareness given for not to carry out such tree cutting work near PGVCL network. | 7 | [9 empty] | HJMN2223009157
77 | JMN | Vavdi , A cow of Shri. Pankajbhai Prabhatbhai Makwana | 06.07.22 | FA | As per site visit and statement of eye witness, we came to know that heavy rain and wind observed at the time, leakage current would have passed through lower clamp which was earthed using GI wire at pole. This pole was having both HT and LT line with HT AB cable passing through projected angle and LT AB cable passing on C-clamp. The insulation of LT AB cable is seen to be damaged at one point which is touching the support wire of ABC. The support wire of LT AB cable might have touched lower clamp which was earthed. Due to rain water logging is seen around the pole. During that time Cow was passing near pole and it seems that while passing, cow would have accidentally come in contact with that leakage earthing wire and got electrocuted and died. | CEI report awaited | NA | NA | The particular span of LT ABC has been replaced with new one. Also necessary maintenance work has been carried out at accident site. | 8 | [9 empty] | AJMN2223009247
78 | JMN | Sarmat , kishor Lakhmanbhai chauhan Electrical Assistant (V.S.) | 07.06.22 | NFHD | As per detail investigation during site visit and statement of victim & eyewitness, it came to know that this accident was occurred on dtd : 07.06.2022 while victim went for attending complaint no. 18397 registered on dtd : 06.06.2022 of Sarmat Village. Before starting complaint work, victim tried to isolate the network by taking wrong hand trip of 11 KV Sarmat Ag feeder. However, actually power feeding to complaint location was from 11 KV Lakhabavad JGY feeder. Victim assumed that he has isolated the network by operating GO switch of Lakhabavad JGY feeder but based on MRI data and other facts on field, revealed that power was ON at accident location and isolation of network prior to work was not carried out. Moreover, no safety measures were followed and victim tried to verify power at jumper by using plier and unfortunately came in induction zone and met with non-fatal accident. | CEI report awaited | NA | NA | This accident was occurred due to non-utilization of safety gadgets and not following safety standards by victim Shri. K L Chauhan (EA-VS) during attending complaint. Hence explanation asked to victim vide letter no. (1) RSD/13, Dtd : 13.6.22. & (2) RSD/14, Dtd : 13.6.22. Also, explanation asked to his co-worker vide letter no. RSD/12, Dtd : 13.6.22 and show cause notice issued to SDO vide letter no. JCD-2/HR/DA/22/124, Dtd : 8.6.22. All the line staff instructed to use safety gadgets while working on line and insisted them to short & earth the line on both the sides of the working location as per standard procedure and Electric Network must be properly isolated before starting work in the network. Also, work with due care during rainy atmosphere to avoid such accident. | 9 | [9 empty] | HJMN2223009158
79 | JMN | Ghadka , Bullock of Shri Parshotambhai Dahyabhai Dabhi | 08.06.22 | FA | As per preliminary Investigation, Shri Parshotambhai Dahyabhai Dabhi was going to his farm by Cart with Bullocks. when he reached near farm's gate , Parshotambhai while closing the gate of his farm the cart with Bullock stand below the 11 kv Gadhka AG feeder. suddenly the conductor of 11 kv Gadhka AG Tap line snapped due to jumper fault and fall down on the Bullocks with cart and these 2 nos of Bullocks got Electrocuted and met with Fatal Electrical Accident . | CEI report awaited | NA | NA | Jumper has been replaced and the said conductor re-joined. Also necessary maintenance work has been carried out at accident site. | 10 | [9 empty] | AJMN2223009160
80 | JMN | Ghadka , Bullock of Shri Parshotambhai Dahyabhai Dabhi | 08.06.22 | FA | As per preliminary Investigation, Shri Parshotambhai Dahyabhai Dabhi was going to his farm by Cart with Bullocks. when he reached near farm's gate , Parshotambhai while closing the gate of his farm the cart with Bullock stand below the 11 kv Gadhka AG feeder. suddenly the conductor of 11 kv Gadhka AG Tap line snapped due to jumper fault and fall down on the Bullocks with cart and these 2 nos of Bullocks got Electrocuted and met with Fatal Electrical Accident . | CEI report awaited | NA | NA | Jumper has been replaced and the said conductor re-joined. Also necessary maintenance work has been carried out at accident site. | 11 | [9 empty] | AJMN2223009160
81 | JMN | Gordhanpar , A buffalo of Shri. Sajan Ratabhai Bambhava | 08.08.22 | FA | On dt. 8.8.22 around 04:30 PM Buffaloes were tied under the 11 KV Rural AG feeder line, at that time Y phase conductor break and snapped on one buffalo and Thus buffalo got electrocuted and fatal accident occurred. | CEI report awaited | NA | NA | The conductor has been replaced and necessary maintenance has been carried at accident location. | 12 | [9 empty] | AJMN2223009329
82 | JMN | Nani rafudad , A Buffalo of Shri. RAMJI PREMJI KHANDHAR | 10.07.22 | FA | As per information received , it is found that accident location is a Nani rafudad ( JGY ) village transformer center. As per statement of person on site it is found that one vehicle was passed on road near transformer center & blowed horn, & same time victimised buffalo was passing on same village road get scared & passed through two pole of transformer center & , may come in to contact with wet pole & earth wire pipe, & Due to humid environment , wet & muddy soil may get electric shock due to leakage current in earth wire or wet pole surface , and died at place. However than on primary investigation, it is found that no any leakage current is observed in nither earthing wire nor on pole surface. | CEI report awaited | NA | NA | Re-activation of earthing has been carried out at above Transformer center. Also necessary maintenance work has been carried out at accident site. | 13 | [9 empty] | AJMN2223009254
83 | JMN | Kalyanpur , Shri. Alabhai Karshanbhai Bela | 11.04.22 | NFHOS | On receipt of telephonic information from mobile no 9909807939 by Shri Govinbhai Dadubhai Karmur a non-fatal electrical accident occurred to Shri Alabhai karsanbhai Bela resi.of Village kalyanpur who was driving a tractor no GJ10 AD 0917 passing below HT line of 11kV kalyanpur ag feeder having nonstandard modified trolly of extended galvanized pipe which came in contact with live 11kV kalyanpur ag feeder and got electrocuted. Thus he met with non-fatal electrical accident on network. SDO, have visited the site and further matter is under investigation. | CEI report awaited | NA | NA | Restringing work has been carried out of conductor span and guy set at transformer center have been re-installed. | 14 | [9 empty] | HJMN2223009088
84 | JMN | Sutariya , A Buffalo of Shri. Ala Bhimshi Gojiya | 12.08.22 | FA | While Buffalo was running from yard towards to transformer it accidentally came in Contact with the base of support angle. The ABC Cable from LT stud to Circuit pole was damaged at the upper side of Circuit pole. The Insulation of ABC Cable was damage due to Atmospheric Condition. The live part of AB Cable was came in Contact with Support Conductor. Support Conductor was tighten with TC pole Structure. The power was came through support conductor and Leakage Current might be flow in SS Set. At that time Buffalo was came in Contact with the base of support angle and electrocuted and died. | CEI report awaited | NA | NA | The messenger from AB cable has been removed from TC and damage part of AB cable repaired and transformer body structure properly earthed. Also necessary maintenance work has been carried out at accident site. | 15 | [9 empty] | AJMN2223009342
85 | JMN | Dared , Shri. Denis Govindbhai Parmar | 13.05.22 | FHOS | On dt. 13.5.22 about 3.30 PM victim went to do centing work of new construction (24 nos of new rooms). While pulling centing box of approx. 13.5 feet iron rod from ground level to first floor by himself alone, Iron rod of 13.5 feet came in contact with 11 KV Alfa JGY line which is above 8 feet horizontal distance from the constructed rooms and approx. 6 meter vertical distance of line from ground level and at that time victim came in contact with 11 KV Alfa JGY line, victim got electrocuted and Fatal accident occurred. Tripping was recorded at 15.50 to 15.55 on Date 13.5.22 for Alfa JGY | CEI report awaited | NA | NA | Notice issued to building owner for illegal construction work near PGVCL line vide letter no. RSD/5430, Dtd : 16.5.22. Also, letter written to local police station for action taken against defaulter of this accident. | 16 | [9 empty] | HJMN2223009123
86 | JMN | Lakhabaval , A Buffalo of Budha Naran Gadhvi | 14.06.22 | FA | On dt. 14.6.22 around 06:00 PM Buffaloes were grazing and rain falling while one buffalo goes near psc pole which is under 132 kv sikka line between Location no 60 and 61 on which pole single phase twin core service cable running and not any bare conductor. due to induction of 132 kv line which is having vertical distance around 8 feet from psc pole top ,earthing current passed through earthing wire of psc pole and passed in water logged nearby meanwhile buffalo came in contact with water running near pole base carrying earthing current and Thus buffalo got electrocuted and fatal accident occurred. | CEI report awaited | NA | NA | The above PSC pole has been shifted. Also, necessary maintenance has been carried at accident location. | 17 | [9 empty] | AJMN2223009169
87 | JMN | Jamnagar , A Buffalo of Shri. Paranshi Aalsurbhai ghoda | 17.07.22 | FA | As per primary investigation and site visit , it is found that due to service wire puncture at pole end touched with fabrication and also due to rain, land surrounding pole was wet and leakage current flows throughout wet surface unfortunately at that time Buffalo passed near the pole and got electrocuted and fatal accident occurred. | CEI report awaited | NA | NA | The damaged service wire been replaced and necessary maintenance has been carried at accident location. | 18 | [9 empty] | AJMN2223009285
88 | JMN | Kharva , A Buffalo of Khimabhai Vejabhai Mundhva | 18.06.22 | FA | As per site visit and information obtained from owner, at evening the buffalo along with other cattle were drinking water at man-made pond (Avedo) near Anganwadi in Kharva village. After drinking water the buffalos and cattle’s were passing near the LT line during rain and heavy wind the earth was wet. this buffalo was passing near to LT pole of kharva ag group in Hadmatiya AG feeder. When the buffalo reached near LT Pole it suddenly fall down and died. On 18.06.2022, because due to monsoon season heavy rain and wind was observed at evening time in this area. As per site visit during inspection, the R-phase of LT line conductor was slipped down from LT shackle insulator and touched to C clamp of LT line due to heavy wind and rain. C-Clamp was connected with GI wire which was earthed along with PVC pipe. Due to leakage of current from conductor to C-clamp and to earth and the land was wet so buffalo when come near LT pole got electrocuted and died. | CEI report awaited | NA | NA | Necessary maintenance work has been carried out at accident site. Field offices were directed to carry out line patrolling to prevent such incidence and accordingly plan for line maintenance work i.e. replace conductor, fabrication, reactivation of earthing of pole and transformer center etc. Also, public awareness program like, village area meeting and campaign regarding safety awareness arranged frequently by PGVCL. | 19 | [9 empty] | AJMN2223009185
89 | JMN | Bhimanugam , Buffalo of Shri. Meghabhai Lakhabhai Vadhrakiya | 19.08.22 | FA | As per the site visit and statement of eye witness of Megha Lakha, it came to know that when 1 no buffalo and 1no cow were grazing near the TC at that time cow's leg came in contact with G.I wire earthing of TC and leakage current flowed through, so it was got electrocuted and died. PM awaited. | CEI report awaited | NA | NA | Reactivation of earthing along with pipe has been carried out. Also necessary maintenance work has been carried out at accident site. | 20 | [9 empty] | AJMN2223009371
90 | JMN | Bhimanugam , Cow of Shri. Meghabhai Lakhabhai Vadhrakiya | 19.08.22 | FA | As per the site visit and statement of eye witness of Megha Lakha, it came to know that when 1 no buffalo and 1no cow were grazing near the TC at that time cow's leg came in contact with G.I wire earthing of TC and leakage current flowed through, so it was got electrocuted and died. PM awaited. | CEI report awaited | NA | NA | Reactivation of earthing along with pipe has been carried out. Also necessary maintenance work has been carried out at accident site. | 21 | [9 empty] | AJMN2223009371
91 | JMN | Naghedi , A Sheep of Shri. Machcha Natha Bambhava | 22.04.22 | FA | On dt. 22.4.22 around 06:45 AM sheep was grazing near Lakhabaval ss. one conductor break and snapped from Sarmat ag Feeder Location 005 and Feeder not tripped although conductor snapped. While grazing that sheep went near snapped live conductor and got electrocuted and fatal accident occurred. | CEI report awaited | NA | NA | The conductor has been replaced and necessary maintenance has been carried at accident location. | 22 | [9 empty] | AJMN2223009100
92 | JMN | Jambuda , Shri. MAHAMMAD RAJUL MAHMMAD SULTAN | 23.04.22 | NFHOS | As per information received from local new paper “ADAG NEWS” on 23rd April regarding electric shock occurred with labour person at supreme hotel, from site visit on dt:25/4/22 come to know that illegal construction of toilet blocks is erected below 11kv KHIJADIYA JGY line. Victim was climbed on that toilet blocks to grab monkey pod fruits from tree and accidently came in induction zone of nearby bare conductor of 11kv high voltage live line. So victim gets electrocuted and this non-fatal accident occurred. After that victim is admitted to G.G.Hospital , Jamnagar by 108 ambulance | CEI report awaited | NA | NA | Notice issued to Supreme hotel to remove illegal construction of toilet block below 11 KV Khijadiya JGY line or apply for shifting of said line immediately. | 23 | [9 empty] | HJMN2223009106
93 | JMN | Laxmipur , A Buffalo of Shri Bhayabhai Rupabhai Zapda | 24.06.22 | FA | As per the site visit and statement of eye witness it came to know that when buffalo Was grazing near the TC at that time buffalo's horns came in contact with guy wire of TC. Accidentally guy wire got broken due to rubbing of buffalo horns. Moreover that broken guy wire also came in contact with live TC jumper and leakage current pass through it, and so buffalo in contact with guy wire got electrocuted and died. PM awaited. At the time of Accident feeder power was in 3-Ph and no Tripping was registered at SS. | CEI report awaited | NA | NA | Necessary maintenance work has been carried out at accident site. Field offices were directed to carry out line patrolling to prevent such incidence and accordingly plan for line maintenance work i.e. replace conductor, fabrication, reactivation of earthing of pole and transformer center etc. Also, public awareness program like, village area meeting and campaign regarding safety awareness arranged frequently by PGVCL. | 24 | [9 empty] | AJMN2223009194
94 | JMN | Gaga-Gurgadh , Cow of BALKRUSHNA PARSOTAMDAS SHARMA | 25.06.22 | FA | As per preliminary Investigation, Shri Balkrushna parsotamdas sharma is handling gaushala of shree gusaiji haveli - gaga gurgadh. And he saw that cow died below the 11 kv MICRO AG feeder. It is found that the conductor of 11 kv Micro AG Tap line is snapped due to wind pressure and fall down on the cow and these 3 nos of cow met with Fatal Electrical Accident. | CEI report awaited | NA | NA | The said conductor has been replaced. Also necessary maintenance work has been carried out at accident site | 25 | [9 empty] | AJMN2223009199
95 | JMN | Gaga-Gurgadh , Cow of BALKRUSHNA PARSOTAMDAS SHARMA | 25.06.22 | FA | As per preliminary Investigation, Shri Balkrushna parsotamdas sharma is handling gaushala of shree gusaiji haveli - gaga gurgadh. And he saw that cow died below the 11 kv MICRO AG feeder. It is found that the conductor of 11 kv Micro AG Tap line is snapped due to wind pressure and fall down on the cow and these 3 nos of cow met with Fatal Electrical Accident. | CEI report awaited | NA | NA | The said conductor has been replaced. Also necessary maintenance work has been carried out at accident site | 26 | [9 empty] | AJMN2223009199
96 | JMN | Gaga-Gurgadh , Cow of BALKRUSHNA PARSOTAMDAS SHARMA | 25.06.22 | FA | As per preliminary Investigation, Shri Balkrushna parsotamdas sharma is handling gaushala of shree gusaiji haveli - gaga gurgadh. And he saw that cow died below the 11 kv MICRO AG feeder. It is found that the conductor of 11 kv Micro AG Tap line is snapped due to wind pressure and fall down on the cow and these 3 nos of cow met with Fatal Electrical Accident. | CEI report awaited | NA | NA | The said conductor has been replaced. Also necessary maintenance work has been carried out at accident site | 27 | [9 empty] | AJMN2223009199
97 | JMN | Chela , Mr.Rahul bhai manji bhai Taviyad | 26.04.22 | FHOS | Contractor Shri Jai ganesh enterprise was given work of TS no 14449150,14449312,14449388 under work order no 703/28.1.22. Three pole DP was erected at place earlier.everyday each contractor is instructed to start work with prior permission of SDO and in presence of supervisor only. As per talk with contractor supervisor Shri Vishal mori,they have started fabrication work of the DP without prior permission of SDO and JE and in absence of supervisor. The victim Shri Rahul Manjibhai Taviyad and other contractor person (Jay Ganesh Ent) went for Erection work for ND scheme in absence of any company supervisor and without prior permission of SDO & JE. Victim climbed on the DP between poles R 59 -R 60 without informing to his supervisor. As the DP was erected below the 11 KV line, and no any LC taken, he came into induction zone and fell down from DP so he met with accident, he immediately transferred to hospital, injuries due to electrocution found near victim's chest, stomach and on face, after short treatment he declared dead. While working on the DP victim had not worn any safety gadgets. | CEI report awaited | NA | NA | Show cause notice issued to Contractor M/s. Jay Ganesh Enterprise by City-2 Division office vide letter no. JCD-2/T-2/Contractor/3499, Dtd: 29.4.22. All the contractor strictly instructed to educate to their labour for use safety gadgets and follow the all safety measures while working on line and insisted them to short & earth the line on both the sides of the working location as per standard procedure and Electrical Network must be properly isolated before starting work in the network. | 28 | [9 empty] | HJMN2223009107
98 | JMN | Ram Nagar,Shankar tekari Jamnagar , Buffalo of Charan Kama Pitha | 27.06.22 | FA | On dated 27.06.2022 at around 10.25 AM a complaint has been received regarding electrocution of two nos of buffaloes at Ramnagar Sankar tekari so immediately the feeder has been made off by DE khambhalia gate and informed to line staff concern. Yesterday night there was heavy wind and moderated rain in this area. During the visit it is found that due to wind pressure LT ABC live jumper came in contact with RSJ pole and RSJ pole become shorted meanwhile two buffaloes passed near the pole came in contact with RSJ pole leakage current passed through their body and got electrocuted and met with fatal electrical accident. | CEI report awaited | NA | NA | New binding of jumper with insulation has been provided and earthing has been reactivated at said accident location. Also, necessary maintenance has been carried at accident location. | 29 | [9 empty] | AJMN2223009204
99 | JMN | Ram Nagar,Shankar tekari Jamnagar , Buffalo of Charan Kama Pitha | 27.06.22 | FA | On dated 27.06.2022 at around 10.25 AM a complaint has been received regarding electrocution of two nos of buffaloes at Ramnagar Sankar tekari so immediately the feeder has been made off by DE khambhalia gate and informed to line staff concern. Yesterday night there was heavy wind and moderated rain in this area. During the visit it is found that due to wind pressure LT ABC live jumper came in contact with RSJ pole and RSJ pole become shorted meanwhile two buffaloes passed near the pole came in contact with RSJ pole leakage current passed through their body and got electrocuted and met with fatal electrical accident. | CEI report awaited | NA | NA | New binding of jumper with insulation has been provided and earthing has been reactivated at said accident location. Also, necessary maintenance has been carried at accident location. | 30 | [9 empty] | AJMN2223009204
100 | JMN | Nandana , A Cow of PREMJI MANJI PARMAR | 27.06.22 | FA | As per information received and site visit, it is found that accident location is a double pole structure of AB switch and one jumper from load side is disconnected and touched with fabrication. So leakage current passed to earth through earth wire. As cow has come in contact with that earth wire, got electric shock and died at place. | CEI report awaited | NA | NA | Conductor has been joint by new jumper work at AB switch. Also necessary maintenance work has been carried out at accident site. | 31 | [9 empty] | AJMN2223009209
101 | JMN | Sethvadala , Udaybhai Atulbhai Vishani | 27.06.22 | NFHOS | On receipt of information from J K lalakiya Villagers of seth Vadala village, On date 02.07.2022 A non-fatal Human accident occurred to shri. Udaybhai Atulbhai Visani At. Seth -Vadala , Due to accidently he was came in contact with live wire of 11KV Dattatrey JGY feeder whose line was passing over victim front side of house. On dated 27.06.2022 approx. 1.0 pm while victim was going to terrace for dry his bath Towel and at that time accidentally he was came in contact with live line and got electrocuted, now he is admitted to Government Hospital Rajkot At present his condition is stable. | CEI report awaited | NA | NA | This accident occurred due to negligence of victim & victim was himself responsible for this accident. Public awareness program like, village area meeting and campaign regarding safety awareness arranged frequently by PGVCL. | 32 | [9 empty] | HJMN2223009221
102 | JMN | Krishnanagar , Hitesh Ramaiya Kumbharvadiya | 28.05.22 | FHOS | As per Information Received from Villager Shri Virambhai Bhura bhai Jilariya, When victim (Hitesh Ramaiya Kumbharvadiya) was Working for hanging of Dish cable on 11 KV line pole of RAMGADH JGY. Somehow might have got electric Shock due to coming in induction zone and Lost his Balance, Fall down on the Earth and Becomes Unconscious. Meanwhile nearby Villagers provided Primary Treatment and Took him Morbi Hospital for More Treatment Where, Hospital Doctor declared Victim Dead. There is possibility of electric Shock from Unknown Source or Some Mechanical Injury occurred due to Falling down from Pole.(PM Report Awaited). | CEI report awaited | NA | NA | The dish cable removed from PGVCL line at above location. Also, notice issued to concern dish cable operator for removing all cable from PGVCL network. | 33 | [9 empty] | HJMN2223009140
103 | JMN | Tankariya , A Buffalo of Shri. Rathod Naran Karamshibhai | 28.08.22 | FA | As per information received From Rathod Naranbhai karamsbhai (Owner)on phone call on dt 28.08.2022.DE/JE Kalyanpur has visited site, and as per statement of eyewitness it is came to know that buffalo was grazing at the site i.e.Nr Tankariya village , A black coloured illegal single phase cable wire from LT pole no 152 was taken by un Authorize person whose premises is not nr the location where accident took place & Inform to police station Kalyanpur for further investigation of unauthorized cable. Also distance of un Authorize cable lying on the ground is about 160 mtrs from existing LT line of village TC of Tankariya village of Hannuman temple. When buffalo was grazing & came in contact with unauthorized live open cable and got electrocuted and died at place. | CEI report awaited | NA | NA | A black coloured illegal single phase cable wire removed from LT pole no 152 and Inform to police station Kalyanpur for further investigation of unauthorized cable. | 34 | [9 empty] | AJMN2223009386
104 | JMN | Hadiyana , A Buffalo of Shri Laxmanbhai Limbabhai vakatar | 30.04.22 | FA | As per site visit and information obtained from Buffalo owner She Buffalo of Shree Laxmanbhai Limbabhai Vakatar with approx. age 7 year was passing near river bank where live return snapped conductor due to heavy wind pressure of 11 kv Kankavati ag lying on earth as Buffalo came in touch with live conductor got electrocuted and died on the spot . As per the Information from 66 kv khiri, 11 kv Kankavati ag is running in single phase and fdr tripped in 1 phase at 12:10 pm after getting try fdr was on and not any tripping than after. Hence due to live part of wire is in the air and not grounded so fdr not tripped and return power conductor is on earth and charged due to return power so this accident might happened when she Buffalo came in contact with it . | CEI report awaited | NA | NA | The above snapped conductor has been replaced with new one. Also necessary maintenance work has been carried out at accident site. | 35 | [9 empty] | AJMN2223009112
105 | JMN | Bhatiya , Mit Prafulbhai Tanna | 30.06.22 | NFHOS | As per site visit it is found that insulation of twin core service wire of NRGP connection is damaged. Also consumer has installed additional plastic roof and twin core service wire is buried under iron plate. Due to aging effect and mechanical pressure of that iron part of plastic roof, insulation may be damaged. Additionally due to rain complete structure of roof was electrically charged. Hence victim came in contact with it and got electric shock. Victim is now admitted to hospital and in stable position. | CEI report awaited | NA | NA | The service wire replaced immediately and necessary maintenance has been carried out at accident location. | 36 | [9 empty] | HJMN2223009216
106 | JMN | SATAPAR , A COW OF SHRI. MERABHAI LAKHMANBHAI HUN | 31.07.22 | FA | As per primary investigation and site visit and information received from Sh. Hun Merabhai Lakhmanbhai, 11KV udepur JGY passed near Merabhai house. The cow was standing under the 11 kv line at morning around 4:30AM.Tripping was recorded at 66KV Satapar SS for 11KV Udepur JGY. Due to heavy wind, conductor slip from disc h/w and broken conductor fall on cow which was standing under the line and came in contact with live conductor and got electrocuted. Died on the spot. | CEI report awaited | NA | NA | The restringing work of conductor and rebinding work of disc hardware have been carried out at accident location. Also necessary maintenance work has been carried out at accident site. | 37 | [9 empty] | AJMN2223009313
107 | JMN | Jamnagar , A Camel of Shri. Lakhaman Pababhai Pandat | 31.08.22 | FA | A fatal accident occurred of camel of Shri lakhaman pababhai pandat On Dt : 31/08/2022 at about 7:30 hrs. As per site visit, it is come to notice that a camel came in contact with live wire of 11 kv GSfC line 2 between no GSFc 2/ 044 & GSFc 2 /43 while running .due to seashore rock area and continuous water logging because of high tide of sea, DP structure of GSFC-2 line got bent and wire span became loose and due to height of camel ,it came in contact with live line wire and got electrocuted. | CEI report awaited | NA | NA | Re stringing work of loose wire span has been carried and new guy provided on DP structure. Also, necessary maintenance has been carried at accident location. | 38 | [9 empty] | AJMN2223009391
108 | JMN | Kalyanpur vadi vistar, Shri Mohanbhai Arjanbhai laxmanbhai Rathod | 16.09.2022 | NFHOS | As information received from Alm Shri D.A. Kanjariya a jumper got disconnected from line so a dim power complaint from farmer of Haripar ag feeder on Dt: 16.09.2022 .During line petrolling a jumper found burnt in Ab switch of 2 nd phase.A line clear on telephonic demanded from on duty operator staff shri Dhavalbhai for the feeder namely 11kV Haripar ag and for crossing of other feeders namely jampar JGY and khijadad ag feeder after confirmation on mobile a contractor labour (contractor: Maheshbhai Karana bhai Gojia) was informed to climbed on pole for rectification of jumper. As soon as he touched the jumper he felt electric shock and fallen down. On SS end a tripping was observed on 11kV Haripar ag feeder. And verbally conform by on duty operator. The breaker of sanosari ag feeder was raked out instead of Haripar AG feeder. Also, line was not shorted and Earthed by staff even at switch where jumper was burnt was not isolated for carry out the work. | CEI report awaited | NA | NA | Informed to S/S in charge for action taken against defaulter (S/S Operator) in this accident as breaker of sanosari AG feeder was raked out instead of Haripar AG feeder. Also, Notice issued to contractor Shri. Maheshbhai Karanabhai Gojia and explanation asked to supervisor Shri. D. A. Kanjariya (ALM - K'pur Sdn) & Shri. V A. Parmar (EA) | 39
109 | JMN | Jaliya Mansar, A Buffalo of Shri. Dineshbhai Manjibhai Solanki | 24.09.2022 | FA | As per site visit and information obtained from owner, during morning at around 10:30, owner took approx. 09 buffaloes for grazing near Und River's bank. Victim buffalo was grazing near transformer centre of consumer. Sh. Karshanbhai Vashrambhai Bediya (cons. no. 31942006136). While grazing, buffalo accidentally touched one guy wire. During monsoon season, water was released from dam during which this guy wire got uplifted from ground. The loose guy wire got tied with buffalo and it moved forward. Meanwhile, as buffalo moved, guy wire came in contact with 11KV conductor between DO fuse and HT bushing of transformer centre and got electrocuted and died. | CEI report awaited | NA | NA | Loose guy wire removed from transformer center and new guy provided. Also necessary maintenance work carried out at accident location. | 40
110 | BHJ | VIRANI , ONE BUFFALO Babulal Pachanbhai Parmar | 02.07.22 | FA | As per information received it came to know that on dated 02.07.2022. Due to heavy rain & wind, water logging was found nearby transformer centre (Village TC ) and accidently momentary leakage current passed on water logged area & Buffalo came in contact with same leakage current & got electrocuted and died. | CEI report awaited | NA | NA | Transformer maintenance was carried out and also tc earthing was done. Letter NO: NKT DO/T-1/Accident/22/2648/Dt.22.07.2022 written to SDO Dayapar regarding regular Maintenance to avoid this type of accident in future. | 1 | [9 empty] | ABHJ2223009222
111 | BHJ | Sekhpir-Dudhai road , Rakesh Muljibhai Maheswari | 03.08.22 | FHOS | A news was received telephonically from Paddhar Police station, that a Mason had an electrical shock at Kisan Cotton Mill, Oppo. R.K. Petrol, Sekhpir-Dudhai Road, Bhuj- Kutch. So, DE & staff of Bhujodi Sdn visited the site. From the statement of the person present at the site and from the Preliminary observation, it has come to the notice that a new Construction work of a small room is carried out at factory inside the premises connection no. 31048 (275 KVA) . Shri Rakeshbhai Muljibhai Maheswari was working as a mason at that site on Dt 3.8.2022. On the day of accident he was standing for the wall plaster work of new room construction. New room is being constructed near to the already existing 11KV line (5ft away) passing outside the premises without maintaining proper clearance and no intimation given to SD office. During the plaster work, victim accidently came in contact of live 11 kv conductor by Plaster Patti [12Ft. Long] and met with a fatal accident. Sign of spark is observed in line conductor. From Incident Site, no one had informed Bhujodi Sdn office about the accident. No tripping observed at VCB panel of 11kv Gada Ag. | CEI report awaited | NA | NA | This accident occurred due to negligence of victim & victim was himself responsible for this accident. Awareness among general public regarding electrical safety "Keep safe distance from Electrical line & Network of PGVCL" during khedut-shibir & village meeting regularly | 2 | [9 empty] | HBHJ2223009321
112 | BHJ | BIDADA , Sh Sagar Shivji Sanghar | 04.07.22 | FHOS | As per site visit and eye witness verbal statement, it seems that the victim was trying to hang on the dead wire of 11 kv Panchvati Ag feeder which was tied with a tree at end from the pole. But on site no any sparking marks or burning marks found on the dead wire which was held by the victim with bare hands. Said wire is removed from the dead span and taken in the custody. Then after, patrolling of this dead line of about 6 spans was done and from 4th span it was noticed that the LT line of Dhrabudi JGY feeder is crossing the dead line from below side and distance between both LT line and HT line is about 4-5 inches. So it the live LT line might have come in contact with the dead HT line at crossing and the victim might have got electric shock while hanging on line. During visit, it could not to be clearly visible due to cloudy weather any sparking marks at possible contact of dead HT line with LT line. Also there was no any sparking marks or burning marks observed on the dead line conductor at accident spot shown by the eye witnesses, | CEI report awaited | NA | NA | Due to sheer negligence of line staff to remove deadline and to erect intermediate pole to maintain safe distance and ground clearance at common public place, show cause notice issued to N B Bharya (ALM) vide O.W 4345 Dt. 05.07.22 and due to negligence of victim this accident was occurred. | 3 | [9 empty] | HBHJ2223009231
113 | BHJ | BHUJ , ONE BUFFALO THEBA ABDULKARIM AAMAD | 06.07.22 | FA | On dated: 06.07.22 at 10:30 am during heavy rain & wind jumper of LT line touched girder pole of the line & current from LT line passes through the girder pole at that time buffalo of shri Theba Abdulkarim Aamad accidently came in contact with that girder pole and got electrocuted at site and fatal Accident occurred | CEI report awaited | NA | NA | Jumper was replaced. At accident place maintenance was completed by sdn level. Safety awareness program were done at various villages. Safety Pamphlets were distributed to the people. | 4 | [9 empty] | ABHJ2223009241
114 | BHJ | Panandhro , MAMAD KASAM IBRAHIM HAJAM | 08.08.22 | NFHD | It came to know that during at late evening heavy cyclonic rainy atmosphere because many feeders got tripped & under fault condition on dt.08.08.2022. To overcome that situation line-staff worked on war foot basis to restore the power to consumer. During this circumstances line staff went to work on muddy land surface for attending fault in 11kv Godhatad JGY. While attending fault on 11 kV GodhatadJGY,line staff ShriM.I.Hazam (Electrical Assi.) With N R Gadhvi(ALM) , during Godhatad JGY patrolling they found the fault by flash and reached the assuming location. A LC was taken by Shri N R Gadhvi for Godhataljgy feeder. After that victim climbed on the pole of New Dhareshi WW feeder (Passing nearby Godhataljgy and belongs to KLTPS- Power station) by mistake. Soon he came in contact with live conductor of New Dhareshi WW Feeder & got electric shock and fell down and got injured. | CEI report awaited | NA | NA | Letter NO: NKT DO/T-1/Accident/22/2951 Date-23/08/2022 written to SDO Dayapar to avoid this type accident in future this type of accident in future. | 5 | [9 empty] | HBHJ2223009332
115 | BHJ | VIRANIYA , ONE COW OF NARAN PETHA KANANI | 09.07.22 | FA | Due to heavy rain and wind from last few days, leakage current was passed from transformer neutral to earth wire of Agriculture Group transformer location num 11 KV VIRANIYA AG/BRY SS/VIR/R33/R1/DT 39 at Viraniya village Sim Area, at that place water logging in surrounding of transformer location area at that time,01 nos cow was passing near that Transformer Structure and accidently came in contact with leakage current of transformer earthing and cow got electrocuted and died. | CEI report awaited | NA | NA | TC maintenance work done. Safety awareness program were done at various villages. Safety Pamphlets were distributed to the people. | 6 | [9 empty] | ABHJ2223009255
116 | BHJ | MANDVI , Shri PREMJI NAGSHI DHEMANI | 09.07.22 | FHOS | After telephonic message, site was visited and it came to knowledge that there was water logging up to approx 3feet due to heavy rain and the tree near Sumatinath tc center had fallen on LT line due to rain and wind pressure.LT conductors were broken due to fallen tree in water .As the victim and another person (VIJAY VISHRAM SOLANKI) along with him were passing across that area by nagar palika rickshaw and they got electric shock. Shri vijay vishram solanki was jumped out and survived and victim cannot jumped and got electric shock and transferred to civil hospital Mandvi and they declared dead. | CEI report awaited | NA | NA | Conductor was replaced and also trree cutting done at accident location.At accident location necessary maintenance was done. Safety awareness program were done at various villages. Safety Pamphlets were distributed to the people. For this Fatal Human Accident Show Cause Notice given to DE SDO Mandvi Town SDn vide letter no. MDO/TECH/SCN/22-23/60 Dated. 11.07.2022 for negligence. | 7 | [9 empty] | HBHJ2223009251
117 | BHJ | MASKA , ONE COW OF AMIRI ALIMAHAMAD SUMRA | 10.07.22 | FA | During site visit at which fatal animal accident took place, a cow had been found dead near the transformer location no: GND SS/11KV RVP AG/12/L04/DT12. At site visit, it was found that due to heavy rain, water logging was at TC. The cow might have touched transformer neutral earthing GI wire and the cow might have got electrocuted due to leakage current of transformer neutral earthing wire and died. | CEI report awaited | NA | NA | TC maintenance work done. Safety awareness program were done at various villages. Safety Pamphlets were distributed to the people. | 8 | [9 empty] | ABHJ2223009264
118 | BHJ | Sanyara vadi vistar , ONE CAMEL OF Kama paba Rabari | 10.08.22 | FA | As per site it is found that when Camel was grazing in Dinesh premji parasiya's ag land, it climbed the stack of soil made By Owner and at that time camel might came in contact with climb on this live wire of 11kv line and got electrocuted. Line clearance of 11KV line was reduced to10 feet appx. Due to stacking and it led camel in direct contact with 11KV line by and got electrocuted. | CEI report awaited | NA | NA | line clearance made proper. Letter NO: NKT DO/T-1/Accident/22/3006/Dt.25.08.2022 written to SDO Nakhatrana regarding regular Maintenance to avoid this type of accident in future. | 9 | [9 empty] | ABHJ2223009349
119 | BHJ | BHUJ , ONE COW OF SHRI Dhanji Chaku Bharvad | 12.08.22 | FA | On dated, 12.08.22 at 09:45 am, due to heavy wind and rain LT Conductor snapped. White passing through this area, one cow come in contact with this conductor and got electrocuted | CEI report awaited | NA | NA | Conductor replaced at accident location. Awareness among general public regarding electrical safety "Do not grazing their animals near the pole/ TC center". | 10 | [9 empty] | ABHJ2223009345
120 | BHJ | Filon vadi vistar , ONE BUFFALO OF SHRI Rabari Thavar Mamu | 12.08.22 | FA | As per site visit it seems that the buffalo was passing between the 11 kv Virani Ag feeder pole location /GAD SS/VIRANI AG/ L51 & L52 at about 04:30 PM on Dt 12.08.2022. On dtd 12.08.2022 there was heavy rain with wind and lightning strokes and at that time, the top pin insulator was flash over and broken on pole L52 and due to which the HT line conductor was also broken. Even though the feeder was not tripped from the S/S and when the buffalo passed nearby the broken conductor between loc L51 & L52, came in contact with the conductor and got electric shock and electrocuted at site. | CEI report awaited | NA | NA | Pin replaced and earthing reactivation work done. Safety awareness program were done at various villages. Safety Pamphlets were distributed to the people. | 11 | [9 empty] | ABHJ2223009340
121 | BHJ | Moti Bhujpar , ONE COW OF Harjibhai Kanjibhai Pataroya | 12.08.22 | FA | As per site visit it seems that the cow was passing through LT line of 11kv mangleshwar jgy feeder, location no mangleshwr fdr/BHPSS/DT09/02 at about 10:00 am on Dt 12.08.2022. Due to heavy rain, wind pressure and lightning strokes water logged near that LT pole .At that same pole insulation of LT AB cable got flash over and damage and touch with LT clamp. At the same time cow came in contact with the wet pole in which leakage current flow through clamp and got electrocuted and died. | CEI report awaited | NA | NA | Due to lightning stroke, damaged insulator and jumpers replaced at accident location. Awareness among general public regarding electrical safety "Do not grazing their animals near the pole/ TC center". | 12 | [9 empty] | ABHJ2223009341
122 | BHJ | PADHHAR , ONE BUFFALO OF Dhanjibhai Rakhyabhai khungla | 13.07.22 | FA | A buffalos was passing near x'mer center situated Opposite owners house and touched GI wire of earthing. Due to rainy season leakage current was passing through earthing. A buffalo came in contact with live part and got electrocuted and died at site. | CEI report awaited | NA | NA | Transformer maintenance done, earthing reactivated done. Awareness among general public regarding electrical safety "Do not grazing their animals near the pole/ TC center". | 13 | [9 empty] | ABHJ2223009271
123 | BHJ | DHRUB , BUFFALO OF Turk Abdul Razak Abdulla. | 13.07.22 | FA | Under Mundra 2 sdn, Today dt: 13.7.22,at 11 kv Nani Dhrub ag feeder (location no. 11kv/NDB/AG/MDR ss/147/L-10) gone tilted due to heavy rain and heavy wind pressure, due to that HT line conductor snapped and gone down near the ground level and at the same time two buffalos were passing near this HT line and came in contact with live conductor and got electrocuted and died. | CEI report awaited | NA | NA | Conductor replaced. Safety awareness program were done at various villages. Safety Pamphlets were distributed to the people. | 14 | [9 empty] | ABHJ2223009270
124 | BHJ | DHRUB , BUFFALO OF Turk Abdul Razak Abdulla. | 13.07.22 | FA | Under Mundra 2 sdn, Today dt: 13.7.22,at 11 kv Nani Dhrub ag feeder (location no. 11kv/NDB/AG/MDR ss/147/L-10) gone tilted due to heavy rain and heavy wind pressure, due to that HT line conductor snapped and gone down near the ground level and at the same time two buffalos were passing near this HT line and came in contact with live conductor and got electrocuted and died. | CEI report awaited | NA | NA | Conductor replaced. Safety awareness program were done at various villages. Safety Pamphlets were distributed to the people. | 15 | [9 empty] | ABHJ2223009270
125 | BHJ | GHADULI , 1 NOS OF CAMEL OF Kumbhar Majid Abdulla, | 15.07.22 | FA | As per information received it came to know that on dated 15.07.2022. Due to heavy rain & wind, water logging was found nearby ghaduli water works connection on Lakhapar road due to wet surface of land pole foundation became weak which tilted the line pole hence reduce the ground clearance , so the Camel passing under this line touched with live conductor got electrocuted and died | CEI report awaited | NA | NA | Pole made straight at that place. Letter NO: NKT DO/T-1/Accident/22/2647/Dt.22.07.2022 written to SDO Dayapar regarding regular Maintenance to avoid this type of accident in future. | 16 | [9 empty] | ABHJ2223009278
126 | BHJ | M. KADIYA , Kasam Junas Parmar | 18.07.22 | FHOS | As Per site visit it is learnt that the victim Kasam Junas Parmar was painting colour on M Kadiya Gram panchayat office, 11KV Ukheda JGY which was passing above GP office. When victim was painting colour above the GP office his head touched the 11KV line and was electrocuted. 11 KV Line is having ground clearance as par norms and about 19 ft height of the lowest conductor from ground. Distance between the terrace of Panchayat office and 11 KV line is 4.5 ft (approx.). It is learnt that the 11 KV Line was in existence before the construction of gram Panchayat. Hence this accident occurred due to ignorance of victim. | CEI report awaited | NA | NA | Victim Himself was responsible for this accident, Letter NO: NKT DO/T-1/Accident/22/2678 Date-25.07.22 written to SDO Nakhatrana regarding regularly arrange awareness meeting related safety to avoid this type of accident in future. | 17 | [9 empty] | HBHJ2223009288
127 | BHJ | Jakhau , ONE BUFFALO OF Isha Ali Ker | 18.08.22 | FA | As per information received it came to know that on dated 18.08.2022 the She Buffalo went for grazing in herd in the morning. Due to heavy rain and wind the LT conductor was snapped the She Buffalo came in contact with broken conductor, electrocuted and died. | CEI report awaited | NA | NA | Conductor replaced. Letter NO: NKT DO/T-1/Accident/22/3353/Dt.20.09.2022 written to SDO Naliya regarding regular Maintenance to avoid this type of accident in future. | 18 | [9 empty] | ABHJ2223009365
128 | BHJ | NETRA , ONE BUFFALO OF Chaki Mubarak Ibhala | 19.07.22 | FA | As per information received it came to know that on dated 19.07.2022 the she buffalo went for grazing herd in morning. due to heavy rain, water logging was found nearby transformer center and accidently leakage current passed on waterlogged area & Buffalo came in contact with same leakage current & got electrocuted and died. | CEI report awaited | NA | NA | Letter NO: NKT DO/T-1/Accident/22/2798/Dt.03.08.2022 written to SDO Dayapar regarding regular Maintenance to avoid this type of accident in future. | 19 | [9 empty] | ABHJ2223009289
129 | BHJ | SAMBHRAI , UN Known Person As Per Police Record | 20.05.22 | FHOS | As per Site visit it is learnt that the (unknown person) Victim Climbed Unauthorizely on 11 Kv Dedhiya Ag Line PSC Pole Due To unknown Reson. And got electrocuted after coming in contact with live line died and fell down on ground and died on the spot. At that time tripping was observed at 66 kv Bayath s/s at 14:00 hours due to earth fault, as per site visit 11 KV Line is having ground clearance as per norms. Hence this accident occurred due to victim's negligence and Blood sports was Found at the top part of PSC Pole. No information has been received from the police department. | CEI report awaited | NA | NA | Victim Himself was responsible for this accident, Letter NO: NKT DO/T-1/Accident/22/ 2219 Date-22/06/2022 written to SDO Kothara regarding regularly arrange awareness meeting related safety to avoid this type of accident in future. | 20 | [9 empty] | HBHJ2223009127
130 | BHJ | BITIYARI , COW OF Savaisinh Indrasinh Rathod | 20.07.22 | FA | Due to heavy rain and wind during last 5 days, HT pole of 11 KV Bitiyari AG feeder got damaged due to lightning stroke and got damaged from bottom, it might have fallen on ground during rainy days but no tripping was observed when feeder was charged on DTD 19.7.22@12.30. HR. Subsequently cow and three nos of calf when they were grazing in nearby sim area, came in direct contact with snapped conductor and all four animals got electrocuted and died. | CEI report awaited | NA | NA | New pole and line was erected. Letter NO: NKT DO/T-1/Accident/22/2769/Dt.01.08.2022 written to SDO Dayapar regarding regular Maintenance to avoid this type of accident in future. | 21 | [9 empty] | ABHJ2223009293
131 | BHJ | BITIYARI , CALF OF Savaisinh Indrasinh Rathod | 20.07.22 | FA | Due to heavy rain and wind during last 5 days, HT pole of 11 KV Bitiyari AG feeder got damaged due to lightning stroke and got damaged from bottom, it might have fallen on ground during rainy days but no tripping was observed when feeder was charged on DTD 19.7.22@12.30. HR. Subsequently cow and three nos of calf when they were grazing in nearby sim area, came in direct contact with snapped conductor and all four animals got electrocuted and died. | CEI report awaited | NA | NA | New pole and line was erected. Letter NO: NKT DO/T-1/Accident/22/2769/Dt.01.08.2022 written to SDO Dayapar regarding regular Maintenance to avoid this type of accident in future. | 22 | [9 empty] | ABHJ2223009293
132 | BHJ | BITIYARI , CALF OF Mulsinh Ranchodsinh Rathod | 20.07.22 | FA | Due to heavy rain and wind during last 5 days, HT pole of 11 KV Bitiyari AG feeder got damaged due to lightning stroke and got damaged from bottom, it might have fallen on ground during rainy days but no tripping was observed when feeder was charged on DTD 19.7.22@12.30. HR. Subsequently cow and three nos of calf when they were grazing in nearby sim area, came in direct contact with snapped conductor and all four animals got electrocuted and died. | CEI report awaited | NA | NA | New pole and line was erected. Letter NO: NKT DO/T-1/Accident/22/2769/Dt.01.08.2022 written to SDO Dayapar regarding regular Maintenance to avoid this type of accident in future. | 23 | [9 empty] | ABHJ2223009293
133 | BHJ | BITIYARI , CALF OF Mulsinh Ranchodsinh Rathod | 20.07.22 | FA | Due to heavy rain and wind during last 5 days, HT pole of 11 KV Bitiyari AG feeder got damaged due to lightning stroke and got damaged from bottom, it might have fallen on ground during rainy days but no tripping was observed when feeder was charged on DTD 19.7.22@12.30. HR. Subsequently cow and three nos of calf when they were grazing in nearby sim area, came in direct contact with snapped conductor and all four animals got electrocuted and died. | CEI report awaited | NA | NA | New pole and line was erected. Letter NO: NKT DO/T-1/Accident/22/2769/Dt.01.08.2022 written to SDO Dayapar regarding regular Maintenance to avoid this type of accident in future. | 24 | [9 empty] | ABHJ2223009293
134 | BHJ | VIRANI , ONE BUFFALO OF Jat Hot Kasam | 21.07.22 | FA | As per site visit it is learnt that on date 21.07.2022 due to rain and heavy wind 11 KV line conductor came in contact with tree due to heavy swing and conductor snapped. The buffalo passing nearby it came in contact of live wire and got electrocuted. | CEI report awaited | NA | NA | Conductor was replaced and tree cutting was done. Letter NO: NKT DO/T-1/Accident/22/2771/Dt.01.08.2022 written to SDO Dayapar regarding regular Maintenance to avoid this type of accident in future. | 25 | [9 empty] | ABHJ2223009296
135 | BHJ | NIRONA , BUFFALO OF SUMRA RAMZAN ILIYAS | 22.05.22 | FA | Two buffalos were passing through the forest area Nirona and Orira and that time conductor of 11 KV Medisar JGY was snapped due to heavy wind .The 2 buffalos came with in direct contact of this broken conductor & got electrocuted. Initially tripping was observed at 11 KV Medisar JGY Panel. But their after power was restored as per standard practice of GETCO Staff. | CEI report awaited | NA | NA | On dated 23.05.22 restringing carried out on location no. 11 KV/Medisar/JGY/feeder/388/NIR/MED/JGY/040/L-75 to L-76 and also new earthing provided to pole no. L-75 -76 and power restored. | 26 | [9 empty] | ABHJ2223009129
136 | BHJ | NIRONA , BUFFALO OF SUMRA RAMZAN ILIYAS | 22.05.22 | FA | Two buffalos were passing through the forest area Nirona and Orira and that time conductor of 11 KV Medisar JGY was snapped due to heavy wind .The 2 buffalos came with in direct contact of this broken conductor & got electrocuted. Initially tripping was observed at 11 KV Medisar JGY Panel. But their after power was restored as per standard practice of GETCO Staff. | CEI report awaited | NA | NA | On dated 23.05.22 restringing carried out on location no. 11 KV/Medisar/JGY/feeder/388/NIR/MED/JGY/040/L-75 to L-76 and also new earthing provided to pole no. L-75 -76 and power restored. | 27 | [9 empty] | ABHJ2223009129
137 | BHJ | ANANDSAR , COW OF SHRI DINESH KANTILAL LIMBANI | 22.08.22 | FA | On date 22/08/2022, Conductor of 11kv Anandsar AG Feeder was snapped due to heavy wind and light rain. At that time, two cow passing nearby came in direct contact with the live Conductor and got electrocuted and died on the spot. | CEI report awaited | NA | NA | Conductor replaced at accident location. Awareness among general public regarding electrical safety "Do not grazing their animals near the pole/ TC center". | 28 | [9 empty] | ABHJ2223009375
138 | BHJ | ANANDSAR , COW OF TRIBHUVAN DEVJI BHAVANI | 22.08.22 | FA | On date 22/08/2022, Conductor of 11kv Anandsar AG Feeder was snapped due to heavy wind and light rain. At that time, two cow passing nearby came in direct contact with the live Conductor and got electrocuted and died on the spot. | CEI report awaited | NA | NA | Conductor replaced at accident location. Awareness among general public regarding electrical safety "Do not grazing their animals near the pole/ TC center". | 29 | [9 empty] | ABHJ2223009375
139 | BHJ | Sayra Near Radha krushn BOP , One buffalo of Jadeja Surubha Desarji | 24.07.22 | FA | As per information received it came to know that on dated 24.07.2022 the buffalo came in contact with GI earth wire of transformer centre and got electrocuted due to leakage current, which might have flown due to load side fault and rainy weather. | CEI report awaited | NA | NA | Letter NO: NKT DO/T-1/Accident/22/2770/Dt.01.08.2022 written to SDO Dayapar regarding regular Maintenance to avoid this type of accident in future. | 30 | [9 empty] | ABHJ2223009302
140 | BHJ | VANKU , Sodha Ranjitsinh Bhurubha | 25.04.22 | FHOS | As per Site it is learnt that the Victim was trying to climb the trolley which was loaded with haybale and might have upper part got struck with the 11 kv line. He might have got electric shock during adjusting the haybale and died, as the fdr was availing single phase power supply that time and no tripping is observed as per GETCO record. 11Kv line is having ground clearance as per norms and about 17 ft height of the lowest conductor from ground | CEI report awaited | NA | NA | Victim Himself was responsible for this accident, Letter NO: NKT DO/T-1/Accident/22/1876 Date-24.5.22 written to SDO Kothara regarding regularly arrange awareness meeting related safety to avoid this type of accident in future. | 31 | [9 empty] | HBHJ2223009113
141 | BHJ | MIRZAPAR , Jatin Arvindray Bhatt | 26.04.22 | NFHD | As per information received and as per site visit, Shri J.A Bhatt, LM, Bhuj Rural alone had gone to attend work of meter shifting of Parmar Dharmeshkumar Karshanbhai, Shajanandnagar, Plot no-27. He had already removed Do fuse of TC center before starting of the work. He had fixed meter in the house and as he was climbing on PSC pole to give connection, he slipped from fourth window of Pole and fell on his bike which was parked near the pole and then on Ground and got injuries in right leg and on face. (Purely Mechanical) | CEI report awaited | NA | NA | Letter NO : BJDN/tech-2/Accident/2021/2615 Date-13.04.22 written to SDO Bhuj Rural regarding regular arrange safety meeting to avoid this type accident in future. | 32 | [9 empty] | HBHJ2223009108
142 | BHJ | MUNDRA , COW of SHANKAR NAGULAL RATHOD | 27.06.22 | FA | In Mundra city and rural area During last night heavy wind, rain and Lightning strike Occurs due to that neutral bare conductor Of Riddhi nagar TC Location Num DT num- 10 Broken at LT Location num DT 10/ 01 TO DT 10/ 02 during this time Two cow Of Shri Shankar Nagulal Rathod passing nearby broken conductor and came in contact with leakage current of neutral Bare conductor due to unbalance load of transformer and electrocuted and died. | CEI report awaited | NA | NA | At accident place rectification work done and conductor repaired. Safety Pamphlets were distributed to the people. | 33 | [9 empty] | ABHJ2223009207
143 | BHJ | MUNDRA , COW of SHANKAR NAGULAL RATHOD | 27.06.22 | FA | In Mundra city and rural area During last night heavy wind, rain and Lightning strike Occurs due to that neutral bare conductor Of Riddhi nagar TC Location Num DT num- 10 Broken at LT Location num DT 10/ 01 TO DT 10/ 02 during this time Two cow Of Shri Shankar Nagulal Rathod passing nearby broken conductor and came in contact with leakage current of neutral Bare conductor due to unbalance load of transformer and electrocuted and died. | CEI report awaited | NA | NA | At accident place rectification work done and conductor repaired. Safety Pamphlets were distributed to the people. | 34 | [9 empty] | ABHJ2223009207
144 | BHJ | MIRZAPAR , Mahobbatsinh Banubha Jadeja | 28.05.22 | FHOS | The building of Sakar Furniture was having renovation work carried out on Dt: 28.05.2022. For this work they were using H-Folding Iron wheeled Ladder had wheels in its base it was easily movable whose height is 5.7 to 6Mts. (At site visit 29.05.22 ladder was dismantled by owner. Photographs taken) During renovation work at around 05:10 PM, due to wind this ladder slipped and started to roll towards 11 KV Mirzapar Ag feeder which is passing nearby parallel main Road. The Distance of 11 KV Mirzapar ag Feeder from Sakar Building is 9 Meter. Two Site workers i.e 1) Mahobbatsinh Banubha Jadeja and 2) Kalpesh Gangji Fafal ran towards the H -frame folding wheels ladder to stop it from rolling and falling down. But at that time topmost part of ladder came in contact with 11 Kv Mirzapar Ag and due to which both victims got electric shock. The ground Clearance of Mirzapar Ag is as per norms.both side poles having T -formation among of 11KV/Mirzapar/AG/feeder/SUK/MIR/048 number of pole vertical distance was 6.56 metre and 11KV/Mirzapar/AG/feeder/SUK/MIR/049 number of pole 5.92 meter. And backfilling work was carried out in front of sakar furniture building under the 11 kv line without permission and the point of accident the ground clearance is 5.2 meter due to back filling done by owner. the Available photograph clearly shows the ladder touching the 11 KV Ag Feeder.. It was confirmed with Sukhpar SS that At the Time Of Accident There was No TT found In 11 KV Mirzapar AG Feeder. | CEI report awaited | NA | NA | Victim Himself was responsible for this accident, safety awareness program were done at various villages. Safety Pamphlets were distributed to the people. | 35 | [9 empty] | HBHJ2223009137
145 | BHJ | MIRZAPAR , Kalpesh Gangji Fafal (NFH) | 28.05.22 | NFHOS | The building of Sakar Furniture was having renovation work carried out on Dt: 28.05.2022. For this work they were using H-Folding Iron wheeled Ladder had wheels in its base it was easily movable whose height is 5.7 to 6Mts. (At site visit 29.05.22 ladder was dismantled by owner. Photographs taken) During renovation work at around 05:10 PM, due to wind this ladder slipped and started to roll towards 11 KV Mirzapar Ag feeder which is passing nearby parallel main Road. The Distance of 11 KV Mirzapar ag Feeder from Sakar Building is 9 Meter. Two Site workers i.e 1) Mahobbatsinh Banubha Jadeja and 2) Kalpesh Gangji Fafal ran towards the H -frame folding wheels ladder to stop it from rolling and falling down. But at that time topmost part of ladder came in contact with 11 Kv Mirzapar Ag and due to which both victims got electric shock. The ground Clearance of Mirzapar Ag is as per norms.both side poles having T -formation among of 11KV/Mirzapar/AG/feeder/SUK/MIR/048 number of pole vertical distance was 6.56 metre and 11KV/Mirzapar/AG/feeder/SUK/MIR/049 number of pole 5.92 meter. And backfilling work was carried out in front of sakar furniture building under the 11 kv line without permission and the point of accident the ground clearance is 5.2 meter due to back filling done by owner. the Available photograph clearly shows the ladder touching the 11 KV Ag Feeder.. It was confirmed with Sukhpar SS that At the Time Of Accident There was No TT found In 11 KV Mirzapar AG Feeder. | CEI report awaited | NA | NA | Victim Himself was responsible for this accident, safety awareness program were done at various villages. Safety Pamphlets were distributed to the people. | 36 | [9 empty] | HBHJ2223009137
146 | BHJ | AMARA , 01 BUFFELO OF Luhar Alimamad osman | 28.05.22 | FA | It came to know that the buffalo (female) was passing through the sim and came in contact with the live wire and got electrocuted. The conductor was snapped due to heavy wind pressure and feeder was having 3 Ph supply schedule. No tripping was observed. | CEI report awaited | NA | NA | Conductor was replaced. Letter NO: NKT DO/T-1/Accident/22/ 2335 Date-26/06/2022 written to SDO Ravapar regarding regular Maintenance to avoid this type of accident in future. | 37 | [9 empty] | ABHJ2223009135
147 | BHJ | PATRI , Balram Vijaybhai Upadhyay | 29.05.22 | FHD | Balrambhai V Upadhyay working as Electrical Assistant(Vidhyut Sahayak) under Mundra 1 sdn and he was going with P S Kalasava(EA) for 11 KV Patri Ag FDR fault work .They found broken conductor of 11 KV Patri Ag feeder near patri village. After line clear of 11 KV Patri Ag taken, P S Kalasava send to Victim to Cut switch of Patri Ag feeder but by mistake victim was climb on near by switch of 11 KV Design tree Exp feeder and he came in contact with live cable wire jumper and he got electrocuted. At the time he couldn't handle his body and fallen down on land. He was shifted to hospital immediately, Doctor declared dead there. | CEI report awaited | NA | NA | Safety awareness meeting has been carried out with line staff to avoid such accident. Give instruction to line staff to short and earth line before working on line. Give strict instruction to line staff Use Safety Gadgets while working on line. | 38 | [9 empty] | HBHJ2223009138
148 | BHJ | Motiber , Gajan Alimamad Ibhrahim | 29.05.22 | FHOS | As Per site visit it is learnt that the Victim Namely Gajan Alimamad Ibhrahim adjusting a bore well machine for doing bore well in AG land of Gajan Adham Rava unfortunately the tail end of bore well tower touched to live span of Pakho AG feeder. He might have got electric shock and died on the spot. As the Feeder was availing 3 ph power supply at that time and tripping was observed as per GETCO record. 11 KV line is having ground clearance as per norms and about 17.5 ft height of the lowest conductor from ground. Hence this accident occurred due to victim's negligence. | CEI report awaited | NA | NA | Victim Himself was responsible for this accident, Letter NO: NKT DO/T-1/Accident/22/2407 Date-30/06/2022 written to SDO Naliya regarding regularly arrange awareness meeting related safety to avoid this type of accident in future. | 39 | [9 empty] | HBHJ2223009136
149 | BHJ | Sukhpar Sim, Shri. Sushik Budek | 9.9.22 | FHOS | On date 09/09/2022 construction work of Shri swamninarayan Distabandhi trust was going on at Mandvi Highway near Divya Bhramlok School in Sukhpar village Sim. 11 Kv Shivparas Ag passes from outside of boundary area of the construction site. During visit it was found that water tank construction was carried out at an approximate distance of 2 feet from Shivparas Ag feeder. During work of this water tank victim was carrying TMT Iron rod from top of water tank towards ground which accidentally came in contact with live conductor of Shiv Paras Ag feeder and victim got electrocuted. Sparking marks seen on 11 Kv line and TMT Iron rod. Height of line from ground is as per norms and span length is 35 mtrs. | CEI report awaited | NA | NA | This accident occurred due to negligence of victim. And also victim was himself responsible for this accident. Awareness among general public regarding electrical safety "Keep safe distance from Electrical line & Network of PGVCL" during khedut-shibir & village meeting regularly | 40
150 | BHJ | Nara, One Buffalo of Maheshbhai Virjibhai Maheshvari | 14.09.22 | FA | As per information received it came to know that on dated 14.09.2022 she buffalo went for grazing herd in morning. Due to heavy rain, water logging was found nearby transformer center and accidently leakage current passed on waterlogged area & Buffalo came in contact with same leakage current & got electrocuted and died. | CEI report awaited | NA | NA | Transformer maintenance done, earthing reactivated done. Awareness among general public regarding electrical safety "Do not grazing their animals near the pole/ TC center". | 41
151 | BHJ | Dhragad vandh (Nara), One Buffalo of Jat Alabhachaya Juma | 26.09.22 | FA | As per information received it came to know that on dated 26.09.2022 , LT Conductor got isolated from the LT shackle Insulator and touched with D clamp in the LT line of the dhragad vandh village transformer , which resulted in leakage current passing through c Earthing wire connected with the D clamp .A Buffalo passing from there incidentally came in contact with earthing wire & got electrocuted. | CEI report awaited | NA | NA | Transformer maintenance done, earthing reactivated done. Awareness among general public regarding electrical safety "Do not grazing their animals near the pole/ TC center". | 42
152 | BHJ | Nadapa, Nirengar shantigar Gusai | 30.09.22 | FHOS | As per information received from newspaper we have visited the site. On 11 KV Hi-Tech industrial feeder one 5 kva single phase transformer is installed on single pole. This transformer is installed to provide 1 single phase Power to weighbridge connection ( 60550/10465 /8). During visit eyewitness was not available at site. As per information available from Shamjibhai vasantbhai dangar ( he is not eyewitness but he heard from eyewitness), the victim was illegally working at transformer centre and while trying to remove D.O. fuse with wooden stick (upper part having iron portion) he felt electric shock and he electrocuted. He was taken to hospital where he was declared dead. | CEI report awaited | NA | NA | This accident occurred due to negligence of victim. And also victim was himself responsible for this accident. Awareness among general public regarding electrical safety "Keep safe distance from Electrical line & Network of PGVCL" during khedut-shibir & village meeting regularly | 43
153 | Anjar | KANDLA , Dosmamad Mishrikhan Masa | 16.04.22 | NFHOS | Information regarding non-fatal electrical accident to victim was received by letter of Kandla marine police station on dated 18.04.2022 at 16:00 hrs. As per police department, on date 16.4.2022 at approx. 11:15 hrs, victim had climbed on tanker. He was having iron bar at that time in his hand. While opening the shutter of tanker, iron bar touched with 11 kv live phase conductor of Kandleshwar feeder under which tanker was parked. As iron bar touched to live conductor, he got electric shock and fell down from tanker due to which non-fatal accident occurred. Note: on dated 16.4.22 no any tripping observed on 11 kv kandleshwar feeder. Also clearance of the lowest conductor from the ground is 7 mtr which is within permissible limit. Minor spot of sparking observed on iron rod and conductor at this location. | CEI report awaited | NA | NA | Letter sent to police station for lodge of fir, safety meeting and village meeting is organised on regular interval for propagation of awareness regarding electrical safety | 1 | [9 empty] | HANJ2223009095
154 | Anjar | Khandek , Buffalo of Ravji Jeram Khandeka | 16.08.22 | FA | As per preliminary Investigation, Shri Maga kara Rabari ("Charvaiya") was going for Grazing Cows and buffalos ("Dhan") from home after then some buffalos and Cow are going near TC for Grazing , when Buffalo reached near 63 KVA TC due to heavy rain and wet land near TC leakage current was there in earthing and due to that 1 no of buffalo got electrocuted and met with the fatal electrical accident. | CEI report awaited | NA | NA | Earthing is rectified & also village meeting arranged by Sub Division office to spread awareness among village people regarding safety against Electricity. | 2 | [9 empty] | AANJ2223009357
155 | Anjar | KHAMBHARA , VISHNUBHAI ARJANBHAI META | 17.04.22 | FHD | On date 17.04.2022 at about 04:35 PM approx., a Fatal Human Department accident occurred to Shri vishnubhai Arjanbhai Meta, App LM. As per site visit and information received, the victim was attending the complian of TC cable fault at Muljibhai Khimabhai AG farm at Khabhara Vadi vistar.Shri Mohanbhai Chandulal Meta , EA, along with apprentice LM Shri Vishnubhai Arjanbhai Meta reached Tc location and Mohanbhai Meta was engaged on phone call for line clear, meanwhile other call received and at that time the victim had climbed on TC structure without prior permision of supervisor and touched the line TC jumper and got electric shock and immediately taken to General Hospital, Anjar and their doctor declared him dead. | CEI report awaited | NA | NA | (1) CS issued to EM - Shri M C .MAHETA, vide no.: ADO/HR/DA/SC/2022/78 DT 03.06.2022. Reply received & decision pending. Awareness among general public regarding electrical safety "Keep safe distance from Electrical line & Network of PGVCL" during khedut-shibir & village meeting regularly. Also safety meeting done at Sub division, division level for awareness of safety | 3 | [9 empty] | HANJ2223009093
156 | Anjar | RATA TALAV , Buffalo of Ahir Rajesh Dana | 24.06.22 | FA | Due to rain and wet land, Leakage current pass from the earth wire of Ratatalav Sim Vistar 10 KVA TC. The Buffalo was passing nearer to the said TC and suddenly came in contact with earthing wire of TC in which leakage current passing and got electrocuted. | CEI report awaited | NA | NA | Earthing reactivated. Awareness among general public regarding electrical safety "Do not grazing their animals near the pole/ TC center". | 4 | [9 empty] | AANJ2223009195
157 | Anjar | ANJAR , COW OF NIRAV VAGHJI PANDYA | 25.08.22 | FA | As per Site visit and eye witness statement, Open Neutral wire of LT Line of Navanagar Area 63 KVA TC was snapped from load side. The Cow & horse were passing nearer to the said snapped conductor and suddenly came in contact with neutral wire & current was passing through both Animals (cow & house) and got electrocuted | CEI report awaited | NA | NA | One Span of neutral Wire was replaced. Awareness among general public regarding electrical safety "Do not grazing their animals near the pole/ TC center". | 5 | [9 empty] | AANJ2223009381
158 | Anjar | ANJAR , HORSE OF SAIYAD ABDULLASHAH ABDULKADAR | 25.08.22 | FA | As per Site visit and eye witness statement, Open Neutral wire of LT Line of Navanagar Area 63 KVA TC was snapped from load side. The Cow & horse were passing nearer to the said snapped conductor and suddenly came in contact with neutral wire & current was passing through both Animals (cow & house) and got electrocuted | CEI report awaited | NA | NA | One Span of neutral Wire was replaced. Awareness among general public regarding electrical safety "Do not grazing their animals near the pole/ TC center". | 6 | [9 empty] | AANJ2223009381
159 | Anjar | kasez , Dashrath Lavjibhai Chauhan | 12.09.22 | NFHOS | As Information regarding non-fatal electrical accident to victim was received by telephonic on dated 12.09.2022 at 08:30 HRS. Site visited by DE KFTZ sdn. 11KV Shreeji FDR crosses boundary wall of KASEZ between location number R1/46 and R1/50. The height of lowest conductor of 11KV line from ground is approx 5.7 mtr and from wall 1.7 mtr. As stated by eye witness Smt. Asha Vishnu Sharma on dated 12.09.2022 at about 08:20 HRS, two numbers of boys climbed the boundary wall (height approx. 4 mtr) of KASEZ illegally (without permission of KASEZ Security Officer) near Ganga SDF Complex. One of the boy jumped down and other boy (Victim Shri Dashrath Lavjibhai Chauhan) on jumping down came in contact with live phase wire of 11KV Shreeji FDR and got electric shock and fell down from the KASEZ boundary wall (At that time TT was observed on 11KV Shreeji FDR at 08:20 HRS) which resulted into non-fatal human accident. Also line staff present at fault office saw the blast near Ganga SDF Complex and rushed to the location and came to know about an accident. The victim had been already moved to the hospital. Spot of sparking observed on conductor at this location. | CEI report awaited | NA | NA | Safety Meeting And Village Meeting Is Organised On Regular Interval For Propagation Of Awareness Regarding Electrical Safety | 7
160 | Anjar | Shinay , 2 nos. of Buffalos of Shri Dilipbhai Ambaram Madhavi | 11.09.22 | FA | On dated 11.09.2022 11Kv Shinay JGY went in permanent fault due to heavy rain and wind pressure. During rectification work message received to line staff for blast on line. So line staff visited the site and found 2 no’s of buffalo dead near 11Kv Shinay JGY pole. 2 no’s buffalo were tied in MS hook approximately 2 meters far away from pole. Also the land was wet due to rain. Pole near buffalo was of 11kV Shinay feeder having 3 no’s pin on top. Out of the 3 no’s, 1 no’s pin was found faulty. So leakage current passed through earth wire and grounded in wet land. Due to leakage current step voltage generated between earth wire and buffalo. Hence 2 no’s buffalo got electrocuted. Further investigation can be made after post mortem report. | CEI report awaited | NA | NA | Damaged Pin Replaced & New Earthing Provided | 8
161 | Anjar | Shinay , 2 nos. of Buffalos of Shri Dilipbhai Ambaram Madhavi | 11.09.22 | FA | On dated 11.09.2022 11Kv Shinay JGY went in permanent fault due to heavy rain and wind pressure. During rectification work message received to line staff for blast on line. So line staff visited the site and found 2 no’s of buffalo dead near 11Kv Shinay JGY pole. 2 no’s buffalo were tied in MS hook approximately 2 meters far away from pole. Also the land was wet due to rain. Pole near buffalo was of 11kV Shinay feeder having 3 no’s pin on top. Out of the 3 no’s, 1 no’s pin was found faulty. So leakage current passed through earth wire and grounded in wet land. Due to leakage current step voltage generated between earth wire and buffalo. Hence 2 no’s buffalo got electrocuted. Further investigation can be made after post mortem report. | CEI report awaited | NA | NA | Damaged Pin Replaced & New Earthing Provided | 9
162 | Anjar | Varsamedi , 1-nos of Buffalo Shri Naranbhai Punjabhai Rabari | 13.09.22 | FA | As per the information received and site visit it was found in preliminary investigation that Shri Naranbhai Punjabhai Rabari, Approx. age 45 years, was going for grazing buffalos in daily routine from home, when he reached near TC of Ambaji nagar where the area near the TC centre was wet due to heavy rain and lightning stroke at that time one of the buffalo while grazing reached near the TC may be got leakage current from earthing wire and due to that 1 nos of buffalo got electrocuted and met with the fatal accident. | CEI report awaited | NA | NA | Earthing reactivated. Awareness among general public regarding electrical safety "Do not grazing their animals near the pole/ TC center". | 10
163 | Anjar | Fatehgadh , 1 Buffalo of Kanabhai Maghabhai Kara | 15.09.22 | FA | As per site visit and Investigation, Shri Kanabhai Maghabhai Kara ("Owner") was going for Grazing buffaloes from home as per his daily routine. Some buffaloes were gone nearer TC for Grazing, during grazing 1 Buffalo reached near 100 kva TC. At that time it was heavy raining with severe lightening strokes and land surrounding TC centre was fully wet and due to that near TC leakage current was there in earthing and 1 no of buffalo got electrocuted and met with the fatal electrical accident. Tripping was not observed in 11 kv Nandela JGY feeder. | CEI report awaited | NA | NA | Earthing is rectified & also Village meeting arranged by Sub Division office to spread awareness among village people regarding safety against Electricity. | 11
164 | Anjar | Bhachau , Sohil Mamadbhai Khalifa | 10.09.22 | NFHOS | Due to heavy wind pressure and frequent lightning strokes top conductor of 11 kV Bhavanipur feeder snapped and fall down in open area of victim house meanwhile victim going to bath in bathroom which is in same open area where conductor was fallen and by accidentally he came in induction zone of conductor and his fingers burnt than after he was admitted in Gove. Hospital and after primary treatment he was discharged from hospital. | CEI report awaited | NA | NA | Four span of 11 KV Bhavanipur URB feeder is dismantling which is passed on resident zuppadpatti area and the 2 TC joint in 11 KV Gurukrupa feeder by replacing conductor of 3 span and one v cross arm and top. | 12
165 | Anjar | Morgar , Sanjay Naresh Rai (Fatal) | 11.09.22 | FHOS | Information received from line staff by phone and according to the site visit by deputy engineer and executive engineer on date 12.09.2022, the truck no GJ 12 BV 9218 was going from mono steel to dudhai Highway, truck driver has roughly overtake traffic and truck distracted from road. Truck driver lost control on driving and truck reached to 11 KV Satansha JGY line, which is 17 meter far away from roadside. The height of truck is 13 feet 8 inch and the height of overhead conductor is 13 feet 7 inch. Due to black sand filling below the line (plot in which line is existing and truck came in contact with line) the height of existing 11 KV line conductor & land is 13 feet 7 inch and due to lost control, truck came in contact with live conductor wire and two person got electrocuted. local people informed to ambulance and both victim sent to nearby dudhai government hospital, where Sanjay Naresh Rai was declared dead by doctor and after primary treatment Pankaj Hardeep Rai was sent to government hospital Bhuj | CEI report awaited | NA | NA | New poles are erected under the line and made proper height to avoid such type accident. Also spread awareness by arranging village meeting with people. | 13
166 | Anjar | Morgar , Pankaj Hardeep Rai (Non Fatal) | 11.09.22 | NFHOS | Information received from line staff by phone and according to the site visit by deputy engineer and executive engineer on date 12.09.2022, the truck no GJ 12 BV 9218 was going from mono steel to dudhai Highway, truck driver has roughly overtake traffic and truck distracted from road. Truck driver lost control on driving and truck reached to 11 KV Satansha JGY line, which is 17 meter far away from roadside. The height of truck is 13 feet 8 inch and the height of overhead conductor is 13 feet 7 inch. Due to black sand filling below the line (plot in which line is existing and truck came in contact with line) the height of existing 11 KV line conductor & land is 13 feet 7 inch and due to lost control, truck came in contact with live conductor wire and two person got electrocuted. local people informed to ambulance and both victim sent to nearby dudhai government hospital, where Sanjay Naresh Rai was declared dead by doctor and after primary treatment Pankaj Hardeep Rai was sent to government hospital Bhuj | CEI report awaited | NA | NA | New poles are erected under the line and made proper height to avoid such type accident. | 14
167 | Anjar | Ner , 3 camels of Navghan Visa Rabari | 25.09.22 | FA | A conductor was broken in Ner JGY feeder. Shri Navghan Visa Rabari ("Owner") was going for Grazing Camels from home as per his daily routine. Some camels were gone near broken conductor for Grazing , during grazing 3 camels came in contact with Live broken conductor and got electrocuted and died on the spot. A tripping was observed in SS at 17:30 time and after trial feeder was remain ON while conductor was on ground. | CEI report awaited | NA | NA | Broken conductor jointed and power restored & also Village meeting arranged by Sub Division office to spread awareness among village people regarding safety against Electricity. | 15
168 | Anjar | Ner , 3 camels of Navghan Visa Rabari | 25.09.22 | FA | A conductor was broken in Ner JGY feeder . Shri Navghan Visa Rabari ("Owner") was going for Grazing Camels from home as per his daily routine. Some camels were gone near broken conductor for Grazing , during grazing 3 camels came in contact with Live broken conductor and got electrocuted and died on the spot. A tripping was observed in SS at 17:30 time and after trial feeder was remain ON while conductor was on ground. | CEI report awaited | NA | NA | Broken conductor jointed and power restored & also Village meeting arranged by Sub Division office to spread awareness among village people regarding safety against Electricity. | 16
169 | Anjar | Ner , 3 camels of Navghan Visa Rabari | 25.09.22 | FA | A conductor was broken in Ner JGY feeder . Shri Navghan Visa Rabari ("Owner") was going for Grazing Camels from home as per his daily routine. Some camels were gone near broken conductor for Grazing , during grazing 3 camels came in contact with Live broken conductor and got electrocuted and died on the spot. A tripping was observed in SS at 17:30 time and after trial feeder was remain ON while conductor was on ground. | CEI report awaited | NA | NA | Broken conductor jointed and power restored & also Village meeting arranged by Sub Division office to spread awareness among village people regarding safety against Electricity. | 17
170 | Anjar | Bhachau , Ibrahimbhai Sulemanbhai Jat | 26.09.22 | FHOS | The truck dumper vehicle no GJ 12 BY 9256 carrying sand was come for unloading the sand and it was unloading near the 11 kV honest feeder span (between location 44 to 45 ). After unloading driver driven the truck forward with keeping hydraulic trolley in rising position with full upward height. During the movement of truck hydraulic trolley touched the live wire of 11 kV line. At that time the cleaner of truck was trying to climb into truck and he got electrocuted. He was sent to Govt hospital where doctor declared him died. The height of lowest conductor from ground is 6.5 meter and Sparking spots were observed on conductor where trolley touched. A tripping was observed in feeder at 15:50 and during taking trial by operator it went into permanent fault. | CEI report awaited | NA | NA | The conductor was restrained which was stretchered by hydraulic trolley of dumper. Also spread awareness by arranging village meeting with people. | 18
171 | JND | KHORASA , Goat OF SHRI MAYURBHAI JAGMALBHAI SARASIYA | 05.07.22 | FA | As per site visit and primary investigation, it is observed that 3 nos of goats of sh. Mayurbhai Jagmalbhai Sarasiya were grazing near road from village Khorasha to Sabri Dam road. As per eye witness, while grazing near dam site, these goats passed nearby transformer centre and suddenly they fell down on the earth and met with accident. During site visit by officers, NO abnormality found in transformer center. Actual reason of death can be traced after post-mortem report. Further matter is under investigation. | CEI report awaited | NA | NA | After occurrence of accident W/W Sabri Dam valu T/C earthng is reactivated and necessary maintenance was carried out at accident place. | 1 | [9 empty] | AJND2223009237
172 | JND | KHORASA , Goat OF SHRI MAYURBHAI JAGMALBHAI SARASIYA | 05.07.22 | FA | As per site visit and primary investigation, it is observed that 3 nos of goats of sh. Mayurbhai Jagmalbhai Sarasiya were grazing near road from village Khorasha to Sabri Dam road. As per eye witness, while grazing near dam site, these goats passed nearby transformer centre and suddenly they fell down on the earth and met with accident. During site visit by officers, NO abnormality found in transformer center. Actual reason of death can be traced after post-mortem report. Further matter is under investigation. | CEI report awaited | NA | NA | After occurrence of accident W/W Sabri Dam valu T/C earthng is reactivated and necessary maintenance was carried out at accident place. | 2 | [9 empty] | AJND2223009237
173 | JND | KHORASA , Goat OF SHRI MAYURBHAI JAGMALBHAI SARASIYA | 05.07.22 | FA | As per site visit and primary investigation, it is observed that 3 nos of goats of sh. Mayurbhai Jagmalbhai Sarasiya were grazing near road from village Khorasha to Sabri Dam road. As per eye witness, while grazing near dam site, these goats passed nearby transformer centre and suddenly they fell down on the earth and met with accident. During site visit by officers, NO abnormality found in transformer center. Actual reason of death can be traced after post-mortem report. Further matter is under investigation. | CEI report awaited | NA | NA | After occurrence of accident W/W Sabri Dam valu T/C earthng is reactivated and necessary maintenance was carried out at accident place. | 3 | [9 empty] | AJND2223009237
174 | JND | JUNAGADH SINDHI SOCIETY , COW (INDIAN), Pending to identified | 07.07.22 | FA | As per site visit and primary investigation, it is observed that one cow passing near PGVCL Lt pole which is near to Muktaben Kishorbhai Mehta's home and came in induction zone of LT pole. On LT pole one of the service wire is cracked near junction point and this live cracked service wire touched to the LT pole. At this situation and time the cow came in contact and got electric shock. | CEI report awaited | NA | NA | Open insulation part of the service cable is removed and fault was rectified And Necessary Maintenance Was Carried out at Accident Place. | 4 | [9 empty] | AJND2223009258
175 | JND | NANI PINDAKHAY , KISHANBHAI VALLABHBHAI BHATTI | 10.06.22 | NFHD | The consumer Shri Mathurbhai Kurjibhai Pansuriya, Vill. Moti Pindakhai having AG Connection from Natraj AG Feeder. Today this Consumer reported his Ag connection fault through Mobile to Shri K.V.Bhatti E.A. VSR 1 Sdn. Shri Bhatti Bhai with Electrical Assistant Shri G.R. Pithiya went to site nearly at 17:45 . Shri Bhatti Bhai has taken Line clear of 11 KV Dairy feeder from Bhalgam S.S. vide LCP No 1536 dt 10.06.22 time 17.50 through SMS and LCP is given to him from SBO of 66 KV SS Bhalgam through SMS at 18.00 PM . At site both E.A. assistant went and for earthing and short work Shri Pithiya Bhai went to Vehicle Bolero to take chain for short and earth, meanwhile victim Shri BhattiBhai climb up the pole to repair the fault and as the LCP is taken of wrong feeder i.e 11 KV Dairy feeder the Power of 11 KV Natraj Ag feeder was on so victim is electrocution and fallen from pole. No any safety precautions taken so non-fatal accident occurred. Though matter is under investigation. Site visit & Rojkam is done by Shri B.D. Parmar E.E. div 1 , Shri H.H. Soni D.E. tech Div 1 Junagadh with Shri N.B. Rathava J.E..Visavadar 1 Sdn., Tripping is noted in 11 KV Natraj Ag Feeder at 18:00 PM | CEI report awaited | NA | NA | More safety awareness meetings will be arranged with line staff. And also adoption of standard work practice and use of safety gadgets during any line works, and DA is pending Due to victim hospitalized. | 5 | [9 empty] | HJND2223009163
176 | JND | JAMBALA , HITESHBHAI GANPATBHAI RATHOD | 10.06.22 | NFHOS | On dt 10.06.2022 for pre-monsoon maintenance Bulandi Contractor team of 11 person was sent to Baradiya ss. Out of 11 person 2 teams were separated one team of 6 person with A.V. Khaniya E.A. and Second team of 5 person with Shri R.K. Makwana.Shri R.K. Makwana went with Shri Hitesh Bhai G.Rathod - Contractor labour person for jumper work in 11 KV Kismat ag feeder emanating from 66 KV Itali S.S. Shri Makvana E A. has taken Line Clear of 11 KV Kismat ag Vide LCP no 2993 Dt 10.06.2022 LCP time 11:03 Am. through SMS . The LCP is given by concern Operator Shri Rainik Talaviya through SMS at 11.08. At site Shri Makvana was doing work at ground for preparing jumper work from 34 mm 2 AAC conductor piece and mean while victim climb up the pole and suddenly fallen down. So Shri Makvana was surprised and scared and immediately called the farmer near him and also informed to Shri KhaniyaBhai E.A. Visavadar 2 and was taken the victim to the main road where contractor other person came and taken victim in 108 ambulance at Mendarda and then Junagadh pvt hospital for further medical treatment., MRI Report of panel meter and consumer meter at site taken for further investigation. | CEI report awaited | NA | NA | Showcause notice issued to supervisor Shri R.K. Makavana E.A. vide no. JRD-1/H.R./S.C.N/0114 Dtd: 15.06.2022 and also aware the line staff and contractors, regarding Electrical Safety. | 6 | [9 empty] | HJND2223009164
177 | JND | BOLASH AG AREA , Calf of SHRI JADAVBHAI KACHRABHAI KAMALIYA | 10.07.22 | FA | As per site visit and eye witness statement, Lt line conductor of 11kv Rampara AG feeder was snapped from LT insulator and Lt line conductor fall on ground at that time power supply is ON (as per GETCO data no tripping occurred) and ground is water logged due to rainy season. At that time a farmer passing with Calf and accidentally one Calf legs touched with live LT line conductor and get electrocuted. | CEI report awaited | NA | NA | Conductor joints done properly and necessary maintenance carried out at accident place, | 7 | [9 empty] | AJND2223009266
178 | JND | MANDODRA , Buffalo of BADHABHAI SIYABHAI MUCHAR | 11.08.22 | FA | As per site visit and primary investigation, it is observed that buffalo of sh. Badha Siya Muchar was passing in dalit vas area of Mandodra village, where Dalit Vas valu 63 KVA transformer is situated in corner area. As per eye witness statement, while buffalo passing nearby transformer centre and suddenly fell down on the earth and met with accident. During site visit by officers, no abnormality found in transformer center. Actual reason of death can be traced after post-mortem report. Further matter is under investigation. | CEI report awaited | NA | NA | Fencing provided at accident location, and also necessary maintenance carried out at accident occurred location. | 8 | [9 empty] | AJND2223009359
179 | JND | GUNDALA , COW OF KADVABHAI MANDABHAI SOLANKI | 11.08.22 | FA | There is a continuous rain at Gundala and line of Jgy feeder is surrounded in river area so soil has become bare and due to this 11 kv Bajrang Jgy pole Broken. During this, Cow was grazing under this 11kv line. Any how it came into contact with live wire and got electrocution. | CEI report awaited | NA | NA | New pole is erected, and also necessary maintenance carried out. at accident occurred location | 9 | [9 empty] | AJND2223009360
180 | JND | JUNAGADH , Cow (Indian), Pending to identified | 12.07.22 | FA | As per site visit and primary investigation, it is observed that one cow passing near PGVCL Ht and Lt composite girder pole which is near to furniture shop of sh. Kurjibhai Meghjibhai Chandegra. After checking with power tester near this pole we found the present of leakage power and this bis due to the LT shackle insulator broken on this pole and live LT 34 sqmm AAAC wire touched to this pole. And there is also one small tree near this pole. Though at the time and situation of this leakage power somehow cow came in contact with this pole and got electric shock. | CEI report awaited | NA | NA | Faulty LT shackle insulator replaced and fault rectified and also necessary maintenance was carried out at accident place. | 10 | [9 empty] | AJND2223009269
181 | JND | DOLATPARA-JUNAGADH , SHRVANKUMAR SATURAMJI MEGHVAL | 13.06.22 | FHOS | As per site visit and primary investigation found that on dated 13.06.202 at 5.20 PM truck no. RJ07 GE 0667 arrived at Dharmananda corporation industries for loading. 11kv Maruti feeder was passing over the place where the truck was parked. Victim climbed on truck cabin to cover truck trolley with PVC sheet. he had taken 29 ft long iron pipe for cover trolley and he lost his balance while lifting iron pipe and iron pipe touched 11kv Maruti feeder and electrocuted and fallen from cabin. After He was taken to hospital but on the way he died. Ground clearance at the point of accident is 7.04 MTR and horizontal distance from factory shed is 3.1 MTR. Though matter is under investigation. And also PM report awaited. | CEI report awaited | NA | NA | Necessary Awareness in public given by SDO to keep safe distance from electrical network while working nearby electrical network. | 11 | [9 empty] | HJND2223009168
182 | JND | JUNAGADH-GROFED MILL AREA , ASHOKBHAI BABUBHAI CHAUHAN | 14.06.22 | FHOS | As per site visit and primary investigation found that Motibag feeder is passing over house of Lilaben Ramji Rathod, work of construction is being done at accident place, victim who was labour might be came in induction zone of 11 kv line conductor. Vertical distance of conductor is about 5 feet from terrace .There was no any tripping of this feeder during that day, matter is under investigation. PM report awaited. | CEI report awaited | NA | NA | Necessary Awareness in public given by SDO to keep safe distance from electrical network while working nearby electrical network. | 12 | [9 empty] | HJND2223009170
183 | JND | PRANSLI AG AREA , Cow of MULJIBHAI RAMBHAI RATHOD | 14.07.22 | FA | As per eye witness statement, at individual tc of Balu Ram Rathod of 11kv Pransli AG feeder blast was heard and cow near to Transformer center get electrocuted and died at that time power supply is ON (as per GETCO data no tripping occurred) and ground is water logged due to rainy season. No leakage current observed on earthing wire. Earthing pipe are in good condition. Actual Reason for the Death is known only after P. M. Report received. Matter under investigation | CEI report awaited | NA | NA | Earthing Reactivated and Necessary Maintenance Was Carried out at Accident Place. | 13 | [9 empty] | AJND2223009272
184 | JND | JETALVAD , Cow (Indian) SHRI UDAYBHAI LAGARBHAI SAVADIYA | 15.07.22 | FA | As per site visit and primary investigation it is found that cow of Sh.Udaybhai lagarabhai savadiya were eating grass at gauchar area land ,opposite bhutda dada temple . At that time so many cows are passed nearby 11 kV kesari ag FDR pole but one of cow touched near pole at that time rain is continue so surrounding land effected by moisture . At that time top (middle) conductor supporting pin faulty. 11 kV kesari ag FDR power on. But FDR not tripped at that time. No any leakage current found at that time. But final reason of death declared after PM report. There was at that time no any GI wire and PVC pipe found at location. | CEI report awaited | NA | NA | Faulty pin insulator replaced and also necessary rectification work was carried out on dtd: 15.07.2022 at accident place. | 14 | [9 empty] | AJND2223009283
185 | JND | UNTDI AG AREA , Elec.AssistantSHRI RAJESHBHAI KHIMJIBHAI PARMAR | 18.07.22 | NFHD | Today on Dt 18.07.22 fault complain repair work of village: Velva and Utadi were allotted to Sh J D Chavda ( Line man) & R K Parmar (Electrical Assistant). As per allotted work, they had attended complain of village: Velva. Afterwards, both line staffs moved to Village: Utadi for attending complain of Utadi villege. They reached at location of complain of consumer Kantilal Mohan faldu's farm (35521/00225/1), who had registered his complain at fault office vide no ( 66724 /17.07.22)., At the location of above farm, other complainer came on site and argued with line man Sh J D Chavda about why their faults are pending. Same time Sh R K parmar had believed that line clear is taken by Line man Sh J D Chavda and without discussing or informing to Lineman Sh J D Chavda, Victim climbed on the DP to repair jumper and victim come in contact with live wire and got electrocution and fell down on earth., No tripping demanded and also No line clear permit was asked from GETCO SS to work on 11 KV Utadi Ag feeder. | CEI report awaited | NA | NA | Show Cause Notice issued to Both. And instructed to carry out more safety awareness meetings will be arranged with line staff. And also adoption of standard work practice and use of safety gadgets during any line works. | 15 | [9 empty] | HJND2223009291
186 | JND | GORAKHMADHI AG AREA , Buffalo of SHRI RAMSHIBHAI UKABHAI KAMALIYA | 19.08.22 | FA | As per site visit and eye witness statement, when Buffalo passing through to Loose Guy Wire of Road Cross Girder Dp , Loose Guy wire touches to 11kv xlpe cable. Suddenly Buffalo get Electrical Shock and get electrocuted and met with fatal accident at that time power supply is ON (as per GETCO data tripping occurred at 11.30 am) and ground is also wet due to rainy season. Spark observed at loose guy wire after 1.5 ft guy insulator. | CEI report awaited | NA | NA | Guy wire was tightened at road cross highway Girder DP and also necessary maintenance was carried out at accident place. | 16 | [9 empty] | AJND2223009369
187 | JND | DHRAMANVA , She Buffalo SHRI RAMABHAI PUNABHAI BARDA | 21.07.22 | FA | Today at approx. 10:30 am the victim buffalo passing through KAPILA river & Due to monsoon season water logging & green grass is there. One 10 kva TC of 11 KV Gomta Ag is nearby river back. When victim passed nearby TC at that time this incident occurred. No leakage current found in earth wire & Tc earthing is proper with pvc pipe. After P.M report receive we will know actual reason of this incident. Matter under investigation | CEI report awaited | NA | NA | Transformer earthing reactivated and also necessary maintenance was carried out at accident place. | 17 | [9 empty] | AJND2223009305
188 | JND | ANKOLWADI , SHRI HARSHADBHAI CHHAGANBHAI PANSURIYA | 22.07.22 | FHOS | On dated 22.07.2022 victim Sh Harshadbhai Chhaganbhai Pansuriya was plucking Bili fruits from Bili tree which was situated near by 11 kv Mandorna Ag line by any instrument. During this, victim might came in contact or in induction zone of 11 kv Mandorna Ag line passing nearby and victim may got electrocuted. | CEI report awaited | NA | NA | Necessary Awareness in public given by SDO to keep safe distance from electrical network while working nearby electrical network. Also informed to police station to lodge FIR against defaulter vide letter no. AKL/TECH/1950, dtd: 25.07.2022 | 18 | [9 empty] | HJND2223009299
189 | JND | GADOI , HIRENBHAI KANTIBHAI PARMAR | 23.06.22 | FHOS | As information received from EA, B. R. Garchar on dated 23.06.2022, site visited by DE Vanthli., As per site information, Victim Sh Hirenbhai Kantibhai Parmar was a driver of dumper of Sand. Today, @ 2:30 PM approximately, Victim had dumped sand at site by erecting dumper container by hydraulic for washing sand and after dumping Victim had not lower dumper container to normal position. Without lowering dumper container, Victim had revers the vehicle and resulted touching of dumper container parts with overhead bare conductor line of 11 kv Akha Ag feeder. Therefore Victim get down from driver seat of vehicle and touch the carrier container part and got electrocuted. Victim was hospitalised where He declared dead. As per preliminary investigation it is observed that by mistake, Victim had reversed the vehicle with erecting position of dumper carrier who touched with live 11 KV line which is 20.3 feet clearance from ground. | CEI report awaited | NA | NA | Necessary awareness in public given by SDO to keep safe distance from electrical network while working nearby electrical network. Also informed to PSI Vanthil police station by Vanthali sub division vide letter no VSD/Tech/5659 dt 28.06.22 that the accident occurred as driver of dumper reversed the vehicle without lowering the carrier container part i.e., due to negligence of dumper vehicle driver and PGVCL company is not responsible for this accident and also letter written to police station vanthli by vanthii sub division to lodge FIR against Shri Kantibhai Jerambhal Parmar, father of victim vide vanthli sub division letter no. VSD/Tech/5845/dt 20.07.22. | 19 | [9 empty] | HJND2223009193
190 | JND | GHANTIYA AG AREA , Calf OF SHRI DIWALIBEN RAJABHAI CHAUHAN | 24.07.22 | FA | As per site visit and eye witness statement, when calf passing nearer to Transformer center victim might came in contact with leakage current and got electrocuted and met with fatal accident at that time power supply is ON (as per GETCO data no tripping occurred) and ground is also wet due to rainy season. | CEI report awaited | NA | NA | Transformer earthing reactivated and also necessary maintenance was carried out at accident place. | 20 | [9 empty] | AJND2223009304
191 | JND | CHIRODA , MAYURBHAI HARSUKHBHAI GIDA | 25.06.22 | FHOS | Telephonic information received from Govt. Hospital Mendarda to J.N.Abda E.A. regarding fatal accident to Sh. Mayur Harsukhbhai Gida in Chiroda Ag area. As per site visit, victim was working for making of Parapet wall on terrace of Kanubhai Vaghabhai Kandoliya's home which is under construction.. Victim was making illegal construction of Parapet wall of balcony under 11kv Chiroda Ag feeder without taking prior permission or without inform of this office. 11 Kv line of Chiroda Ag feeder is exactly passing over the balcony. Conductors of this span are covered by PVC pipe. During construction work under 11 KV line, Victim came in contact with live conductor & got electric Shock & fell down in Balcony. There are two dark spots found on PVC pipe. | CEI report awaited | NA | NA | Give notice to Vaghabhai Jivabhai Khant C/O Rajeshbhai Kanubhai Kandoriya, representative of owner of farm, filled checking sheet no 118709 dt 26.06.22 for illegal use of power supply in residential construction from Ag connection consumer no 80324/00396/0. Asked explanation of Shri A.K.Solanki EA Mendarda sub division vide Mendarda Sub Division letter no MSD/Tech/08//27.06.2022 regarding negligence in carrying out safety survey of feeder allotted to him. Informed PSI Mendarda Police Station to lodge FIR vide Mendarda Sub Division letter no.: MSD/Tech/8575 dt 26.06.22 and also Necessary Awareness in public given by SDO to keep safe distance from electrical network while working nearby electrical network. | 21 | [9 empty] | HJND2223009200
192 | JND | KOYLI , Buffalo Of SHRI SANGABHAI UGABHAI HUN | 25.06.22 | FA | As per information received from sh. Jagabhai Galabhai Rabari at fault center on dated 25.06.2022, Around 12:45, One buffalo of owner Sh.Sangabhai Ugabhai Hun was passing and grazing grass near Village transformer at village: Koyali connected on 11 KV Nandrakhi JGY feeder. At that time when buffalo was grazing grass, it collapsed and shouted as per eye witness. As per preliminary investigation no any leakage current passing through earthing wire or guy at transformer center. Therefore it cannot defined reason of how buffalo collapsed and dead. So it is instructed to send buffalo for PM. There is no any evidence seen of electric shock due to network. 11 KV line and transformer centre condition is as per norms. | CEI report awaited | NA | NA | Transformer center earthing reactivated and also necessary maintenance carried out at accident occurred location. | 22 | [9 empty] | AJND2223009202
193 | JND | BILKHA , Cow (Indian), Of SHRI BHIMABHAI KABABHAI PADSHALIYA | 25.06.22 | FA | As per site visit and primary investigation it is found that Cow of sh. Bhimabhai Kababhai Padshaliya was drinking water from cement water tank which is located approximately 7 feet away from 5 kva transformer centre. After drinking water due to some reason this cow passed nearby tc centre and suddenly fell down on the earth and met with accident. During site visit it is found that transformer internally shorted so leakage current would be passed through earth wire which may be cause of accident. Actual reason of death can be known after post-mortem. Further matter is under investigation. | CEI report awaited | NA | NA | After occurrence of accident faulty transformer replacement and new pole and x'mer earthing and new jumper rectification work was carried out on dtd: 29.06.2022. | 23 | [9 empty] | AJND2223009201
194 | JND | THARELI , SHRI HARESHBHAI ARJANBHAI BHADARKA | 27.04.22 | FHOS | Today corporate drive was arranged at Thareli Village and 11 nos.of connections detected and drive was still continue. during this, probably the victim climbed on nearby AG area TC structure for removal of unauthorised service and somehow he might came in contact of live part of transformer with service wire and got electric shock afterward victim was taken to hospital where he was declared dead. | CEI report awaited | NA | NA | Instruction given to SDO for More Safety awareness meeting will be arranged regarding electrical safety. | 24 | [9 empty] | HJND2223009110
195 | JND | BHALCHHEL , SHRI BENTIBHAI RAMESHBHAI MEGHVAL | 29.05.22 | FHOS | On dated 29.05.202 one tourist bus was park near Gir-Garden dhaba & restaurant under 11 kv Bhalchhel ag feeder. Approx. 9:55 am The victim climb up on bus roof carrier for luggage related work at that time he might came in induction zone of 11 kv line & this fatal accident might be occurred. As per GETCO record feeder was in single phase and no any tripping was observed at the time of accident. Nobody has informed PGVCL from site. The clearance between ground and lowest conductor is measure 19.6 feet. | CEI report awaited | NA | NA | Necessary Awareness in public given by SDO to keep safe distance from electrical network while working nearby electrical network. | 25 | [9 empty] | HJND2223009147
196 | JND | Dungarpur - Shri Hushainbhai Ahemadbhai Saikh, (Network) | 27.06.22 | FHOS | On date- 27.06.22 early morning 6 labour including victim came with Shri shabbir Bhai Ishmail Bhai Belim in Truck No GJ 16X7111 at Dungarpur vill. at Shri Ishmilbhai Hasambhai Belim ( Bhangar vala ) Dela for lifting Iron Scrap ( ભંગાર ) in the said truck . The work is started with all the labour and nearly at 4.15 PM victim might be touch with 11 KV sanatha JGY while he was holding big iron rod and the accident occurred. The matter came to know from Civil hospital to GIDC city Sdn and GIDC city Sdn to Junagadh Rural fault office. During site visit at night one black spot found in 11 kv line with battery light. No any tripping noted in Sanatha JGY. The ground clearance at site is found 5.8 meter from ground and 6.8 meter at tapping site near 5 kva TC i.e. filling of sand and stone is found at site nearly 2.5 feet to 3.00 feet. , Though the matter is under investigation. | CEI report awaited | NA | NA | Necessary Awareness in public given by SDO to keep safe distance from electrical network while working nearby electrical network. Also Informed to Police Station to lodge FIR against defaulter vide latter no. JNDR/TECH/ACCIDENT/2867, dtd: 01.09.2022, and proposal send for approval to replace bare conductor by ABC vide letter no. DEJNDR/SD/TECH/2294, dtd: 05.07.2022. | 26
197 | BVN | Badi , 1 Buffalo-Vijay dula kantariya | 03.07.22 | FA | According to statement of eye witness Haresh bhai Dula bhai kantariya's Buffalo Was passing near to AB switch DP of Padva Ag feeder and touched broken guy wire and got electric shock and electrocuted. During site visit black spot found on lower jumper of B phase. The guy insulator provided above AB switch. The land nearer DP structure was also wet. | CEI report awaited | CEI report awaited | CEI report awaited | New Guy erected at said location | 1 | [9 empty] | ABVN2223009228
198 | BVN | Valukad , 1 Bullock-Anandbhai Madhabhai Khodifad | 04.07.22 | FA | There is LT having LT ABC. The insulation of phase wire of dropper was damage and live part of phase wire touched to messenger wire of LT ABC and due to that earthed fault current passed through messenger wire to Girder pole. The land near said girder pole was wet. At that time, Bullock cart was passing near said Girder pole and got electric shock and electrocuted. | CEI report awaited | CEI report awaited | CEI report awaited | Damage part of dropper wire cut out and fault rectified | 2 | [9 empty] | ABVN2223009232
199 | BVN | Piparla , 1 Cow-Bhupatbhai karamshibhai Khambhaliya | 04.07.22 | FA | During site visit and primary information received from Electrical assistant at site, cow was passing between two pole of transformer center of piparla village where land was wet due to heavy Rain. Cow got electric shock due to leakage current of transformer earthing and electrocuted. No any complaints lodged in sub division | CEI report awaited | CEI report awaited | CEI report awaited | Awareness among general public regarding electrical safety "not tied the animals near the pole/ TC center" during khedut-shibir & village meeting regularly. | 3 | [9 empty] | ABVN2223009233
200 | BVN | CHONDA , Mukeshbhai Balwantbhai Gohel- EA(VS) | 06.08.22 | NFHD | As per morning work distribution Victim went for GEO Urja Survey of 11 KV Nanimal AG FDR. But at time approx. 3:15 PM, Sarpanch of Village Chonda telephonically informed to JE Ghodidhal that 2 nos of JGY LT Pole of Village Chonda is damaged. Hence JE Ghodidhal informed Shri B B Joshi (ALM) and Shri K J Rathod (EA) that to go for Village Chonda for 2 nos of LT Poles damage. Also JE Ghodidhal instructed Shri M B Gohil EA(VS) to go with Shri B B Joshi due to quantum of work at village Chonda is Huge. After that All above 3 staff went to Village Chonda, and found that due to heavy rain, 1 LT Pole fall down and 1 LT Pole broken. Also there is 2 circuit from TC, and both circuit are started from TC DP poles. There is LT ABC in one circuit, and open Conductor in another circuit. Hence they decided to bypass said damaged LT Pole circuit and restore power supply by connecting remaining LT Line to another circuit which is nearest by one span. Hence first they removed DO Fuse for safe working in LT Side. After that they earthed in open conductor LT line circuit. When work completed, victim went to TC for Disconnection of LT ABC from TC DP Pole of first circuit in which LT Pole damaged. At that time due to wet clothes of victim due to rain, he came in induction zone of 11 KV Line, and got electric shock and fell down. He immediately admitted to private hospitals in Palitana and than shifted to BIMS Hospital, Bhavnagar for further treatment. At present his health is good and stable. After X-ray examination, doctor stated that there is no any internal fracture and injury and only burns on right hand and minor Burns on right side chest. He can talk, walk and eat food. | CEI report awaited | CEI report awaited | CEI report awaited | Strictly instruction given to all line staff to use safety measures & tools while working on line. | 4 | [9 empty] | HBVN2223009327
201 | BVN | MOTI VADAL , 1 Cow-Champubhai Valabhai Khuman | 07.07.22 | FA | During site visit and primary information received from villagers present at site, a cow was passing between DP for transformer center and land was wet. Due to wet land and leakage current from earthing, cow got electric shock and electrocuted. HD PVC rigid pipe was provided. No any complaints lodged in sub division. | CEI report awaited | CEI report awaited | CEI report awaited | Awareness among general public regarding electrical safety "not tied the animals near the pole/ TC center" during khedut-shibir & village meeting regularly. | 5 | [9 empty] | ABVN2223009248
202 | BVN | TAVIDA , 1 Bullock-Shidha Jagubhai bhikhubhai | 09.07.22 | FA | During site visit and primary information received from owner present at site, a bullock was passing near transformer center and land was wet. Due to wet land and leakage current from earthing, bullock got electric shock and electrocuted. HD PVC rigid pipe was not provided. As primary information received from present people at site. No any complaints lodged in sub division. | CEI report awaited | CEI report awaited | CEI report awaited | New HD PVC Pipe provided and awareness among general public regarding electrical safety "not tied the animals near the pole/ TC center" during khedut-shibir & village meeting regularly. | 6 | [9 empty] | ABVN2223009256
203 | BVN | BHADRA , Vasantdas Tribhuvandas Gondaliya | 10.06.22 | NFHOS | There is a AG connection in name of Abhabhai Chhaganbhai of CD 10 HP and consumer No 37056/05598/2.During site visit and as per telephonic statement of first eye witness, middle conductor from DO to TC bushing was loose hence victim removed DO element and unauthorizally climbed on TC DP with long binding wire at that time long binding wire touched to incoming live phase of DO fuse and got electric shock and fell down. Eyewitness shifted him to Hanumant hospital, Mahuva. Electric burns found on victim's hand. Victim can talk. Feeder was trip at time of accident. No any complaint received at Sdn. During site inspection, long binding wire found on TC DO. | CEI report awaited | CEI report awaited | CEI report awaited | Letter Written to police station for illegal work on line vide letter no: MAHUVA/R1/ESTA/3240, Dt: 11.6.2022. As per information received victim had died after 2 or 3 days. Also, Awareness among general public regarding electrical safety "Keep safe distance from Electrical line & Network of PGVCL" during khedut-shibir & village meeting regularly. | 7 | [9 empty] | HBVN2223009162
204 | BVN | Dakana , Buffalo-Owner Sagarambhai Haribhai Dabhi | 10.08.22 | FA | As per Telephonic information received by Arjanbhai Jerambhai Jambucha, Surpanch of Village Dakana at 8:10 AM on Dt:10/08/2022 and SDO site visited, near gam kuva area there is LT ABC and separate bare conductor for neutral. This morning approx 7:30 AM, Shri Sagarambhai Haribhai Dabhi was going to his farm with his buffaloes. When buffaloes were passing said location at that time, The land was wet due to rain and buffalo came in contact with said broken neutral wire and got electric shock and electrocuted. | CEI report awaited | CEI report awaited | CEI report awaited | Said broken wire repaired and rectification of said site done. | 8 | [9 empty] | ABVN2223009336
205 | BVN | Taveda , Cow OF Chhaprajbhai valkubhai shidha | 14.08.22 | FA | During site visit and primary information received from present person at site, Phase conductor was broken at area, a cow and buffalo came in contact with live broken conductor of LT line and got electric shock and electrocuted. Power supply is in single phase. PM and Police punchnama awaited. No any complaints lodged in sub division. | CEI report awaited | CEI report awaited | CEI report awaited | Said broken wire repaired and rectification of said site done. | 9 | [9 empty] | ABVN2223009351
206 | BVN | Taveda , Buffalo OF Chhaprajbhai valkubhai shidha | 14.08.22 | FA | During site visit and primary information received from present person at site, Phase conductor was broken at area, a cow and buffalo came in contact with live broken conductor of LT line and got electric shock and electrocuted. Power supply is in single phase. PM and Police punchnama awaited. No any complaints lodged in sub division. | CEI report awaited | CEI report awaited | CEI report awaited | Said broken wire repaired and rectification of said site done. | 10 | [9 empty] | ABVN2223009351
207 | BVN | Dudhala-2 , Cow OF Babubhai Laljibhai Doliya | 15.06.22 | FA | During site visit and primary information received from villagers present at site, 2 nos of cow were passing between transformer center and land was wet. Due to wet land and leakage current from earthing, both cow got electric shock and electrocuted. HD PVC rigid pipe was provided. As primary information received from present people at site. No any complaints lodged in sub division. | CEI report awaited | CEI report awaited | CEI report awaited | Awareness among general public regarding electrical safety "not tied the animals near the pole/ TC center" during khedut-shibir & village meeting regularly. | 11 | [9 empty] | ABVN2223009180
208 | BVN | Dudhala-2 , Cow OF Babubhai Laljibhai Doliya | 15.06.22 | FA | During site visit and primary information received from villagers present at site, 2 nos of cow were passing between transformer center and land was wet. Due to wet land and leakage current from earthing, both cow got electric shock and electrocuted. HD PVC rigid pipe was provided. As primary information received from present people at site. No any complaints lodged in sub division. | CEI report awaited | CEI report awaited | CEI report awaited | Awareness among general public regarding electrical safety "not tied the animals near the pole/ TC center" during khedut-shibir & village meeting regularly. | 12 | [9 empty] | ABVN2223009180
209 | BVN | Dudhala-1 , Cow-Owner Mahipatsinh (mafatsinh )Patubha Vala | 16.07.22 | FA | During site visit and primary information received from present person at site, neutral conductor was broken in water logging area, a cow came in contact with said water and got electric shock and electrocuted. As primary information received from present people at site. No any complaints lodged in sub division. | CEI report awaited | CEI report awaited | CEI report awaited | Broken conductor repaired and rectification of said site done. | 13 | [9 empty] | ABVN2223009377
210 | BVN | Satapada , Buffalo-Ranabhai Sardulbhai Garaniya | 19.06.22 | FA | There is owners House and water tank outside home for drinking of water for his cattles. Also one LT PSC Pole almost 15 feet far from his house. Land surrounding this PSC Pole is wet due to recent rain. Phase wire of dropper on this LT Psc pole is open and touched to C-Clamp, and GI wire of earthing is connected with C-Clamp, hence leakage current passed from dropper to C-Clamp and than GI wire and than to wet land. Hence while Buffalo goes to drink water from that tank outside House, it passes from nearby that PSC Pole, and comes in contact with wet land surrounding LT Pole, and electrocuted and died | CEI report awaited | CEI report awaited | CEI report awaited | Dropper wire location rectified and awareness among general public regarding electrical safety "not tied the animals near the pole/ TC center" during khedut-shibir & village meeting regularly. | 14 | [9 empty] | ABVN2223009186
211 | BVN | Sartanpar , Sanjaybhai Manjibhai Sarvaiya | 19.07.22 | FHOS | As per site visit and information given by Talaja Police station Latter I/W No. 881/22-JUL-2022, SDO visited site on dated: 27.07.22. At accident location, there is one construction work of new House of Shri Tulsibhai Dhirubhai Makwana is on going and 11 KV Mahadev JGY passed from nearby of this construction place. There is scaffold (PALAK) which is made of Iron Pipes (Almost 15 feet long) was tied for filing of Slab of this house. At the time of accident, Victim went to unfold Scaffold (PALAK) after completion of Slab work, and at that time iron pipe of Scaffold touched to 11 KV line wire and got electric shock and died. He immediately shifted sarkari hospital Talaja at that time doctor declared him death. The site visit it is confirmed that at accident location vertical distance from ground was 19 feet (5.79 mtr) and Horizontal distance from house was 6 feet (1.82 mtr). No information given by house owner regarding construction work to PGVCL. | CEI report awaited | CEI report awaited | CEI report awaited | Notice issued to Shri Tulsibhai hirabhai Makwana vide letter no 2976 dt 13.10.22. Also, Awareness among general public regarding electrical safety "Keep safe distance from Electrical line & Network of PGVCL" during khedut-shibir & village meeting regularly. | 15 | [9 empty] | HBVN2223009324
212 | BVN | Bhumbhali , Buffalo-Jorubhai Abhelbhai Lapa | 20.06.22 | FA | During site visit and primary information received from owner of Buffalo at site, Buffalo was passing near transformer center and land was wet. Due to wet land and leakage current from earthing, Buffalo got electric shock and electrocuted. HD PVC rigid pipe was provided. As primary information received from owner, PM and Police punchnama awaited. | CEI report awaited | CEI report awaited | CEI report awaited | Awareness among general public regarding electrical safety "not tied the animals near the pole/ TC center" during khedut-shibir & village meeting regularly. | 16 | [9 empty] | ABVN2223009189
213 | BVN | Shihor , Shri Y M Rathod - LM | 22.04.22 | NFHD | There is shutdown of 11 kv Navnath urb feeder maintenance in which shri Y M RATHOD along with two App L.M assign work of Tree cutting. During shutdown, near Anilbhai's house, bharvadpa area there is a small temple having compound wall and floor having tiles. Victim climbed on wall with the help of wooden ladder for trimming of tree branches suddenly ladder slipped so victim got mechanical injuries on leg and shoulder. Preliminary treatment has been given at CHC Shihor then shifted to BIMS, hospital Bhavnagar. Victim is suffering due to one thigh born broken and hind limbs (ગોળો) also affected. LC of 11 KV Navnath Urban (1). LC No :-706 Time :- 7:20 to 14:20 Taken by :- D A Rajyguru (2) LC No:- 708 Time :- 7:50 to 14:40 Taken by :- V V Rathod (ALM) (3) 11 KV Tarsingda AG LC No:- 707 Time :- 7:30 to 14:35 Taken by :- D A Rajyguru Victim had worn Safety gadgets of Helmet. | CEI report awaited | CEI report awaited | CEI report awaited | Instruction given to staff for takeing proper care while performing climbing work | 17 | [9 empty] | HBVN2223009101
214 | BVN | Nesvad , Kanasingh Ravat | 22.04.22 | FHOS | There was shutdown of 11 kv Kobadi AG feeder hence LC has been taken of Kobdi AG, IOTA Ind and Nagdhanimba AG by A J Bhoj, LM. Line earthed and short at both side. As per statement of supervisor, Victim was standing on ground and carrying out work of conductor jointing after pole erection in tap line of Kobdi AG. At that time, consumer name Dabhi Bharatbhai Jinabhai having AG connection of consumer No 37845/15085/1 and CD 7.5 HP had taken unauthorised power from near by 1 Ph RGPR connection of Dabhi Vinubhai Pragajibhai connected to Ukharalla jgy having consumer No 37845/15110/6 by lying approx 40 meter private twin wire. AG consumer didn't cut DO fuse hence LT power of Ukharalla jgy stepped up and passed through Kobadi AG feeder and Victim got electric shock and electrocuted. Victim shifted to Civil hospital Bhavnagar. Doctor declared him dead. | CEI report awaited | CEI report awaited | CEI report awaited | Mr.A.J.Bhoj suspended vide OO. no.: BVNC/HR-5/DA/271 Dt.16.6.22 & charge sheet given to Mr.Bhoj vide no.BCD-2/HR/DA/OJB/116 Dt.8.6.22, reply received of Mr.Bhoj on dt.16.7.22 & inquiry officer appointed on dt.25.8.22 further actions are under process. FIR is logged on both RL connection using un-authorised power 1. Dabhi Bharatbhai Jinabhai and 2.Dabhi Vinubhai Pragjibhai. Both connection is booked under sec-135 and theft bill issue to them. And both connections are removed from the site. Moreover, Instruction given for stopping un authorized activity and awareness among general public regarding electrical safety during khedut-shibir & village meeting regularly. | 18 | [9 empty] | HBVN2223009102
215 | BVN | Rabari Nes, Nr Anganwadi Kedra, Talav Area , cow OF Danabhai Karsanbhai Khambhlya | 22.06.22 | FA | There is one Girder Pole ( Location no K-170) near Rabari Nes, and one LED Streetlight fixture fixed on this Pole. Land near girder pole is wet due to droppings (Dung) of cattles. While observing it is found that Streetlight fixture was short and hence leakage current passed from fixture to girder pole and than to wet land near girder pole. As per victim's statement, While Cows and Calf were passing near said girder pole, one cow came in contact of wet land and electrocuted, after that another 1 cow & calf touched with dead body of cow and both electrocuted. | Due to leakage current and wet surounding land near girder pole | Proper re activation of earthing should be done | Yes | Notice issued to Palitana Nagarpalika vide letter no PLT-T/TECH/4572, dt: 13.10.22. Also, Awareness among general public regarding electrical safety "Keep safe distance from Electrical line & Network of PGVCL" during khedut-shibir & village meeting regularly. | 19 | 35, 48, 12 | 1164 | 14 | 9 | 22 | 6848 | 20 | 9 | 22 | ABVN2223009191
216 | BVN | Rabari Nes, Nr Anganwadi Kedra, Talav Area , cow OF Danabhai Karsanbhai Khambhlya | 22.06.22 | FA | There is one Girder Pole ( Location no K-170) near Rabari Nes, and one LED Streetlight fixture fixed on this Pole. Land near girder pole is wet due to droppings (Dung) of cattles. While observing it is found that Streetlight fixture was short and hence leakage current passed from fixture to girder pole and than to wet land near girder pole. As per victim's statement, While Cows and Calf were passing near said girder pole, one cow came in contact of wet land and electrocuted, after that another 1 cow & calf touched with dead body of cow and both electrocuted. | Due to leakage current and wet surounding land near girder pole | Proper re activation of earthing should be done | Yes | Awareness among general public regarding electrical safety "Keep safe distance from Electrical line & Network of PGVCL" during khedut-shibir & village meeting regularly. | 20 | 35, 48, 12 | 1164 | 14 | 9 | 22 | 6848 | 20 | 9 | 22 | ABVN2223009191
217 | BVN | Rabari Nes, Nr Anganwadi Kedra, Talav Area , calf OF Danabhai Karsanbhai Khambhlya | 22.06.22 | FA | There is one Girder Pole ( Location no K-170) near Rabari Nes, and one LED Streetlight fixture fixed on this Pole. Land near girder pole is wet due to droppings (Dung) of cattles. While observing it is found that Streetlight fixture was short and hence leakage current passed from fixture to girder pole and than to wet land near girder pole. As per victim's statement, While Cows and Calf were passing near said girder pole, one cow came in contact of wet land and electrocuted, after that another 1 cow & calf touched with dead body of cow and both electrocuted. | Due to leakage current and wet surounding land near girder pole | Proper re activation of earthing should be done | Yes | Awareness among general public regarding electrical safety "Keep safe distance from Electrical line & Network of PGVCL" during khedut-shibir & village meeting regularly. | 21 | 35, 48, 12 | 1164 | 14 | 9 | 22 | 6848 | 20 | 9 | 22 | ABVN2223009191
218 | BVN | Satapada , UPENDRABHAI VELJIBHAI KHARADI (EA) | 23.07.22 | NFHD | Victim has been allotted complain No 20399 regarding tilted LT pole at village satapada in Damarala JGY feeder. Then after team of line staff J T Dund (LI), A K Damor (EA), V B Makvana (EA) and S B Manat (EA) joined with him. After straightening of pole, new GUY provided on this pole and stringing of AB cable was done. After that during the joint of 1 Phase RL service wire on the same pole by shri U V Kharadi- EA suddenly Guy was broken due to nut bolt separate from each other between Anchor Road and Turn buckal, Due to tension of AB Cable, pole broke from bottom and Shri U V kharadi fell down on ground and got mechanical injuries in right and left leg. He immediately shifted Gokul Hospital at Gariyadhar. After primary treatment found fractured on his left and right leg. His helth is good now. Safety Gadgets was wear by Victim during work. | CEI report awaited | CEI report awaited | CEI report awaited | New Guy set erected as well of rectification of said site done | 22 | [9 empty] | HBVN2223009298
219 | BVN | Karela , Buffalo-Owner Lakhabhai dharamsibhai godakiya | 25.07.22 | FA | During site visit and primary information received from villagers present at site, 1 no buffalo was passing between transformer center and land was wet. Due to wet land and leakage current from earthing and as per site situation, disc insulator found faulty so may be leakage current passed by disc insulator to earthing so buffelo contact to leakage current and got electric shock and electrocuted . HD PVC rigid pipe was provided. As primary information received from present people at site. No any complaints lodged in sub division. | CEI report awaited | CEI report awaited | CEI report awaited | Awareness among general public regarding electrical safety "not tied the animals near the pole/ TC center" during khedut-shibir & village meeting regularly. | 23 | [9 empty] | ABVN2223009378
220 | BVN | Sidsar , Nonghabhai Jasabhai Lakum | 25.08.22 | FHOS | As per the site visit there is a Single Phase Temporary Connection in a name of Prerak Chimanbhai Patel Consumer No.:- 36703614768 CD:- 1 KW. During site visit it is found that victim was work on iron ledder at balcony in first floor of the house. During work ledder suddenly slip and fell down to nearer passing 11 KV Line of Sidsar Urban Feeder and victim was electrocuted and fell down to earth. At same time 11 KV Sidsar Urban Feeder was triped and due to such incident jumper was blown out and found in hanged position at nearby location of incident site. PM and PP Report is awaited | CEI report awaited | CEI report awaited | CEI report awaited | Notice issued to Prerak Chimanbhai Patel Consumer No.:- 36703614768 vide letter no: 5340 (A)/ dt: 13.10.22. Also, Awareness among general public regarding electrical safety "Keep safe distance from Electrical line & Network of PGVCL" during khedut-shibir & village meeting regularly. | 24 | [9 empty] | HBVN2223009380
221 | BVN | Parvadi , Cow-Owner Hardikbhai Ramjibhai Dambhala | 29.08.22 | FA | There is one Girder pole of 11 KV Pachchegam AG near Madhav Gaushala and another 11 KV Valam Urban Line passes nearby this Girder pole. Also there is loose guy hanging at this girder pole due to already broken from bottom. Hence while owner of the cow going to give fodder their cows, in meantime one of the cow passed near this girder pole, and its leg entrapped in this hanging loose` guy wire and run with this wire. Due to this guy wire touched to nearby 11 KV Valam Urban live conductor and current passed from 11 KV Valam Urban feeder conductor to guy wire and cow got electric shock and electrocuted. | CEI report awaited | CEI report awaited | CEI report awaited | Broken/Hanging guy was removed and new guy erected | 25 | [9 empty] | ABVN2223009389
222 | BVN | Nana Asarna , Abhalbhai Samantbhai Nakum | 30.05.22 | NFHOS | During site visit and as per statement of first eye witness it has came to know that 11 KV conductor has broken at near gate of enterance of farm. Victim Abhalbhai Samatbhai Nakum has tried to removed this broken conductor from his two vhiler. Tripping observe in 11 KV Vadal JGY feeder at 13:45 and might be possible that at same time when victim try to touch to remove broken conductor from gate of entarance of farm conductor, at same time 1st try for restoring power of said feeder taken by sub station.During site inspection it has found that wind speed is high. And due to this conductor broken. Span between two pole is 50 meters.No any complain received regarding this broken conductor. Victim has been shifted to Hanumant Hospital Mahuva by 108 ambyulance. From Hanumant hospital, victim had reffered to Bhavnagar. | CEI report awaited | CEI report awaited | CEI report awaited | Broken conductor repaired and rectification of said site done. | 26 | [9 empty] | HBVN2223009141
223 | BVN | Mahuva , Himmatbhai Bhikhabhai Nayka | 19.09.22 | FHOS | During site visit and as per first eye witness it has came to know that victim Himmatbhai Bhikhabhai Nayaka working new road work at Bandar Road and he was touch with Pevar Machine. At that time Dumper rise up and touch with near by 11 KV vaghanagar Jgy feeder and Dumper was touch with Pevar machine and Victim was touch with pevar machine and got electric shock. As per information received from R & B department, the said work was doing by contractor name OM construction under R & B department and victim was doing labour work under Om construction agency. During site inspection it has came to know that vartical distance of line from Road is Aprox 20 ft. Further it is to inform that no any information received regarding this work at time i.e no any permission taken by victim. Also no any tripping observed in 11 KV Vaghanagar JGY during this time. Victim was shifted to Mahuva hospital and at where victim was declare died. This accident occurred due to negligency and unawareness of victim. | CEI report awaited | CEI report awaited | CEI report awaited | Letter written to R & B department for illegal work under existing live electricity line vide letter no MHVT/TECH/5258, Dt: 13.10.22. Also, Awareness among general public regarding electrical safety "Keep safe distance from Electrical line & Network of PGVCL" during khedut-shibir & village meeting regularly. | 27
224 | BVN | Nana Asarna , Rathod Jagdishbhai Bhikhabhai | 25.09.22 | FHOS | During site visit and primary information received from eyewitness at site, victim and his father trying to remove the motor from bor with help of electrical puller (Kampi) at time puller touched with 11kv kinkariya ag feeder was passing above the bor and 3 person were got electrical shock, one of them i.e Rathod Jagdishbhai Bhikhabhai dead on the spot and other i.e Rathod Bhikhabhai Ranchhodbhai and Vaghmashi Maheshbhai Atubhai have got electric shock and shifted to hospital for treatment. No any kind of permission taken by victim for this work. Line clearance from ground is approximate 20 feet. Tripping observed on 11 KV kikriya AG feeder at 5:35 PM date: 26.09.2022 and Vaghmashi Maheshbhai Atubhai had inform to SS for not take other try for said feeder. | CEI report awaited | CEI report awaited | CEI report awaited | Awareness among general public regarding electrical safety "Keep safe distance from Electrical line & Network of PGVCL" during khedut-shibir & village meeting regularly. | 28
225 | BVN | Nana Asarna , Rathod Bhikhabhai Ranchodbhai | 25.09.22 | NFHOS | During site visit and primary information received from eyewitness at site, victim and his father trying to remove the motor from bor with help of electrical puller (Kampi) at time puller touched with 11kv kinkariya ag feeder was passing above the bor and 3 person were got electrical shock, one of them i.e Rathod Jagdishbhai Bhikhabhai dead on the spot and other i.e Rathod Bhikhabhai Ranchhodbhai and Vaghmashi Maheshbhai Atubhai have got electric shock and shifted to hospital for treatment. No any kind of permission taken by victim for this work. Line clearance from ground is approximate 20 feet. Tripping observed on 11 KV kikriya AG feeder at 5:35 PM date: 26.09.2022 and Vaghmashi Maheshbhai Atubhai had inform to SS for not take other try for said feeder. | CEI report awaited | CEI report awaited | CEI report awaited | Awareness among general public regarding electrical safety "Keep safe distance from Electrical line & Network of PGVCL" during khedut-shibir & village meeting regularly. | 29
226 | BVN | Nana Asarna , Vaghamshi Maheshbhai Atubhai | 25.09.22 | NFHOS | During site visit and primary information received from eyewitness at site, victim and his father trying to remove the motor from bor with help of electrical puller (Kampi) at time puller touched with 11kv kinkariya ag feeder was passing above the bor and 3 person were got electrical shock, one of them i.e Rathod Jagdishbhai Bhikhabhai dead on the spot and other i.e Rathod Bhikhabhai Ranchhodbhai and Vaghmashi Maheshbhai Atubhai have got electric shock and shifted to hospital for treatment. No any kind of permission taken by victim for this work. Line clearance from ground is approximate 20 feet. Tripping observed on 11 KV kikriya AG feeder at 5:35 PM date: 26.09.2022 and Vaghmashi Maheshbhai Atubhai had inform to SS for not take other try for said feeder. | CEI report awaited | CEI report awaited | CEI report awaited | Awareness among general public regarding electrical safety "Keep safe distance from Electrical line & Network of PGVCL" during khedut-shibir & village meeting regularly. | 30
227 | BVN | Akolali , Bipinbhai Manjibhai Padaya | 28.09.22 | NFHD | As per morning work distribution victim B.M.Padaya- EA(VS) instructed to go with Shri P. C. Karata-LI, A.M.Chudasma-EA for feeder fault work and power supply complains, at the time 12:40 PM 11 KV Mastram AG goes in fault and LC taken by Shri P.C.Katara- LI by LC no 6204 Time:- 12:40 PM. After that at approx time 15:00 PM, all above 3 staff goes to 66 KV Ankolali SS and found that on LSCT DP of 11 KV Mastram AG Feeder one jumper of “R” phase broken, and hence due to running LC of 11 KV Mastram AG, LI Shri P.C.Katara instructed victim to go for Jumper work and hence victim shri Padaya climbed DP pole for jumper work, at that time power supply came from unknown source (due to reason not found), Victim got electrocuted and fell down, and non fatal electrical accident occurred. Safety gadgets are laying down on land near DP. He immediately admitted to private hospital in Palitana and then shifted to private Bajrangdash Bapa Hospital, Bhavnagar for further treatment. At present his health is good and stable. | CEI report awaited | CEI report awaited | CEI report awaited | Explanation asked to supervisor vide no.: GHO/TECH/KHANGI/15 dt.3.10.22. Also, Strictly instruction given to all line staff to use safety measures & tools while working on line. | 31
228 | BTD | RAYPAR , Cow of Bhikhubhai Dhirubhai Govaliya | 01.04.22 | FA | As per site visited, there was water lodging surrounding transformer center of Raypar Village due to water leakage from nearby well from which villager's gets water for their use. The cow passed from nearby transformer center and there may be due to leakage of earthing from GI wire of transformer center. The cow got electrocuted due to minor leakage current and wet surroundings at transformer center. | Due to leakage current passes through poor earthing of tansformer center, where water lodging also obserevd | If the transformer centre maintain at regular interval and if proper breaker put up at LT side and if proper earthing maintain than this accident may not occure | Yes | Reactivation of tc earthing done | 1 | 12, 41 | 1167 | 14 | 9 | 22 | 6849 | 20 | 9 | 22 | ABTD2223009083
229 | BTD | GADHALI , Cow of Khengabhai Gelabhai Mevada | 03.07.22 | FA | As per site visit, there was rain and heavy wind flowed at site continues during day hence land was wet through rainy water. Due to minor puncture in the LT AB cable minor leakage current was flowing. This LT AB Cable was touching to C clamp fabrication and GI wire was passing through this C clamp. So the leakage current passes through the GI wire. The cow passed from nearby LT line pole of Juni Gadhali Village TC. The cow came in contact with such pole and got electrocuted due to minor leakage current and wet surroundings at this LT pole. | CEI report awaited | NA | NA | Punctured LT AB cable span replaced | 2 | [9 empty] | ABTD2223009236
230 | BTD | Nana Chhaida , Bhimabhai Sangrambhai Zapadiya | 04.06.22 | FHOS | As per site visit and information received, victim Shri Bhimabhai Sangrambhai Zapadiya unauthorized climbed on transformer center DP (DT-158) with unknown reason, This Transformer feed power supply to agriculture A-2 connection having consumer no. 6914/01113/3 from 11KV Nana chaida Ag feeder. Victim came in contact with the live part of this transformer center or jumper between DO fuse & transformer center and got electric shock and electrocuted. Also DO fuse & jumper of one phase side is in "Blown Off" position.11 KV Nana chaida Ag feeder tripping noted at 66KV Ratanpar SS at time 06:30 am. No any power complaint received at fault center of paliyad subdivision office for this location and no any other repairing tools like plier etc. found at this site. No any load connected with meter load side and load side wire looks unused since long. No any touch spot found on HT and LT bushing and on nearby wire. Dark spot found on R phase jumper conductor, below D.O. fuse. (Approx. 1.5ft). | CEI report awaited | NA | NA | Connection is disconnected and only after fresh test report it will be reconnected | 3 | [9 empty] | HBTD2223009153
231 | BTD | Jalalpur , Sureshbhai Vajubhai Visani | 09.06.22 | FHOS | As per site visit and information received, victim Shri Sureshbhai Vajubhai Visani unauthorizly climbed on transformer center for might be repairing on DP (DT-192), This Transformer feed power supply to agriculture A-2 connection having consumer no. 37911/03301/3 from 11KV Ramapir Ag feeder. Victim came in contact with the live part of this transformer center jumper between DO fuse & transformer center and got electric shock and electrocuted. Also Dark spot is observed in jumper of R phase side from DO fuse to Transformer. No any tripping is registered in 11 KV Ramapir Ag feeder at 66 KV Jalalpur SS | If consumer/victim call the uathorised person of PGVCL for repairing the fault at DP Structure than this accident may not occurred. | There is a breach of CEI Regulation No.19 | Yes | A letter was written to the police station regarding unauthorised climbing on TC dtd. 10.06.22 | 4 | 19 | 1188 | 14 | 9 | 22 | 6849 | 20 | 9 | 22 | HBTD2223009161
232 | BTD | Botad , BUFFALO of MIR NARANBHAI KHENGARBHAI | 16.08.22 | FA | As per Telephonic Information and site visited on Dated: 16/08/2022, two No's of Buffalo was found dead near 5 Kva TC which was on single PSC pole No. BTD2/SON/056/R104. As per the sight visit it looks that, while two no's.of buffalo passing nearby this TC, One buffalo scrubbing her body with guy wire of this TC pole. Due to rain, the land was wet and as a result the land razed, and guy rod come out from the land and with swing, guy wire's part below the guy insulator touch with 11 KV jumper of this 5 kva TC and current pass through this guy wire to one buffalo and get electrocuted. Due to rainy season and wet land leakage current also pass to other nearby Buffalo and both got electrocuted. One black spot at jumper was observed from the ground level. PM report is awaited. Tripping of 11 KV Sonavala Urban feeder was observed @ 12:10pm. | CEI report awaited | NA | NA | Guy is removed from this location and new guy will provided tomorrow... | 5 | [9 empty] | ABTD2223009356
233 | BTD | Botad , BUFFALO of MIR NARANBHAI KHENGARBHAI | 16.08.22 | FA | As per Telephonic Information and site visited on Dated: 16/08/2022, two No's of Buffalo was found dead near 5 Kva TC which was on single PSC pole No. BTD2/SON/056/R104. As per the sight visit it looks that, while two no's.of buffalo passing nearby this TC, One buffalo scrubbing her body with guy wire of this TC pole. Due to rain, the land was wet and as a result the land razed, and guy rod come out from the land and with swing, guy wire's part below the guy insulator touch with 11 KV jumper of this 5 kva TC and current pass through this guy wire to one buffalo and get electrocuted. Due to rainy season and wet land leakage current also pass to other nearby Buffalo and both got electrocuted. One black spot at jumper was observed from the ground level. PM report is awaited. Tripping of 11 KV Sonavala Urban feeder was observed @ 12:10pm. | CEI report awaited | NA | NA | Guy is removed from this location and new guy will provided tomorrow... | 6 | [9 empty] | ABTD2223009356
234 | BTD | BHANDARIYA , Buffallo of Bhupatbhai Rambhai Rabari | 19.04.22 | FA | As per Telephonic Information and site visited on date 19.04.2022 at 16:45 PM, a Buffalo of owner Shri. Bhupatbhai Rambhai Rabari, was passing near by the village Transformer named as Aveda Valu TC of Village Bhandariya. As per statement of buffalo’s Owner , while buffalo was passing near by the circuit pole of TC, buffalo scrubbing with Guy Wire of LT Circuit Pole near TC DP, at that time, Guy wire break from guy rod due to the rusting and touched with the live part of LT AB Cable on the circuit pole and got electrocuted. PM report is awaited. | When the buffalo scrubbing with Guy wire, due to that Guy wire (Without Guy Insulator) touch with the open LT Jumper of the first LT Pole of the transformer | As per CEI Regulation-2010 regulation no.12 & 72, If periodicaly maintenance done of transformer center with proper earthing and proper capacity of fuse provided at LT side and Guy insulatore provided than this accident may not occurred. | Yes | E/O of new guy set | 7 | 12, 72 | 1158 | 14 | 9 | 22 | 6849 | 20 | 9 | 22 | ABTD2223009096
235 | BTD | Botad , BUFFALO of Shri Mahmadbhai Jinabhai Bhas | 29.06.22 | FA | As per Telephonic Information and site visited on Dated: 29/6/2022, one Buffalo was found dead near LT PSC pole No. SON/DT-014/C1/005. LT ABC line passing on this pole and one street light with metal body fixer fixed on this pole. The fixture of street light is in contact with GI earthing wire. This street light badly burnt and leakage current passing through burnt street light to metal body fixture through GI wire of pole Earthing. PVC rigid pipe found damaged at lower part of PSC pole. As per owner’s statement while buffalo scrubbing her body with pole, leakage current pass through buffalo and get electrocuted. PM report is awaited. | CEI report awaited | NA | NA | This street light dropper disconnected and informed to concern officer of Nagarpalika vide letter No. 5485 Dtd: 30.6.22 | 8 | [9 empty] | ABTD2223009213
236 | BTD | BUFFACLO-Shri Yogeshbhai Nagjibhai Khambhaliya | 12.09.22 | FA | As per Telephonic Information and site visited, one Buffalo was found dead near Haridarshan TC at behind Gurukrupa Mobile, Opposite Ratnadeep complex, Aveda Gate, at river bank, Botad. There is 100 KVA Transformer center erected on PSC pole .Rigid PVC pipe provided at earthing of transformer. Due to continue rain, the land was wet around this transformer center. At LT side , 150 mm2 pvc cable burnt and due to heavy wind this burnt pvc cable comes in contact with DP angle which is in contact with earthing wire . Due to continuous rain, leakage current passes through this cable to DP Angle to earthing wire. When a buffalo passes nearby this transformer center, she experienced leakage current and electrocuted. There is a sparking spot found on DP angle. PM report is awaited | CEI report awaited | NA | NA | Cable rectified | 9
237 | BTD | COW OF Lalabhai Sangabhai Mevada | 15.09.22 | FA | As per Site visit, Due to rain and lightning stroke, 11 KV pin insulator fault occurred on pole no.26 of 11 KV Ingorala ag feeder, due to this live 11 KV conductor slipped from pin and fallen on V X arm. There was iron wire fencing of farm tied with the HT PSC pole. Because of this fault, fault current passed through G.I earthing wire of pole to iron wire fencing and at the same time the cow passing nearer to fencing and touched the iron wire fencing of farm and electrocuted. Tripping was observed in 11kv Ingorala ag feeder and was gone in permanent fault.PM report is awaited | CEI report awaited | NA | NA | PVC rigid earthing pipe provided | 10
238 | AMR | UNA , COW OF RANJITBHAI PUNABHAI BAMBHANIYA | 01.07.22 | FA | As per primary information a cow & calf was passing near LT Line pole during that time due to heavy rain near Swami Narayan Temple TC (Varsingpur Road) LT Line Second Pole Jumper Burnt and touch LT Cross arm and leakage current passing through the LT line wet pole and that time cow & calf accidentally touched the LT Line pole and got electrocuted and fatal animal accident occurred. | CEI report awaited | NA | NA | Provided New Jumper with Biding | 1 | [9 empty] | AAMR2223009217
239 | AMR | UNA , CALF OF RANJITBHAI PUNABHAI BAMBHANIYA | 01.07.22 | FA | As per primary information a cow & calf was passing near LT Line pole during that time due to heavy rain near Swami Narayan Temple TC (Varsingpur Road) LT Line Second Pole Jumper Burnt and touch LT Cross arm and leakage current passing through the LT line wet pole and that time cow & calf accidentally touched the LT Line pole and got electrocuted and fatal animal accident occurred. | CEI report awaited | NA | NA | Provided New Jumper with Biding | 2 | [9 empty] | AAMR2223009217
240 | AMR | HEMAL , SHEEP OF LALJIBHAI MEGHABHAI BARAD | 01.07.22 | FA | As per the eye witness statement when sheep try to run nearby from TC at the time accidentally came in contact with leakage current of TC neutral and got electrocuted. | CEI report awaited | NA | NA | Reactivation of earthing carried out and maintenance done | 3 | [9 empty] | AAMR2223009223
241 | AMR | MALILA , COW OF ANADBHAI BHIKHABHAI PADSALIYA | 02.07.22 | FA | as per site visit & information received it is came to knowledge that accident location is 11 KV DP with AB switch. When cow was passing nearer to this DP, she was rubbing her head with Guy Wire. Due to AB Switch jumper touched with this Guy Wire below Guy Insulator part, cow was directly came in contact with live current through Guy Wire & got electrocuted. | CEI report awaited | NA | NA | New Guy Provided | 4 | [9 empty] | AAMR2223009220
242 | AMR | NATHAD , COW OF SARMANBHAI GABHARUBHAI CHUDASAMA | 03.07.22 | FA | As per primary information received and site visited accident location is LT pole of nathad jgy feeder. Service connection of household consumer: Panchiben Dhirubhai Chudasma, Consumer No: 84521/00948/4 has been provided from LT pole. Insulation of service wire of above said connection found deteriorated and broken and into direct contact with LT cross arm. PSC LT pole was wet due to rain and surrounding area nearby pole was also found wet as it was raining. Thus leakage current was passing through deteriorated service wire to LT cross arm to wet pole and when a cow passing nearby wet land got electrocuted due to this leakage current and an animal fatal accident occurred. | CEI report awaited | NA | NA | Faulty Service Rectified | 5 | [9 empty] | AAMR2223009227
243 | AMR | PIPALVA , COW OF RUKHADBHAI VALABHAI RATADIYA | 04.07.22 | FA | During Site visit it is observed that Due to rain soil is wet and due to voltage in Neutral, leakage current may flow in Transformer neutral earthing and that time A Cow and Calf were passing near Transformer center of above location, got electrocuted and fatal animal accident occurs. At site all earthing on both side of Transformer are provided with PVC pipes. | CEI report awaited | NA | NA | Reactivation of earthing carried out and maintenance done | 6 | [9 empty] | AAMR2223009229
244 | AMR | PIPALVA , CALF OF RUKHADBHAI VALABHAI RATADIYA | 04.07.22 | FA | During Site visit it is observed that Due to rain soil is wet and due to voltage in Neutral, leakage current may flow in Transformer neutral earthing and that time A Cow and Calf were passing near Transformer center of above location, got electrocuted and fatal animal accident occurs. At site all earthing on both side of Transformer are provided with PVC pipes. | CEI report awaited | NA | NA | Reactivation of earthing carried out and maintenance done | 7 | [9 empty] | AAMR2223009229
245 | AMR | MUNDHIYA RAVANI , BUFFALO OF MANDANBHAI SHAMLABHAI MALVI | 04.07.22 | FA | As per site visit & information received it is came to knowledge that during heavy rain LT Neutral Conductor broke from Shackle Insulator and fell on ground by touching with another live phase conductor of that LT Line. At that time buffalo was passing from there and came in contact with that broken conductor and got electrocuted. | CEI report awaited | NA | NA | Re-Joint of conductor | 8 | [9 empty] | AAMR2223009230
246 | AMR | KAGDADI , JIVRAJBHAI PUNABHAI GADHIYA | 05.05.22 | FHOS | As per site visit & information received, it is come to knowledge that both Victims were trying to pulled out Electric Submersible Motor Pump with help of "Mechanical Pulling Machine (Ghodi)” keeping below live HT Line of 11kv Maheshwar Ag Feeder which is passing nearer to that place. During that time iron rod pipe having length of 23 Ft. which was connected with machine touched to live Conductor of HT Line. Due to that live current passed through iron rod pipe to pulling machine & both victim who were working with pulling machine got electric shock. The Vertical distance of conductor from ground level is 19 Ft. But due to having long size of pulling pipe of iron rod, it touched to line which is passing over there. No any responsibility of PGVCL. | CEI report awaited | NA | NA | Safety awareness meeting done | 9 | [9 empty] | HAMR2223009116
247 | AMR | KAGDADI , Pintubhai Ramjibhai | 05.05.22 | FHOS | As per site visit & information received, it is come to knowledge that both Victims were trying to pulled out Electric Submersible Motor Pump with help of "Mechanical Pulling Machine (Ghodi)” keeping below live HT Line of 11kv Maheshwar Ag Feeder which is passing nearer to that place. During that time iron rod pipe having length of 23 Ft. which was connected with machine touched to live Conductor of HT Line. Due to that live current passed through iron rod pipe to pulling machine & both victim who were working with pulling machine got electric shock. The Vertical distance of conductor from ground level is 19 Ft. But due to having long size of pulling pipe of iron rod, it touched to line which is passing over there. No any responsibility of PGVCL. | CEI report awaited | NA | NA | Safety awareness meeting done | 10 | [9 empty] | HAMR2223009116
248 | AMR | RAJULA , DILIPBHAI BHIKHBHAI JADAV | 05.06.22 | FHOS | As per information received from police station letter and newspaper and site visit accident location is HT line passing nearby house of Jamalbhai hasambhai dal at bidi kamdar area, Rajula city. Victim as profession as mason working on daily basis. On that day jamalbhai dal hired victim for parapet work on the roof shed which was located 1st floor on his house and 11 Kv ht Rajula city line was passing nearby working place. For parapet work victim stood on wall of 1 st floor of the house and to do parapet work he tried to jump on roof shed but that time he accidentally came in to contact with one conductor of HT line of city feeder and got electrocuted. Accident occurred due to unauthorised construction done nearby PGVCL network and work carried out work without prior information. | Victim as profession as mason working on daily basis and On that day jamalbhai dal hired victim for perafit work on the roof shed which was located 1st floor on his house and 11 Kv ht Rajula city line was passing nearby working place. For perafit work victim stood on wall of 1 st floor of the house and to do perafit work he tried to jump on roof shed and accidentally came in to contact with one conductor of HT line of city feeder and got electrocuted. | Breach the rules of CEA regulation no. 13 &61. If victim maintain distance between house and 11 KV line and did not extended 3-feet unauthorized construction so this accident may not occurred. | YES | Notice issued to Premises owner for unauthorized construction near HT line | 11 | 13, 61 | 1073 | 18 | 8 | 22 | 6217 | 25 | 8 | 22 | HAMR2223009159
249 | AMR | DEVLA , BUFFALO OF PATABHAI KUKABHAI DHAGAL | 06.07.22 | FA | As per site visit & information received it is came to knowledge that land surrounding of 10 kva Transformer Center was wet due to rain. Buffalo might have got electrocuted due to leakage current of Transformer when she was passing nearby that place | CEI report awaited | NA | NA | Reactivation of earthing carried out and maintenance done | 12 | [9 empty] | AAMR2223009239
250 | AMR | BHAKODAR , BUFFALO OF BHAGVANBHAI NANJIBHAI SHIYAL AND OTHER 1 | 09.08.22 | FA | As per the eye witness statement and site visited surrounding Land of accident location was found wet due to rain. Pin insulator on HT pole loc no JFD/VAR/260/R021 found faulty. Also tripping recorded in 11KV Varaswarup JGY feeder. Buffalo might be electrocuted due to leakage fault current while passing on wet land nearby HT pole | CEI report awaited | NA | NA | Faulty Pin Replaced | 13 | [9 empty] | AAMR2223009337
251 | AMR | BHAKODAR , BUFFALO OF BHAGVANBHAI NANJIBHAI SHIYAL AND OTHER 1 | 09.08.22 | FA | As per the eye witness statement and site visited surrounding Land of accident location was found wet due to rain. Pin insulator on HT pole loc no JFD/VAR/260/R021 found faulty. Also tripping recorded in 11KV Varaswarup JGY feeder. Buffalo might be electrocuted due to leakage fault current while passing on wet land nearby HT pole | CEI report awaited | NA | NA | Faulty Pin Replaced | 14 | [9 empty] | AAMR2223009337
252 | AMR | VADVIYALA , BUFFALO OF MANHARBHAI RAVJIBHAI DAMODARIYA | 10.08.22 | FA | As per information received and site visited, as per owner's statement when Buffalo passed adjacent to the transformer centre got electrocuted and died. On site visit it has been observed that land surrounding to tc was highly wet due to rain. The accident may possibly occurred due to the Buffalo came in contact with leakage current passing through wet psc pole and got electrocuted. | CEI report awaited | NA | NA | Reactivation of earthing carried out and maintenance done | 15 | [9 empty] | AAMR2223009338
253 | AMR | DHARI , BUFFALO OF BHIMJIBHAI GOVINDBHAI RATHOD | 11.08.22 | FA | As per site visit & information received it is came to knowledge that land surrounding of 10 kva Transformer Center was wet due to rain. Buffalo might have got electrocuted due to leakage current of Transformer when she was passing nearby that place. | CEI report awaited | NA | NA | Reactivation of earthing carried out and maintenance done | 16 | [9 empty] | AAMR2223009339
254 | AMR | PITHADIYA , BHARATBHAI BHIMJIBHAI SOLANKI | 12.05.22 | NFHD | As per site visit & information received, it is come to knowledge that Supervisor Sh. H B Vaghasiya (LM) and Victim were attending 11 KV Pithadiya AG feeder which was in Fault. Both were carrying out line patrolling from Pithadiya village to 'hazari group' Ag taping. "Hajari group" tapping is a part of 11kv Pithadiya Ag line but nearby that Ag group, 11kv Juna Vaghaniya Ag Feeder line was existing. During Line Patrolling they found a tilted L Top on HT Pole. So, By assuming that it was Pithadiya Ag, Sh. H B Vaghasiya(LM) took Line clear of 11 KV Pithadiya AG Feeder with LCP No. - 7495 time - 10.30 to repair L Top without verifying Feeder. But actually Feeder was Juna Vaghaniya Ag. After receiving Line Clear of 11 KV Pithadiya Ag, Victim climbed on Pole without shorting and earthing of line & without verifying power ON/OFF. When Victim reached near Top, he came to Induction Zone of live HT Line of Juna Vaghaniya Ag which was in 3 phase at that time. He got electrocuted and fell down. Then, He was hospitalized immediately. No any burn or puncture mark to victim. Health is normal. | CEI report awaited | NA | NA | Warning memo issued to Both Emp. (1) H P Vaghasiya AD-2/HR/ 109 DT 04-07-2022 (2) B B SOLANKI AD2/HR/110 DT 04-07-2022 | 17 | [9 empty] | HAMR2223009120
255 | AMR | SAVARKUNDLA , KADARI SIDIKBHAI ABDDULATIFBHAI | 12.06.22 | NFHOS | As per site visit and statement of eye witness, the victim is rojamdar of savarkundla nagar palika and was climbed on LT LINE pole for street light wire(twin wire ) jumper repairing work and suddenly got electrical shocked and fall down on earth and got injuries on neck and head and hospitalized at Bhavnagar for treatment. During site visit switch of street light was found off and leakage power found in street light wiring. Notice is issued for Nagar palika for carrying out unsafe work on PGVCL line without prior information | CEI report awaited | NA | NA | Faulty Street Light Was Removed From Pole | 18 | [9 empty] | HAMR2223009166
256 | AMR | NAVA KHIJADIYA , BHIKHUBHAI VALLABHBHAI VIRANI | 12.06.22 | FHOS | As Per information received from Sarpanch of village Nava Khijadiya dtd:13.06.2022 and as per site visit, accident occurred near 25 kva Transformer center of Ag consumer No.83267010870,15HP Bhikhubhai Vallabhbhai Virani at Village Nava Khijadiya Ta.Amreli. Said consumer getting power supply from 11 KV Nava Khijadiya Ag feeder. There is no nay eyewitness of this incidence. However information given by neighbour farmer, Victim may be trying to bind D.O. fuse by using Bamboo stick(Which was Wet) and surrounding land area also wet due to rain in early morning. During site visit it is confirmed that surrounding area of Transformer center is wet also wet Bamboo available at said location and Centre D.O. found blown. Due to wet land Victim may be electrocuted during unauthorized D.O. connection work as there were no any complain has been noted at Amreli Rural SDn fault centre office for this connection. There were 3 nos. of tripping recorded between 09:05am to 9:25 am in 11 Kv Nava Khijadiya Ag feeder during 3-phase power supply schedule (08:15 to 16:15) emanating from 66kv Gawadaka Substation. Victim got primary treatment at Amreli Private Hospital and he was referred to Rajkot for further treatment where next day victim was died | Victim may be trying to bind D.O. fuse by using Bamboo stick(Which was Wet) and surrounding land area also wet due to rain in early morning.Due to wet land Victim may be electrocuted during unauthorized D.O. connection work as there were no any complain has been noted at Amreli Rural SDn fault centre office for this connection. There were 3 nos. of tripping recorded between 09:05am to 9:25 am in 11 Kv Nava Khijadiya Ag feeder during 3-phase power supply schedule (08:15 to 16:15) emanating from 66kv Gawadaka Substation. | As per regulation no. 19 if PGVCL victim were not tried to Do repair work unauthorizedly himself than this accident may not occurred. | YES | Connection disconnected and Letter issued to Police Station for FIR AMRL/DE/3007 Dt 26-07-2022 | 19 | 19 | 1185 | 14 | 9 | 22 | 6851 | 20 | 9 | 22 | HAMR2223009167
257 | AMR | RAMPUR , BUFFALO OF DEVRAJBHAI BHIKHABHAI CHAVDA | 13.08.22 | FA | As per site visit & information received it is came to knowledge that land surrounding of 63 kva Transformer Center was wet due to rain. Buffalo might have got electrocuted due to leakage current of Transformer when she was passing nearby that place | CEI report awaited | NA | NA | Reactivation of earthing carried out and maintenance done | 20 | [9 empty] | AAMR2223009347
258 | AMR | DHARI , NO OWNER | 16.06.22 | FA | As per site visit & information received it is came to knowledge that land surrounding of 5 kva Transformer Center having single girdle pole was wet due to rain. Cow got electrocuted due to leakage current of Transformer when she was passing nearby that place. | Cow got electrocuted due to leakage current of Transformer when she was passing nearby that place. | As per regulation no. 12 and 48 if PGVCL done Transformer maintenance at regular intervaland and LT side provided with proper capacity circuit braker than this accident may not occurred. | Yes | Reactivation of earthing carried out and maintenance done | 21 | 12, 48 | 1179 | 14 | 9 | 22 | 6851 | 20 | 9 | 22 | AAMR2223009183
259 | AMR | DANDI , LASHUBEN MADHABHAI BANBHANIYA | 16.07.22 | FHOS | As per primary information received and site visited accident location is on the road of Dandi village to Delwada Saiyad rajpara road due to rain 11KV dandi JGY HT pole no. Dandi Jgy/203 tilted on road and on that psc pole there is FRP V-cross arm and conductor not touch to earth so 11kv dandi jgy feeder was in on condition at that time rickshaw passing through the road accidentally victim (Lashuben Madhabhai Bambhaniya) touch the 11kv wire of Dandi jgy and causes death due to electrocution. As per logbook record of 66 KV Dandi ss a tripping in 11 KV Dandi jgy has been recorded tripped at 4:10, 4:20 AM on Dt16/07/2022 copy of police panchnama and post-mortem report is awaited | CEI report awaited | NA | NA | Safety awareness meeting done | 22 | [9 empty] | HAMR2223009276
260 | AMR | PIPALVA , BUFFALO OF PARESHBHAI MANUBHAI VAGHELA | 16.07.22 | FA | As per information received and site visited a Buffalo was passing under Transformer center DP at the time accidentally came in contact with GI wire and due to leakage current of TC neutral got electrocuted. Surrounding Land area nearby TC center found wet due to previous day rain. | CEI report awaited | NA | NA | Reactivation of earthing carried out and maintenance done | 23 | [9 empty] | AAMR2223009281
261 | AMR | KHADASALI , COW OF MANSUKHBHAI POPATBHAI MAKAVANA | 16.08.22 | FA | As per the eye witness statement and site visited it came to knowledge that at the time of accident light rain was there and all surrounding land was wet. A cow was wondering nearby TC centre and somehow might be electrocuted due to leakage current | CEI report awaited | NA | NA | Reactivation of earthing carried out and maintenance done | 24 | [9 empty] | AAMR2223009358
262 | AMR | AMRELI , COW OF RAMANIKBHAI RANABHAI DHANANI | 17.04.22 | FA | Shri Prabhaben Ramnikbhai Dhanani (Wife of Owner) was going to give water to her cows from nearby through (Aveda), while in way one of cow was rubbing horn to the guy of Transformer Centre. While inspecting guy it found loose and guywire below guy insulator might came in contact with DO Section while cow rubbing horn to guy and cow got electrocuted. Also there’s sparking spot found in guy wire below guy insulator | cow was rubbing horn to the guy of Transformer Centre. While inspecting guy it found loose and guywire below guy insulator might came in contact with DO Section while cow rubbing horn to guy and cow got electrocuted. | As per regulation no. 12 &72 if PGVCL done eathing maintenance at regular interval and maintained guy insulator height at 3 mtr height among guy wire than this accident may not occurred. | YES | Guy removed from Transformer center | 25 | 12, 72 | 1155 | 14 | 9 | 22 | 6851 | 20 | 9 | 22 | AAMR2223009094
263 | AMR | DEVLA , BUFFALO OF KISHORBHAI NAGJIBHAI LATHIYA | 17.07.22 | FA | As per site visit & information received it is came to knowledge that land surrounding of 10 kva Transformer Center was wet due to rain. Buffalo might have got electrocuted due to leakage current of Transformer when passing nearby that place | CEI report awaited | NA | NA | Reactivation of earthing carried out and maintenance done | 26 | [9 empty] | AAMR2223009282
264 | AMR | ALIDAR , COW OF NARANBHAI BOGHABHAI VANSH | 19.07.22 | FA | As per information received and site visited accident location is Agriculture Transformer Center. As per owner's statement when cow passed adjacent to the transformer centre got electrocuted .On site visit it has been observed that land surrounding to TC was highly wet due to rainy water. Cow might be came in contact of earthing GI wire and got electrocuted.PM report is awaited | CEI report awaited | NA | NA | Reactivation of earthing carried out and maintenance done | 27 | [9 empty] | AAMR2223009294
265 | AMR | BODIDHAR , VALA PRATAPBHAI MALABHAI | 21.06.22 | FHOS | As per primary information received and site visited accident location is TC center of Vala Kesurbhai Bhanabhai. At the time of investigation, sparking spots found on transformer’s conservator tank and 11KV Bushing of transformer Center. No any other symptoms found near transformer DP. The Victim might be climbed on transformer DP to repair any fault or some other reason and might be accidentally touched to 11 kv side of Transformer center and might be got electrocuted. No any complaint regarding any fault lodged for this Connection. As per logbook record of 66 KV Bodidar SS a tripping in 11 Kv zanzariya Ag has been recorded tripped at 17.55 pm on DT: 21/06/22. Surrounding area was dry. Copy of Police panchanama and post-mortem Report is awaited | CEI report awaited | NA | NA | Victim himself responsible for accident, Awareness among general public regarding electrical safety "Keep safe distance from Electrical line & Network of PGVCL" during khedut-shibir & village meeting regularly. | 28 | [9 empty] | HAMR2223009190
266 | AMR | ADPOKAR , LEOPARD | 21.08.22 | FA | As per information received and site visited it has came to know that leopard was running and jumped to Kashid tree and at that time accidentally came in contact with live 11 Kv line of 11 Kv Adpokar jgy feeder and got electrocuted. Rokam by forest department has been done | CEI report awaited | NA | NA | New Cable Provided | 29 | [9 empty] | AAMR2223009373
267 | AMR | RAMPARA , COW OF GHANSHYAMBHAI BAGHABHAI VAGH | 21.08.22 | FA | As per owner statement and site visited it came to knowledge that at the time of accident light rain was there and all surrounding land was wet. A cow was wondering nearby TC centre and accidently came in contact with earthing wire. Earthing wire found open and binded with its leg. Hence cow might be electrocuted due to leakage current. | CEI report awaited | NA | NA | Reactivation of earthing carried out and maintenance done | 30 | [9 empty] | AAMR2223009372
268 | AMR | LIKHALA , KISHNBHAI MANUBHAI VAGHELA | 28.04.22 | FHOS | As per site visit and information received from farm owner and victim's brother, victim and his brother were wondering with goat and sheep for their chara. At the accident location HT line passed from neem tree, victim was climbed on neem tree for cutting tree branch for their goat and sheep chara, and incidentally came in contact with live 11 kV likhala ag line and got electrocuted and fatal accident occurred. At the accident location neem tree was exist near HT line, where ground clearance from bottom conductor is 5.9 MTR which is permissible in elsewhere condition. As per statement given by victim's brother not done pm. | At the accident location HT line passed from neem tree, victim was climbed on neem tree for cutting tree branch for their goat and sheep chara, and incidentally came in contact with live 11 kV likhala ag line and got electrocuted and fatal accident occurred. | As per regulation no. 12 & 19 if PGVCL had done tree branch cutting to maintain safe clearance of line cundoctor and If victim had maintained safe distance from live line conductor during tree branch treeming work than this accident may not occurred. | YES | Necessary maintenance and Tree branch trimming work carried out | 31 | 12, 19 | 1061 | 18 | 8 | 22 | 6217 | 25 | 8 | 22 | HAMR2223009115
269 | AMR | LILIYA,COW OF TUSHARBHAI CHOTHABHAI RATHOD | 10.09.22 | FA | As per site visited, circuit cable of TC center found damaged and in contact with metal Distribution box and cow accidentally came in contact with this metal DB box and got electrocuted. | CEI report awaited | NA | NA | New Circuit Cable provided | 32
270 | AMR | VAVDI,ALPESHBHAI RAVJIBHAI POLARA | 12.09.22 | FHOS | As Per information received from Parsotambhai of village Vavdi and site visited accident location is 63 kva Transformer center for group connection at Village Vavdi Ta.Babra getting power supply from 11 kV Vasuki Ag feeder. There was no any eyewitness of incidence however as per information of Nearby farmer, Victim might be trying to repair lug of LT side stud of TC by unauthorised climbing on TC during 3PH power supply schedule without taking any precaution of safety during work. Transformer centre’s it side lug is found broken. Victim might be electrocuted during unauthorized lug connection repair work as there were no any other linkage current or network abnormalities found nearby accident location. Also no any complain has been noted at Babra Rural SDN fault centre for this Ag group. 1 nos.trippings has been recorded between 12:00 pm to 12:05 pm in 11 KV Vasuki Ag feeder during 3-phase power supply schedule (05:30 to 13:30) emanating from 66kv Kuvargadh Substation. Victim got primary treatment at Babra Government hospital and he was referred to Rajkot for further treatmen | CEI report awaited | NA | NA | Provided New Jumper with Binding. Awareness among general public regarding electrical safety "Keep safe distance from Electrical line & Network of PGVCL" during khedut-shibir & village meeting regularly. | 33
271 | AMR | KESARIYA,COW OF CHINABHAI PUNABHAI CHAUHAN | 17.09.22 | FA | As per primary information received and site visited accident location is 11 KV Tad AG feeder. Return 11 Kv conductor of tad ag feeder was found broken at site and no any tripping recorded in feeder. Calf was passing through that broken conductor and surrounding area was also found wet as it was rain. Thus calf was came in contact and got electrocuted. | CEI report awaited | NA | NA | Re-Joint of conductor | 34
272 | AMR | HEMAL,BUFFALO OF RANABHAI SURABHAI SINDHAV | 19.09.22 | FA | As per owner statement and site visited it came to knowledge that at the time of accident light rain was their last night and all surrounding land was wet. Earthing wire found provided with PVC rigid pipe. A buffalo was wondering nearby TC centre and might be electrocuted due to leakage current on wet surface nearby TC | CEI report awaited | NA | NA | Reactivation of earthing carried out and maintenance done | 35
273 | SNR | SAYLA , Cow of Gopalbhai Selabhai Sabhad | 05.08.22 | FA | Due to heavy rain and wind at village sayla nr. Sudamada darvaja eye hospital there was water logging surrounding LT Pole, more over due to heavy wind open multiple twin junction on the pole vibrant and touched to the steel structure pole, hence leakage current flow through pole to ground, anyhow cow passing near to this pole accidentally touch to pole and electrocuted, and met to death | CEI report awaited | NA | NA | Earthing reactivated and proper maintenance carried out. Awareness among general public regarding electrical safety "Do not grazing their animals near the pole/ TC center" during khedut-shibir & village meeting regularly. | 1 | [9 empty] | ASNR2223009326
274 | SNR | Kharaghoda , Cow of Velabhai jesingbhai khatana | 10.07.22 | FA | One of lighting connection service wire was given through 6 mm2 pvc cable dropper on lt girder pole. Service wire insulation was got damaged and due to heavy wind pressure and rain, came in contact with girder pole and hence due to this leakage current was passing through girder pole. At that time one Cow was passing nearby it and came in contact with LT girder pole and got electrocuted and died | CEI report awaited | NA | NA | Service wire replaced and proper maintenance carried out. Awareness among general public regarding electrical safety "Do not grazing their animals near the pole/ TC center" during khedut-shibir & village meeting regularly. | 2 | [9 empty] | ASNR2223009257
275 | SNR | MINAPUR , Dhadvi Labhubhai Thakarshibhai | 11.05.22 | FHOS | As per information received from divyabhaskar on date 12.05.2022. As per site visit, the victim had constructed his house just 1 feet near to the existing line and now he was constructing first floor. while arranging iron rod on the terrace of the house, unknowingly he extended iron rod outside the terrace and toward the HT line, an Iron rode came in the induction of live conductor of 11 KV minapur AG feeder and victim got electrocuted and died. The vertical height of the line from ground is 17 feet. There is no tripping registered in the line | Victim Himself is responsible for this accident. | NO | NA | Awareness among general public regarding electrical safety "Keep safe distance from Electrical line & Network of PGVCL" during khedut-shibir & village meeting regularly. | 3 | 64 | 1070 | 18 | 8 | 22 | 6220 | 25 | 8 | 22 | HSNR2223009121
276 | SNR | Dhikvali , Buffalo of Jodhabhai Somabhai Sambhad | 11.07.22 | FA | As per site visit and primary investigation it is found that during rain as buffalo of shri. Jodhabhai Somabhai Sambhad passing through nearby area of Dudh Utpadak Mandali Connection TC Center at Dhinkvadi Village. Due to heavy rain surrounding area of TC Center water logging and at the time of Buffalo was passing nearby TC Center and touched with neutral earthing of TC center which was not covered by rigid PVC pipe and due to leakage neutral current flows buffalo got electrocuted and Died. | CEI report awaited | NA | NA | Transformer Earthing reactivated and proper maintenance carried out. Awareness among general public regarding electrical safety "Do not grazing their animals near the pole/ TC center" during khedut-shibir & village meeting regularly. | 4 | [9 empty] | ASNR2223009261
277 | SNR | SAYLA , Buffalo of Bhadka Raghubhai Gandabhai | 15.06.22 | FA | as per site visit and primary investigation due to rain and wind at village sayla momentary leakage current passed through LT girder pole of urban feeder. At that time buffalo came in contact with girder pole and electrocuted | CEI report awaited | NA | NA | Pole Earthing reactivated and proper maintenance carried out. Awareness among general public regarding electrical safety "Do not grazing their animals near the pole/ TC center" during khedut-shibir & village meeting regularly. | 5 | [9 empty] | ASNR2223009177
278 | SNR | THAN , Buffalo of Karshanbhai Merabhai | 17.05.22 | FA | As per site visit & information given by owner shri karshanbhai , it is came to knowledge that Buffalo was rubbing at TC pole, due to this guy wire may came in induction zone of nearby D.O fuse and return power may pass through earthing wire and Buffalo came in contact with it and got electrocuted | CEI report awaited | NA | NA | New guy properly installed & Transformer Earthing reactivated and proper maintenance carried out. Awareness among general public regarding electrical safety "Do not grazing their animals near the pole/ TC center" during khedut-shibir & village meeting regularly. | 6 | [9 empty] | ASNR2223009125
279 | SNR | LIMBDI , Cow of Haribhai Bhalabhai Jograna | 19.06.22 | FA | As per site visit and primary investigation due to heavy wind 4 LT Pole were broken and LT wire are laying on ground and feeder was live at that time cow came in contact with LT wire laying on ground and electrocuted. | CEI report awaited | NA | NA | 04 New LT pole erected & proper LT line maintenance carried out. Awareness among general public regarding electrical safety "Do not grazing their animals near the pole/ TC center" during khedut-shibir & village meeting regularly. | 7 | [9 empty] | ASNR2223009187
280 | SNR | LIMBDI , Cow of Haribhai Bhalabhai Jograna | 19.06.22 | FA | As per site visit and primary investigation due to heavy wind 4 LT Pole were broken and LT wire are laying on ground and feeder was live at that time cow came in contact with LT wire laying on ground and electrocuted. | CEI report awaited | NA | NA | 04 New LT pole erected & proper LT line maintenance carried out. Awareness among general public regarding electrical safety "Do not grazing their animals near the pole/ TC center" during khedut-shibir & village meeting regularly. | 8 | [9 empty] | ASNR2223009187
281 | SNR | LIMBDI , Cow of Haribhai Bhalabhai Jograna | 19.06.22 | FA | As per site visit and primary investigation due to heavy wind 4 LT Pole were broken and LT wire are laying on ground and feeder was live at that time cow came in contact with LT wire laying on ground and electrocuted. | CEI report awaited | NA | NA | 04 New LT pole erected & proper LT line maintenance carried out. Awareness among general public regarding electrical safety "Do not grazing their animals near the pole/ TC center" during khedut-shibir & village meeting regularly. | 9 | [9 empty] | ASNR2223009187
282 | SNR | LIMBDI , Cow of Haribhai Bhalabhai Jograna | 19.06.22 | FA | As per site visit and primary investigation due to heavy wind 4 LT Pole were broken and LT wire are laying on ground and feeder was live at that time cow came in contact with LT wire laying on ground and electrocuted. | CEI report awaited | NA | NA | 04 New LT pole erected & proper LT line maintenance carried out. Awareness among general public regarding electrical safety "Do not grazing their animals near the pole/ TC center" during khedut-shibir & village meeting regularly. | 10 | [9 empty] | ASNR2223009187
283 | SNR | LIMBDI , Rahulbhai Chhaganbhai Mariya | 24.07.22 | FHOS | As per site visit, and primary investigation it is primarily established that the victim late shri rahulbhai chhaganbhai Mariya was a truck driver. Being a truck driver he was carrying material in his truck (GJ-14-T-4388) and had parked the truck exactly beneath the overhead 11 KV line of Limbdi City Urban Feeder. While laying Plastic carpolin on the upper surface of the truck with the help of rope, accidentally the wet rope (Due to rain rope was wet) and victim came in contact with the live induction zone of the overhead 11 KV line of Limbdi City Urban feeder and he was electrocuted and met with Fatal Electrical Accident. Later on he was taken to Limbdi Civil Hospital where he was declared dead. The vertical ground clearance of the 11 KV line wire is as per norms and appx. 6.1 meter from the ground. The victim himself dangerously parked his truck under the live 11 KV line and accidently met with electrical Accident. The prima fascia evidence suggests that victim himself is responsible for the above Accident and nowhere PGVCL employees and system responsible for the above accident. No tripping in this feeder observed. | CEI report awaited | NA | NA | Awareness among general public regarding electrical safety "Keep safe distance from Electrical line & Network of PGVCL" during khedut-shibir & village meeting regularly. | 11 | [9 empty] | HSNR2223009301
284 | SNR | Nani Moldi , Buffalo of Rudabhai Devayatbhai Khatana | 30.07.22 | FA | A fatal animal accident occurred due to buffalo rubbing its head with a transformer pole and near the transformer center surrounding area water logging due to monsoon season. At the time of the buffalo rubbing the transformer pole, at that time it might be possible that momentary leakage current passed through GI earth wire, and buffalo passed near the TC structure and due to step potential generate buffalo got shocked and died. | CEI report awaited | NA | NA | Transformer Earthing reactivated and proper maintenance carried out. Awareness among general public regarding electrical safety "Do not grazing their animals near the pole/ TC center" during khedut-shibir & village meeting regularly. | 12 | [9 empty] | ASNR2223009311
285 | SNR | Bhechada, Buffalo of Nathabhai Valabhai Aal | 12.09.22 | FA | In 11KV Pavan AG feeder at location number NRC/PVN/98, 11KV Disc insulator was got fired and conductor was departed from Disc hardware and came in contact with Tapping angle and due to rainy season leakage current was passing through tapping angle to the earthing wire, at that time the Buffalos were passing near this pole and came in contact with live earthing wire and hence got electrocuted and died | CEI report awaited | NA | NA | New Disc insulator installed & Pole Earthing reactivated and proper maintenance carried out. Awareness among general public regarding electrical safety "Do not grazing their animals near the pole/ TC center" during khedut-shibir & village meeting regularly. | 13
286 | SNR | Bhechada, Buffalo of Nathabhai Valabhai Aal | 12.09.22 | FA | In 11KV Pavan AG feeder at location number NRC/PVN/98, 11KV Disc insulator was got fired and conductor was departed from Disc hardware and came in contact with Tapping angle and due to rainy season leakage current was passing through tapping angle to the earthing wire, at that time the Buffalos were passing near this pole and came in contact with live earthing wire and hence got electrocuted and died | CEI report awaited | NA | NA | New Disc insulator installed & Pole Earthing reactivated and proper maintenance carried out. Awareness among general public regarding electrical safety "Do not grazing their animals near the pole/ TC center" during khedut-shibir & village meeting regularly. | 14
287 | SNR | Bhechada, Buffalo of Jivabhai Valabhai Aal | 12.09.22 | FA | In 11KV Pavan AG feeder at location number NRC/PVN/98, 11KV Disc insulator was got fired and conductor was departed from Disc hardware and came in contact with Tapping angle and due to rainy season leakage current was passing through tapping angle to the earthing wire, at that time the Buffalos were passing near this pole and came in contact with live earthing wire and hence got electrocuted and died | CEI report awaited | NA | NA | New Disc insulator installed & Pole Earthing reactivated and proper maintenance carried out. Awareness among general public regarding electrical safety "Do not grazing their animals near the pole/ TC center" during khedut-shibir & village meeting regularly. | 15
288 | SNR | Bhechada, Buffalo of Narendrasinh Manubha Zala | 12.09.22 | FA | In 11KV Pavan AG feeder at location number NRC/PVN/98, 11KV Disc insulator was got fired and conductor was departed from Disc hardware and came in contact with Tapping angle and due to rainy season leakage current was passing through tapping angle to the earthing wire, at that time the Buffalos were passing near this pole and came in contact with live earthing wire and hence got electrocuted and died | CEI report awaited | NA | NA | New Disc insulator installed & Pole Earthing reactivated and proper maintenance carried out. Awareness among general public regarding electrical safety "Do not grazing their animals near the pole/ TC center" during khedut-shibir & village meeting regularly. | 16
289 | SNR | Rajpar, Cow of Santubhai Dhanjibhai Aal | 03.09.22 | FA | As per information received from Owner of COW at 07:00 Am on date 02.09.2022, The cow passes in free area of their owners premises and the 11 KV Line of Katuda JGY passing near this place and the pole having number WAD/KAT/JGY/179 was inclined due to heavy pressure of water came from the drainage line nearer to that pole and heavy water logging area. Due to tension of overhead conductor the pole goes fall down on cow passing nearer the pole and due to that the body of came in contact with the live conductor of pole and cow got electrocuted and death | CEI report awaited | NA | NA | New pole erected & proper line maintenance carried out. Awareness among general public regarding electrical safety "Do not grazing their animals near the pole/ TC center" during khedut-shibir & village meeting regularly. | 17

## 3B
Performa SoP 003 B: APPENDIX-B (already in the SoP regulation)
REGISTER FOR COMPILING THE COMPLAINTS CLASSIFICATIONWISE
Name of Area / Circle | Classification |  | Pending complaints of previous Qtr | Complaints received during the Qtr | Total Complaints | No. of Complaints redressed during the Qtr |  |  |  |  | Balance Complaints to be redressed (5) – (10)
[6 empty] | In stipulated time |  | Beyond stipulated time |  | Total (6) to (9)
[6 empty] | Within 50% of stipulated time. | Within stipulated time. | Up to double the stipulated time | More than double the stipulated time
1 | 2 |  | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11
RJC | A(i) | Loose connections from pole | 0 | 15318 | 15318 | 8711 | 6607 | 0 | 0 | 15318 | 0
| A(ii) | Interruption due to line breakdown | 0 | 6306 | 6306 | 1416 | 4890 | 0 | 0 | 6306 | 0
| A(iii) | Interruption due to failure of transformer | 0 | 1449 | 1449 | 265 | 1184 | 0 | 0 | 1449 | 0
| B(i) | Ordinary case, which requires no augmentation. | 0 | 181 | 181 | 55 | 126 | 0 | 0 | 181 | 0
| B(ii) | Where augmentation is required. | 0 | 177 | 177 | 30 | 147 | 0 | 0 | 177 | 0
| C(i) | Stopped/Defective Meters | 0 | 1615 | 1615 | 422 | 1193 | 0 | 0 | 1615 | 0
| C(ii) | Billing on average basis for more than two bills | 0 | 1231 | 1231 | 346 | 885 | 0 | 0 | 1231 | 0
| D(i) | Loose Wires | 0 | 950 | 950 | 298 | 652 | 0 | 0 | 950 | 0
| D(ii) | Inadequate ground clearance | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| E(i) | For current bills where no additional information is required | 0 | 476 | 476 | 112 | 364 | 0 | 0 | 476 | 0
| E(ii) | Where additional information relating to correctness of reading etc. is required | 0 | 580 | 580 | 71 | 509 | 0 | 0 | 580 | 0
| F(i) | Where extension of mains is not required | 0 | 346 | 346 | 76 | 270 | 0 | 0 | 346 | 0
| F(ii) | Where extension of mains is required | 0 | 281 | 281 | 59 | 222 | 0 | 0 | 281 | 0
| F(iii) | Modification in connected load | 0 | 1098 | 1098 | 200 | 898 | 0 | 0 | 1098 | 0
| F(iv) | Name change/reconnection | 0 | 2253 | 2253 | 567 | 1686 | 0 | 0 | 2253 | 0
| G | Refund of amount due in regard to temporary connection | 0 | 334 | 334 | 31 | 303 | 0 | 0 | 334 | 0
| H | Others | 0 | 399 | 399 | 78 | 321 | 0 | 0 | 399 | 0
RJR | A(i) | Loose connections from pole | 2 | 3968 | 3970 | 3088 | 880 | 0 | 0 | 3968 | 2
| A(ii) | Interruption due to line breakdown | 1 | 7174 | 7175 | 4972 | 2202 | 0 | 0 | 7174 | 1
| A(iii) | Interruption due to failure of transformer | 2 | 5202 | 5204 | 3669 | 1533 | 0 | 0 | 5202 | 2
| B(i) | Ordinary case, which requires no augmentation. | 0 | 917 | 917 | 637 | 280 | 0 | 0 | 917 | 0
| B(ii) | Where augmentation is required. | 1 | 329 | 330 | 310 | 19 | 0 | 0 | 329 | 1
| C(i) | Stopped/Defective Meters | 0 | 2816 | 2816 | 1913 | 903 | 0 | 0 | 2816 | 0
| C(ii) | Billing on average basis for more than two bills | 0 | 354 | 354 | 274 | 80 | 0 | 0 | 354 | 0
| D(i) | Loose Wires | 1 | 3987 | 3988 | 2651 | 1336 | 0 | 0 | 3987 | 1
| D(ii) | Inadequate ground clearance | 0 | 513 | 513 | 384 | 129 | 0 | 0 | 513 | 0
| E(i) | For current bills where no additional information is required | 0 | 710 | 710 | 501 | 209 | 0 | 0 | 710 | 0
| E(ii) | Where additional information relating to correctness of reading etc. is required | 1 | 359 | 360 | 324 | 35 | 0 | 0 | 359 | 1
| F(i) | Where extension of mains is not required | 0 | 1728 | 1728 | 1088 | 640 | 0 | 0 | 1728 | 0
| F(ii) | Where extension of mains is required | 0 | 278 | 278 | 246 | 32 | 0 | 0 | 278 | 0
| F(iii) | Modification in connected load | 0 | 626 | 626 | 455 | 171 | 0 | 0 | 626 | 0
| F(iv) | Name change/reconnection | 1 | 834 | 835 | 605 | 229 | 0 | 0 | 834 | 1
| G | Refund of amount due in regard to temporary connection | 0 | 389 | 389 | 309 | 80 | 0 | 0 | 389 | 0
| H | Others | 247 | 10143 | 10390 | 6374 | 3769 | 0 | 0 | 10143 | 247
MRB | A(i) | Loose connections from pole | 0 | 9829 | 9829 | 6655 | 3174 | 0 | 0 | 9829 | 0
| A(ii) | Interruption due to line breakdown | 0 | 18219 | 18219 | 7326 | 10893 | 0 | 0 | 18219 | 0
| A(iii) | Interruption due to failure of transformer | 0 | 1154 | 1154 | 636 | 518 | 0 | 0 | 1154 | 0
| B(i) | Ordinary case, which requires no augmentation. | 0 | 51 | 51 | 21 | 30 | 0 | 0 | 51 | 0
| B(ii) | Where augmentation is required. | 0 | 99 | 99 | 39 | 60 | 0 | 0 | 99 | 0
| C(i) | Stopped/Defective Meters | 0 | 5183 | 5183 | 1704 | 3479 | 0 | 0 | 5183 | 0
| C(ii) | Billing on average basis for more than two bills | 0 | 598 | 598 | 312 | 286 | 0 | 0 | 598 | 0
| D(i) | Loose Wires | 0 | 1555 | 1555 | 561 | 994 | 0 | 0 | 1555 | 0
| D(ii) | Inadequate ground clearance | 0 | 7 | 7 | 5 | 2 | 0 | 0 | 7 | 0
| E(i) | For current bills where no additional information is required | 0 | 1838 | 1838 | 1051 | 787 | 0 | 0 | 1838 | 0
| E(ii) | Where additional information relating to correctness of reading etc. is required | 0 | 988 | 988 | 506 | 482 | 0 | 0 | 988 | 0
| F(i) | Where extension of mains is not required | 0 | 151 | 151 | 84 | 67 | 0 | 0 | 151 | 0
| F(ii) | Where extension of mains is required | 0 | 326 | 326 | 114 | 212 | 0 | 0 | 326 | 0
| F(iii) | Modification in connected load | 0 | 312 | 312 | 137 | 175 | 0 | 0 | 312 | 0
| F(iv) | Name change/reconnection | 0 | 1480 | 1480 | 538 | 942 | 0 | 0 | 1480 | 0
| G | Refund of amount due in regard to temporary connection | 0 | 18 | 18 | 14 | 4 | 0 | 0 | 18 | 0
| H | Others | 0 | 2908 | 2908 | 1144 | 1764 | 0 | 0 | 2908 | 0
PBR | A(i) | Loose connections from pole | 0 | 6509 | 6509 | 2759 | 3750 | 0 | 0 | 6509 | 0
| A(ii) | Interruption due to line breakdown | 0 | 16474 | 16474 | 6712 | 9762 | 0 | 0 | 16474 | 0
| A(iii) | Interruption due to failure of transformer | 0 | 1217 | 1217 | 510 | 707 | 0 | 0 | 1217 | 0
| B(i) | Ordinary case, which requires no augmentation. | 0 | 86 | 86 | 46 | 40 | 0 | 0 | 86 | 0
| B(ii) | Where augmentation is required. | 0 | 16 | 16 | 7 | 9 | 0 | 0 | 16 | 0
| C(i) | Stopped/Defective Meters | 0 | 1657 | 1657 | 507 | 1150 | 0 | 0 | 1657 | 0
| C(ii) | Billing on average basis for more than two bills | 0 | 161 | 161 | 38 | 123 | 0 | 0 | 161 | 0
| D(i) | Loose Wires | 0 | 1023 | 1023 | 82 | 941 | 0 | 0 | 1023 | 0
| D(ii) | Inadequate ground clearance | 0 | 10 | 10 | 0 | 10 | 0 | 0 | 10 | 0
| E(i) | For current bills where no additional information is required | 0 | 41 | 41 | 13 | 28 | 0 | 0 | 41 | 0
| E(ii) | Where additional information relating to correctness of reading etc. is required | 0 | 87 | 87 | 19 | 68 | 0 | 0 | 87 | 0
| F(i) | Where extension of mains is not required | 0 | 40 | 40 | 21 | 19 | 0 | 0 | 40 | 0
| F(ii) | Where extension of mains is required | 0 | 10 | 10 | 2 | 8 | 0 | 0 | 10 | 0
| F(iii) | Modification in connected load | 0 | 69 | 69 | 8 | 61 | 0 | 0 | 69 | 0
| F(iv) | Name change/reconnection | 0 | 36 | 36 | 15 | 21 | 0 | 0 | 36 | 0
| G | Refund of amount due in regard to temporary connection | 0 | 128 | 128 | 27 | 101 | 0 | 0 | 128 | 0
| H | Others | 0 | 174 | 174 | 37 | 137 | 0 | 0 | 174 | 0
JMN | A(i) | Loose connections from pole | 71 | 10761 | 10832 | 4368 | 6440 | 0 | 0 | 10808 | 24
| A(ii) | Interruption due to line breakdown | 40 | 4826 | 4866 | 3453 | 1401 | 0 | 0 | 4854 | 12
| A(iii) | Interruption due to failure of transformer | 73 | 4525 | 4598 | 1415 | 2720 | 419 | 0 | 4554 | 44
| B(i) | Ordinary case, which requires no augmentation. | 28 | 1026 | 1054 | 275 | 753 | 4 | 0 | 1032 | 22
| B(ii) | Where augmentation is required. | 8 | 444 | 452 | 2 | 442 | 2 | 0 | 446 | 6
| C(i) | Stopped/Defective Meters | 47 | 3866 | 3913 | 1989 | 1904 | 0 | 0 | 3893 | 20
| C(ii) | Billing on average basis for more than two bills | 27 | 231 | 258 | 154 | 82 | 0 | 0 | 236 | 22
| D(i) | Loose Wires | 51 | 3492 | 3543 | 2359 | 1158 | 0 | 0 | 3517 | 26
| D(ii) | Inadequate ground clearance | 3 | 655 | 658 | 111 | 546 | 0 | 0 | 657 | 1
| E(i) | For current bills where no additional information is required | 5 | 295 | 300 | 169 | 127 | 0 | 0 | 296 | 4
| E(ii) | Where additional information relating to correctness of reading etc. is required | 13 | 8 | 21 | 2 | 3 | 0 | 0 | 5 | 16
| F(i) | Where extension of mains is not required | 7 | 88 | 95 | 43 | 45 | 0 | 0 | 88 | 7
| F(ii) | Where extension of mains is required | 2 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 2
| F(iii) | Modification in connected load | 23 | 276 | 299 | 100 | 176 | 0 | 0 | 276 | 23
| F(iv) | Name change/reconnection | 27 | 1386 | 1413 | 318 | 1078 | 0 | 0 | 1396 | 17
| G | Refund of amount due in regard to temporary connection | 16 | 907 | 923 | 164 | 740 | 0 | 0 | 904 | 19
| H | Others | 11 | 3175 | 3186 | 1073 | 2099 | 11 | 0 | 3183 | 3
BHJ | A(i) | Loose connections from pole | 0 | 4415 | 4415 | 4415 | 0 | 0 | 0 | 4415 | 0
| A(ii) | Interruption due to line breakdown | 0 | 7271 | 7271 | 7271 | 0 | 0 | 0 | 7271 | 0
| A(iii) | Interruption due to failure of transformer | 0 | 1073 | 1073 | 1073 | 0 | 0 | 0 | 1073 | 0
| B(i) | Ordinary case, which requires no augmentation. | 0 | 1052 | 1052 | 1052 | 0 | 0 | 0 | 1052 | 0
| B(ii) | Where augmentation is required. | 0 | 390 | 390 | 390 | 0 | 0 | 0 | 390 | 0
| C(i) | Stopped/Defective Meters | 0 | 952 | 952 | 952 | 0 | 0 | 0 | 952 | 0
| C(ii) | Billing on average basis for more than two bills | 0 | 1017 | 1017 | 1017 | 0 | 0 | 0 | 1017 | 0
| D(i) | Loose Wires | 0 | 376 | 376 | 376 | 0 | 0 | 0 | 376 | 0
| D(ii) | Inadequate ground clearance | 0 | 101 | 101 | 101 | 0 | 0 | 0 | 101 | 0
| E(i) | For current bills where no additional information is required | 0 | 1243 | 1243 | 1243 | 0 | 0 | 0 | 1243 | 0
| E(ii) | Where additional information relating to correctness of reading etc. is required | 0 | 845 | 845 | 845 | 0 | 0 | 0 | 845 | 0
| F(i) | Where extension of mains is not required | 0 | 200 | 200 | 200 | 0 | 0 | 0 | 200 | 0
| F(ii) | Where extension of mains is required | 0 | 72 | 72 | 72 | 0 | 0 | 0 | 72 | 0
| F(iii) | Modification in connected load | 0 | 430 | 430 | 430 | 0 | 0 | 0 | 430 | 0
| F(iv) | Name change/reconnection | 0 | 867 | 867 | 867 | 0 | 0 | 0 | 867 | 0
| G | Refund of amount due in regard to temporary connection | 0 | 133 | 133 | 133 | 0 | 0 | 0 | 133 | 0
| H | Others | 0 | 2182 | 2182 | 2182 | 0 | 0 | 0 | 2182 | 0
ANJAR | A(i) | Loose connections from pole | 0 | 2240 | 2240 | 1211 | 1029 | 0 | 0 | 2240 | 0 | 0
| A(ii) | Interruption due to line breakdown | 0 | 1783 | 1783 | 1226 | 557 | 0 | 0 | 1783 | 0 | 0
| A(iii) | Interruption due to failure of transformer | 0 | 1178 | 1178 | 772 | 406 | 0 | 0 | 1178 | 0 | 3
| B(i) | Ordinary case, which requires no augmentation. | 0 | 152 | 152 | 124 | 28 | 0 | 0 | 152 | 0 | 0
| B(ii) | Where augmentation is required. | 0 | 155 | 155 | 123 | 32 | 0 | 0 | 155 | 0 | 0
| C(i) | Stopped/Defective Meters | 0 | 961 | 961 | 509 | 452 | 0 | 0 | 961 | 0 | 0
| C(ii) | Billing on average basis for more than two bills | 0 | 778 | 778 | 545 | 233 | 0 | 0 | 778 | 0 | 8
| D(i) | Loose Wires | 0 | 926 | 926 | 655 | 271 | 0 | 0 | 926 | 0 | 0
| D(ii) | Inadequate ground clearance | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| E(i) | For current bills where no additional information is required | 0 | 629 | 629 | 341 | 288 | 0 | 0 | 629 | 0 | 0
| E(ii) | Where additional information relating to correctness of reading etc. is required | 0 | 573 | 573 | 357 | 216 | 0 | 0 | 573 | 0 | 0
| F(i) | Where extension of mains is not required | 0 | 178 | 178 | 122 | 56 | 0 | 0 | 178 | 0 | 1
| F(ii) | Where extension of mains is required | 0 | 26 | 26 | 20 | 6 | 0 | 0 | 26 | 0 | 0
| F(iii) | Modification in connected load | 0 | 505 | 505 | 419 | 86 | 0 | 0 | 505 | 0 | 0
| F(iv) | Name change/reconnection | 0 | 529 | 529 | 414 | 115 | 0 | 0 | 529 | 0 | 6
| G | Refund of amount due in regard to temporary connection | 0 | 112 | 112 | 98 | 14 | 0 | 0 | 112 | 0 | 0
| H | Others | 0 | 3003 | 3003 | 1007 | 1996 | 0 | 0 | 3003 | 0 | 6
JND | A(i) | Loose connections from pole | 0 | 15211 | 15211 | 10164 | 5047 | 0 | 0 | 15211 | 0
| A(ii) | Interruption due to line breakdown | 0 | 7283 | 7283 | 4460 | 2823 | 0 | 0 | 7283 | 0
| A(iii) | Interruption due to failure of transformer | 0 | 3646 | 3646 | 2332 | 1314 | 0 | 0 | 3646 | 0
| B(i) | Ordinary case, which requires no augmentation. | 0 | 114 | 114 | 79 | 35 | 0 | 0 | 114 | 0
| B(ii) | Where augmentation is required. | 0 | 58 | 58 | 53 | 5 | 0 | 0 | 58 | 0
| C(i) | Stopped/Defective Meters | 0 | 437 | 437 | 303 | 134 | 0 | 0 | 437 | 0
| C(ii) | Billing on average basis for more than two bills | 0 | 170 | 170 | 114 | 56 | 0 | 0 | 170 | 0
| D(i) | Loose Wires | 0 | 206 | 206 | 134 | 72 | 0 | 0 | 206 | 0
| D(ii) | Inadequate ground clearance | 0 | 55 | 55 | 51 | 4 | 0 | 0 | 55 | 0
| E(i) | For current bills where no additional information is required | 0 | 55 | 55 | 53 | 2 | 0 | 0 | 55 | 0
| E(ii) | Where additional information relating to correctness of reading etc. is required | 0 | 53 | 53 | 53 | 0 | 0 | 0 | 53 | 0
| F(i) | Where extension of mains is not required | 0 | 47 | 47 | 45 | 2 | 0 | 0 | 47 | 0
| F(ii) | Where extension of mains is required | 0 | 41 | 41 | 39 | 2 | 0 | 0 | 41 | 0
| F(iii) | Modification in connected load | 0 | 96 | 96 | 80 | 16 | 0 | 0 | 96 | 0
| F(iv) | Name change/reconnection | 0 | 96 | 96 | 75 | 21 | 0 | 0 | 96 | 0
| G | Refund of amount due in regard to temporary connection | 0 | 52 | 52 | 46 | 6 | 0 | 0 | 52 | 0
| H | Others | 0 | 32 | 32 | 31 | 1 | 0 | 0 | 32 | 0
BVN | A(i) | Loose connections from pole | 0 | 14832 | 14832 | 11282 | 3550 | 0 | 0 | 14832 | 0
| A(ii) | Interruption due to line breakdown | 0 | 3933 | 3933 | 2464 | 1425 | 44 | 0 | 3933 | 0
| A(iii) | Interruption due to failure of transformer | 0 | 1226 | 1226 | 739 | 487 | 0 | 0 | 1226 | 0
| B(i) | Ordinary case, which requires no augmentation. | 0 | 102 | 102 | 57 | 45 | 0 | 0 | 102 | 0
| B(ii) | Where augmentation is required. | 0 | 139 | 139 | 98 | 41 | 0 | 0 | 139 | 0
| C(i) | Stopped/Defective Meters | 0 | 3287 | 3287 | 2183 | 1104 | 0 | 0 | 3287 | 0
| C(ii) | Billing on average basis for more than two bills | 0 | 1677 | 1677 | 1138 | 539 | 0 | 0 | 1677 | 0
| D(i) | Loose Wires | 0 | 794 | 794 | 481 | 313 | 0 | 0 | 794 | 0
| D(ii) | Inadequate ground clearance | 0 | 294 | 294 | 195 | 99 | 0 | 0 | 294 | 0
| E(i) | For current bills where no additional information is required | 0 | 42 | 42 | 24 | 18 | 0 | 0 | 42 | 0
| E(ii) | Where additional information relating to correctness of reading etc. is required | 0 | 1945 | 1945 | 1308 | 637 | 0 | 0 | 1945 | 0
| F(i) | Where extension of mains is not required | 0 | 663 | 663 | 508 | 155 | 0 | 0 | 663 | 0
| F(ii) | Where extension of mains is required | 0 | 109 | 109 | 56 | 53 | 0 | 0 | 109 | 0
| F(iii) | Modification in connected load | 0 | 654 | 654 | 454 | 200 | 0 | 0 | 654 | 0
| F(iv) | Name change/reconnection | 0 | 3595 | 3595 | 2672 | 923 | 0 | 0 | 3595 | 0
| G | Refund of amount due in regard to temporary connection | 0 | 215 | 215 | 146 | 69 | 0 | 0 | 215 | 0
| H | Others | 0 | 1321 | 1321 | 725 | 596 | 0 | 0 | 1321 | 0
BTD | A(i) | Loose connections from pole | 0 | 4631 | 4631 | 3740 | 891 | 0 | 0 | 4631 | 0
| A(ii) | Interruption due to line breakdown | 0 | 967 | 967 | 671 | 296 | 0 | 0 | 967 | 0
| A(iii) | Interruption due to failure of transformer | 0 | 699 | 699 | 458 | 241 | 0 | 0 | 699 | 0
| B(i) | Ordinary case, which requires no augmentation. | 0 | 3 | 3 | 3 | 0 | 0 | 0 | 3 | 0
| B(ii) | Where augmentation is required. | 0 | 4 | 4 | 4 | 0 | 0 | 0 | 4 | 0
| C(i) | Stopped/Defective Meters | 0 | 1183 | 1183 | 767 | 416 | 0 | 0 | 1183 | 0
| C(ii) | Billing on average basis for more than two bills | 0 | 190 | 190 | 159 | 31 | 0 | 0 | 190 | 0
| D(i) | Loose Wires | 0 | 154 | 154 | 117 | 37 | 0 | 0 | 154 | 0
| D(ii) | Inadequate ground clearance | 0 | 23 | 23 | 19 | 4 | 0 | 0 | 23 | 0
| E(i) | For current bills where no additional information is required | 0 | 13 | 13 | 12 | 1 | 0 | 0 | 13 | 0
| E(ii) | Where additional information relating to correctness of reading etc. is required | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| F(i) | Where extension of mains is not required | 0 | 3 | 3 | 2 | 1 | 0 | 0 | 3 | 0
| F(ii) | Where extension of mains is required | 0 | 8 | 8 | 5 | 3 | 0 | 0 | 8 | 0
| F(iii) | Modification in connected load | 0 | 245 | 245 | 193 | 52 | 0 | 0 | 245 | 0
| F(iv) | Name change/reconnection | 0 | 37 | 37 | 19 | 18 | 0 | 0 | 37 | 0
| G | Refund of amount due in regard to temporary connection | 0 | 10 | 10 | 7 | 3 | 0 | 0 | 10 | 0
| H | Others | 0 | 58 | 58 | 41 | 17 | 0 | 0 | 58 | 0
AMR | A(i) | Loose connections from pole | 0 | 19573 | 19573 | 14426 | 5018 | 113 | 16 | 19573 | 0
| A(ii) | Interruption due to line breakdown | 0 | 22100 | 22100 | 16020 | 6027 | 46 | 7 | 22100 | 0
| A(iii) | Interruption due to failure of transformer | 0 | 5345 | 5345 | 2452 | 2813 | 72 | 8 | 5345 | 0
| B(i) | Ordinary case, which requires no augmentation. | 0 | 1002 | 1002 | 691 | 311 | 0 | 0 | 1002 | 0
| B(ii) | Where augmentation is required. | 0 | 55 | 55 | 33 | 22 | 0 | 0 | 55 | 0
| C(i) | Stopped/Defective Meters | 1474 | 2633 | 4107 | 1126 | 843 | 231 | 218 | 2418 | 1689
| C(ii) | Billing on average basis for more than two bills | 0 | 414 | 414 | 294 | 111 | 8 | 1 | 414 | 0
| D(i) | Loose Wires | 0 | 2677 | 2677 | 1741 | 921 | 11 | 4 | 2677 | 0
| D(ii) | Inadequate ground clearance | 0 | 375 | 375 | 286 | 74 | 12 | 3 | 375 | 0
| E(i) | For current bills where no additional information is required | 0 | 473 | 473 | 327 | 146 | 0 | 0 | 473 | 0
| E(ii) | Where additional information relating to correctness of reading etc. is required | 0 | 402 | 402 | 282 | 117 | 2 | 1 | 402 | 0
| F(i) | Where extension of mains is not required | 0 | 3193 | 3193 | 2278 | 910 | 5 | 0 | 3193 | 0
| F(ii) | Where extension of mains is required | 0 | 174 | 174 | 126 | 44 | 3 | 1 | 174 | 0
| F(iii) | Modification in connected load | 0 | 264 | 264 | 164 | 92 | 7 | 1 | 264 | 0
| F(iv) | Name change/reconnection | 0 | 138 | 138 | 63 | 74 | 1 | 0 | 138 | 0
| G | Refund of amount due in regard to temporary connection | 0 | 57 | 57 | 9 | 47 | 1 | 0 | 57 | 0
| H | Others | 4 | 10696 | 10700 | 7857 | 2761 | 68 | 11 | 10697 | 3
SNR | A(i) | Loose connections from pole | 0 | 1360 | 1360 | 840 | 377 | 103 | 40 | 1360 | 0
| A(ii) | Interruption due to line breakdown | 0 | 1330 | 1330 | 765 | 435 | 100 | 30 | 1330 | 0
| A(iii) | Interruption due to failure of transformer | 0 | 1278 | 1278 | 789 | 414 | 65 | 10 | 1278 | 0
| B(i) | Ordinary case, which requires no augmentation. | 0 | 405 | 405 | 140 | 240 | 25 | 0 | 405 | 0
| B(ii) | Where augmentation is required. | 30 | 250 | 280 | 95 | 115 | 33 | 7 | 250 | 30
| C(i) | Stopped/Defective Meters | 0 | 625 | 625 | 350 | 260 | 15 | 0 | 625 | 0
| C(ii) | Billing on average basis for more than two bills | 0 | 805 | 805 | 490 | 260 | 50 | 5 | 805 | 0
| D(i) | Loose Wires | 0 | 308 | 308 | 175 | 103 | 30 | 0 | 308 | 0
| D(ii) | Inadequate ground clearance | 0 | 310 | 310 | 192 | 99 | 15 | 4 | 310 | 0
| E(i) | For current bills where no additional information is required | 0 | 395 | 395 | 250 | 115 | 20 | 10 | 395 | 0
| E(ii) | Where additional information relating to correctness of reading etc. is required | 0 | 85 | 85 | 40 | 38 | 4 | 3 | 85 | 0
| F(i) | Where extension of mains is not required | 0 | 100 | 100 | 59 | 27 | 13 | 1 | 100 | 0
| F(ii) | Where extension of mains is required | 0 | 105 | 105 | 35 | 65 | 3 | 2 | 105 | 0
| F(iii) | Modification in connected load | 0 | 245 | 245 | 138 | 72 | 30 | 5 | 245 | 0
| F(iv) | Name change/reconnection | 0 | 190 | 190 | 100 | 70 | 15 | 5 | 190 | 0
| G | Refund of amount due in regard to temporary connection | 0 | 200 | 200 | 110 | 70 | 20 | 0 | 200 | 0
| H | Others | 0 | 720 | 720 | 345 | 350 | 25 | 0 | 720 | 0
PGVCL | A(i) | Loose connections from pole | 73 | 108647 | 106480 | 71659 | 36763 | 216 | 56 | 108694 | 26
| A(ii) | Interruption due to line breakdown | 41 | 97666 | 95924 | 56756 | 40711 | 190 | 37 | 97694 | 13
| A(iii) | Interruption due to failure of transformer | 75 | 27992 | 26889 | 15110 | 12337 | 556 | 18 | 28021 | 46
| B(i) | Ordinary case, which requires no augmentation. | 28 | 5091 | 4967 | 3180 | 1888 | 29 | 0 | 5097 | 22
| B(ii) | Where augmentation is required. | 39 | 2116 | 2000 | 1184 | 892 | 35 | 7 | 2118 | 37
| C(i) | Stopped/Defective Meters | 1521 | 25215 | 25775 | 12725 | 11838 | 246 | 218 | 25027 | 1709
| C(ii) | Billing on average basis for more than two bills | 27 | 7626 | 6875 | 4881 | 2686 | 58 | 6 | 7631 | 22
| D(i) | Loose Wires | 52 | 16448 | 15574 | 9630 | 6798 | 41 | 4 | 16473 | 27
| D(ii) | Inadequate ground clearance | 3 | 2343 | 2346 | 1344 | 967 | 27 | 7 | 2345 | 1
| E(i) | For current bills where no additional information is required | 5 | 6210 | 5586 | 4096 | 2085 | 20 | 10 | 6211 | 4
| E(ii) | Where additional information relating to correctness of reading etc. is required | 14 | 5925 | 5366 | 3807 | 2105 | 6 | 4 | 5922 | 17
| F(i) | Where extension of mains is not required | 7 | 6737 | 6566 | 4526 | 2192 | 18 | 1 | 6737 | 7
| F(ii) | Where extension of mains is required | 2 | 1430 | 1406 | 774 | 647 | 6 | 3 | 1430 | 2
| F(iii) | Modification in connected load | 23 | 4820 | 4338 | 2778 | 1999 | 37 | 6 | 4820 | 23
| F(iv) | Name change/reconnection | 28 | 11441 | 10940 | 6253 | 5177 | 16 | 5 | 11451 | 18
| G | Refund of amount due in regard to temporary connection | 16 | 2555 | 2459 | 1094 | 1437 | 21 | 0 | 2552 | 19
| H | Others | 262 | 34811 | 32070 | 20894 | 13811 | 104 | 11 | 34820 | 253
|  |  | 2216 | 367073 | 355561 | 220691 | 144333 | 1626 | 393 | 367043 | 2246
|  | RED MARK SHOULD BE GREATER THAN 0. | 4: BLANK; 5: AUTO; 6: BLANK; 10: AUTO; 11: PUT IN FIRST COLUMN
COLUMN - D IS NOT EQUAL TO COLUMN - L
|  |  |  | 122357.6667 | 118520.3333
Note on N109: PL. CHECK WHEN UPDATION OF NEW REPORT OF ANJAR CIRCLE

## 004
Performa SoP 004:Publicity carried out
Sr. No | Name of Area/Circle | Actions or steps carried out by distribution licensee towards public awareness in the quarter | Likely number of consumers influenced | Earlier Submission
1 | Rajkot/ Rajkot City | Field area visit at different school, Colleges, Temple, residential areas-society, RMC gardens, RMC office for safety awareness and energy conservation and also village meeting & Khedut Shibir is arranged for safety | 11239 | Rajkot/ Rajkot City | Field area visit at different school, Colleges, Temple, residential areas-society, RMC gardens, RMC office for safety awareness and energy conservation and also village meeting & Khedut Shibir is arranged for safety | 10648
2 | Rajkot/ Rajkot City | safety pamphlets/Booklets distributed in all s.dn area | 7824 | Rajkot/ Rajkot City | safety pamphlets/Booklets distributed in all s.dn area | 6282
3 | Rajkot Rural/ Rajkot Rural | Field area visit at different village meeting & Khedut Shibir is arranged for safety | 6489 | Rajkot Rural/ Rajkot Rural | safety pamphlets/Booklets distributed in all s.dn area | 243
4 | Rajkot Rural/ Rajkot Rural | safety pamphlets/Booklets distributed in all s.dn area | 3659 | Morbi/ MRB | safety pamphlets distributed in all s.dn area | 996
5 | Morbi/ MRB | Accident awareness to village people and school students regarding safety awareness during field visit | 6730 | Porbandar/ PBR | Accident awareness to village people and school students regarding safety awareness during field visit | 1452
6 | Morbi/ MRB | safety pamphlets distributed in all s.dn area | 533 | Porbandar/ PBR | safety pamphlets distributed in Safety & Energy Conservation Rally at porbandar | 5635
7 | Porbandar/ PBR | 220 no. of safety meetings has been arranged in divions and sub division for safety point of view | 2144 | Jamnagar/ JMN | Field area visit at different school, Colleges, Temple, residential areas-society, JMC gardens, JMC office for safety awareness and energy conservation and also village meeting & Khedut Shibir is arranged for safety | 7381
8 | Porbandar/ PBR | Safety training given to departmental employees | 226 | Jamnagar/ JMN | Accident awareness to village people and school students regarding safety awareness during field visit | 147
9 | Porbandar/ PBR | 3830 No. of Safety Pamphlates are distributed | 3830 | Jamnagar/ JMN | safety pamphlets distributed in all s.dn area | 918
10 | Porbandar/ PBR | stall/Mela has been organised at JANMASTAMI LOK Mela under kamlabaug sdn | 45120 | Junagadh/ JND | 297 - no of Field area & village visit arranged | 4623
11 | Jamnagar/ JMN | Field area visit at different school, Colleges, Temple, residential areas-society, JMC gardens, JMC office for safety awareness and energy conservation and also village meeting & Khedut Shibir is arranged for safety | 8323 | Junagadh / JND | Safety pamphlets distributed to general public during Seva Setu | 3420
12 | Jamnagar/ JMN | Accident awareness to village people and school students regarding safety awareness during field visit | 1608 | Junagadh / JND | 14- Nos OF Stall Mela Arranged during Seva Setu & KSY Launching | 2093
13 | BHUJ/ BHUJ | Public awareness programmes were arranged at Village level (village visit/Khedut Shibir) for awareness of general public regarding electrical safety & accident.Safety pamphlets distributed to general public. | 2431 | BHUJ/ BHUJ | Public awareness programmes were arranged at Village level (village visit/Khedut Shibir) for awareness of general public regarding electrical safety & accident. | 2705
14 | MANDVI/ BHUJ | Public awareness programmes were arranged at Village level (village visit/Khedut Shibir) for awareness of general public regarding electrical safety & accident.Safety pamphlets distributed to general public. | 1900 | Anjar/ Anjar | Field area visit at different school, Colleges, Temple, residential areas-society for safety awareness and energy conservation and around 267 village meeting & Khedut Shibir is arranged for safety | 1811
15 | NAKHATRANA/ BHUJ | Public awareness programmes were arranged at Village level (village visit/Khedut Shibir) for awareness of general public regarding electrical safety & accident.Safety pamphlets distributed to general public. | 978 | Anjar/ Anjar | Around 65 no. of safety meetings arranged in 3 divisions & 1 no. of committee meetings arranged at circle level | 469
16 | Anjar/ Anjar | Field area visit at different school, Colleges, Temple, residential areas-society for safety awareness and energy conservation and around 306 village meeting & Khedut Shibir is arranged for safety | 2460 | Anjar/ Anjar | 61 no. of Contractor's meetings has been arranged in all divions for safety point of view | 380
17 | Anjar/ Anjar | Around 153 no. of safety meetings arranged in 3 divisions & 3 no. of committee meetings arranged at circle level | 1998 | Anjar/ Anjar | 3000 No. of Safety Pamphlates are distributed | 3000
18 | Anjar/ Anjar | 84 no. of Contractor's meetings has been arranged in all divions for safety point of view | 458 | Bhavnagar / BVN | safety pemplate distribute under bhavnagar circle. | 1415
19 | Anjar/ Anjar | 100 No. of Safety Pamphlates are distributed | 100 | Botad | Safety pamphlets distributed in the Botad town area while rally arranged for Energy Conservation in Azadi Ka Amrut Mahotsav Program | 3000
20 | Anjar/ Anjar | 39 No. of mock drill arranged in 3 divisions | 403 | Amreli / AMR | Village meeting /khedut shibir/field visit carried out/Contractor meeting | 2207
21 | Anjar/ Anjar | Safety training given to 118 no. of employees | 118 | Amreli / AMR | Safety pamphlets distributed in the Botad town area while rally arranged for Energy Conservation in Azadi Ka Amrut Mahotsav Program | 600
22 | Junagadh/ JND | 907 - no of Field area & village visit arranged | 15125 | Amreli / AMR | Mock Drill | 116
23 | Junagadh/ JND | Safety pamphlets distributed to general public | 412 | SNR | safety pamphlets/Booklets distributed in all s.dn area | 178
24 | Junagadh/ JND | 03- Nos OF Stall Mela Arranged during Seva Setu | 72 | Surendranagar/ SNR | safety pamphlets/Booklets distributed in all s.dn area | 0
25 | BVN/ BVN | gramsabha arranged at variour place under bhavnagar circle. | 5452
26 | BVN/ BVN | ward meeting arranged at variour place under bhavnagar circle. | 2101
27 | BVN/ BVN | Programme arranged i.e slogan,drawing,essay,drama compettition | 0
28 | Botad/ BTD | Arranged 290 nos. of Field Area Visit/Village meeting/Khedut Shibir under different villages of Botad Circle | 6176
29 | Amreli / AMR | Village meeting /khedut shibir/field visit carried out/Contractor meeting | 6812
30 | Amreli / AMR | Safety pamphlets distributed in the Botad town area while rally arranged for Energy Conservation in Azadi Ka Amrut Mahotsav Program | 9066
31 | Amreli / AMR | Mock Drill | 58
32 | SNR/ SNR | safety pamphlets/Booklets distributed in all s.dn area | 5642
33 | SNR/ SNR | Field area visit | 1135

## 05B
Performa – SoP 005 B:Action taken report by the Redressal Committee (2021-22-4th Qtr.)
Sr. No | Name of Area/Circle | Qtr | FY-2021-22 | Date and Time Meeting conducted | No of complaints registered at the meeting | No. of complaints pending at the end of the meeting
1 | RJC | 4th Quarter | 10th Month (Jan-22) | 10 & 20 of the Month | 0 | 0
|  |  | 11th Month (Feb-22) | 10 & 20 of the Month | 0 | 0
|  |  | 12th Month (Mar-22) | 10 & 20 of the Month | 0 | 0
2 | RRC | 4th Quarter | 10th Month (Jan-22) | 10 & 20 of the Month | 0 | 0
|  |  | 11th Month (Feb-22) | 10 & 20 of the Month | 0 | 0
|  |  | 12th Month (Mar-22) | 10 & 20 of the Month | 1 | 0
3 | MRB | 4th Quarter | 10th Month (Jan-22) | 10 & 20 of the Month | 0 | 0
|  |  | 11th Month (Feb-22) | 10 & 20 of the Month | 0 | 0
|  |  | 12th Month (Mar-22) | 10 & 20 of the Month | 0 | 0
4 | PBR | 4th Quarter | 10th Month (Jan-22) | 10 & 20 of the Month | 0 | 0
|  |  | 11th Month (Feb-22) | 10 & 20 of the Month | 0 | 0
|  |  | 12th Month (Mar-22) | 10 & 20 of the Month | 0 | 0
5 | JMN | 4th Quarter | 10th Month (Jan-22) | 10 & 20 of the Month | 0 | 0
|  |  | 11th Month (Feb-22) | 10 & 20 of the Month | 0 | 0
|  |  | 12th Month (Mar-22) | 10 & 20 of the Month | 0 | 0
6 | JND | 4th Quarter | 10th Month (Jan-22) | 10 & 20 of the Month | 1 | 0
|  |  | 11th Month (Feb-22) | 10 & 20 of the Month | 0 | 0
|  |  | 12th Month (Mar-22) | 10 & 20 of the Month | 0 | 0
7 | Bhuj | 4th Quarter | 10th Month (Jan-22) | 10 & 20 of the Month | 0 | 0
|  |  | 11th Month (Feb-22) | 10 & 20 of the Month | 0 | 0
|  |  | 12th Month (Mar-22) | 10 & 20 of the Month | 0 | 0
8 | ANJ | 4th Quarter | 10th Month (Jan-22) | 10 & 20 of the Month | 0 | 0
|  |  | 11th Month (Feb-22) | 10 & 20 of the Month | 0 | 0
|  |  | 12th Month (Mar-22) | 10 & 20 of the Month | 0 | 0
9 | BVN | 4th Quarter | 10th Month (Jan-22) | 10 & 20 of the Month | 0 | 0
|  |  | 11th Month (Feb-22) | 10 & 20 of the Month | 0 | 0
|  |  | 12th Month (Mar-22) | 10 & 20 of the Month | 0 | 0
10 | BTD | 4th Quarter | 10th Month (Jan-22) | 10 & 20 of the Month | 0 | 0
|  |  | 11th Month (Feb-22) | 10 & 20 of the Month | 0 | 0
|  |  | 12th Month (Mar-22) | 10 & 20 of the Month | 0 | 0
11 | AMR | 4th Quarter | 10th Month (Jan-22) | 10 & 20 of the Month | 0 | 0
|  |  | 11th Month (Feb-22) | 10 & 20 of the Month | 0 | 0
|  |  | 12th Month (Mar-22) | 10 & 20 of the Month | 0 | 0
12 | SNR | 4th Quarter | 10th Month (Jan-22) | 10 & 20 of the Month | 0 | 0
|  |  | 11th Month (Feb-22) | 10 & 20 of the Month | 0 | 0
|  |  | 12th Month (Mar-22) | 10 & 20 of the Month | 0 | 0
| PGVCL | 4th Quarter | 10th Month (Jan-22) | 10 & 20 of the Month | 1 | 0
|  |  | 11th Month (Feb-22) | 10 & 20 of the Month | 0 | 0
|  |  | 12th Month (Mar-22) | 10 & 20 of the Month | 1 | 0
| Total |  |  | Total | 2 | 0

## 006
Performa SoP 006: Failure of Distribution Transformer
Sr. No. | Name of Area/Circle | No. of existing Distribution Transformers at the start of the quarter / year | No. of Distribution Transformers added during the quarter / year | Total number of Distribution Transformers | Total number of Distribution transformer failed | % failure rate of Distribution transformer | Remarks
|  | A | B | C=A+B | D | H = (D)*100/C
1 | RJC | 15071 | 171 | 15242 | 151 | 0.99068
2 | RJR | 180557 | 820 | 181377 | 5647 | 3.1134
3 | MRB | 63283 | 695 | 63978 | 2127 | 3.3246
4 | PBR | 81513 | 488 | 82001 | 3518 | 4.2902
5 | JMN | 161779 | 1617 | 163396 | 7921 | 4.8477
6 | BHJ | 51778 | 600 | 52378 | 2002 | 3.8222
7 | ANJAR | 32043 | 366 | 32409 | 1268 | 3.9125
8 | JND | 86104 | 859 | 86963 | 2773 | 3.1887
9 | BVN | 96642 | 1348 | 97990 | 3273 | 3.3401
10 | BTD | 55916 | 917 | 56833 | 1786 | 3.1425
11 | AMR | 139543 | 1147 | 140690 | 7135 | 5.0714
12 | SNR | 72435 | 1373 | 73808 | 2807 | 3.8031
PGVCL |  | 1036664 | 10401 | 1047065 | 40408 | 3.8592
[5 empty] | CHANGE LINK |  | UPTO MAR | CROSS CHECK
QTR - 4 |  |  | 0 |  |  | #DIV/0! |  | -276
|  |  | 0 |  |  | #DIV/0! |  | -8803
|  |  | 0 |  |  | #DIV/0! |  | -3453
|  |  | 0 |  |  | #DIV/0! |  | -5332
|  |  | 0 |  |  | #DIV/0! |  | -11946
|  |  | 0 |  |  | #DIV/0! |  | -3028
|  |  | 0 |  |  | #DIV/0! |  | -1955
|  |  | 0 |  |  | #DIV/0! |  | -4526
|  |  | 0 |  |  | #DIV/0! |  | -5497
|  |  | 0 |  |  | #DIV/0! |  | -2719
|  |  | 0 |  |  | #DIV/0! |  | -11337
|  |  | 0 |  |  | #DIV/0! |  | -4488
|  | 0 | 0 | 0 | 0 | #DIV/0! | 0 | -63360
[5 empty] | CHANGE LINK |  | UPTO DEC | CROSS CHECK
QTR - 3 |  |  | 0 |  |  | #DIV/0! |  | -276
|  |  | 0 |  |  | #DIV/0! |  | -8803
|  |  | 0 |  |  | #DIV/0! |  | -3453
|  |  | 0 |  |  | #DIV/0! |  | -5332
|  |  | 0 |  |  | #DIV/0! |  | -11946
|  |  | 0 |  |  | #DIV/0! |  | -3028
|  |  | 0 |  |  | #DIV/0! |  | -1955
|  |  | 0 |  |  | #DIV/0! |  | -4526
|  |  | 0 |  |  | #DIV/0! |  | -5497
|  |  | 0 |  |  | #DIV/0! |  | -2719
|  |  | 0 |  |  | #DIV/0! |  | -11337
|  |  | 0 |  |  | #DIV/0! |  | -4488
|  | 0 | 0 | 0 | 0 | #DIV/0! | 0 | -63360
UPTO SEP
QTR - 2 |  | 15071 | 171 | 15242 | 151 | 0.99068 | 276 | 151
|  | 180557 | 820 | 181377 | 5647 | 3.1134 | 8803 | 5647
|  | 63283 | 695 | 63978 | 2127 | 3.3246 | 3453 | 2127
|  | 81513 | 488 | 82001 | 3518 | 4.2902 | 5332 | 3518
|  | 161779 | 1617 | 163396 | 7921 | 4.8477 | 11946 | 7921
|  | 51778 | 600 | 52378 | 2002 | 3.8222 | 3028 | 2002
|  | 32043 | 366 | 32409 | 1268 | 3.9125 | 1955 | 1268
|  | 86104 | 859 | 86963 | 2773 | 3.1887 | 4526 | 2773
|  | 96642 | 1348 | 97990 | 3273 | 3.3401 | 5497 | 3273
|  | 55916 | 917 | 56833 | 1786 | 3.1425 | 2719 | 1786
|  | 139543 | 1147 | 140690 | 7135 | 5.0714 | 11337 | 7135
|  | 72435 | 1373 | 73808 | 2807 | 3.8031 | 4488 | 2807
|  | 1036664 | 10401 | 1047065 | 40408 | 3.8592 | 63360 | 40408
QTR - 1 |  | 14880 | 191 | 15071 | 125 | 0.82941
|  | 179807 | 750 | 180557 | 3156 | 1.7479
|  | 63099 | 184 | 63283 | 1326 | 2.0953
|  | 81513 | 0 | 81513 | 1814 | 2.2254
|  | 159147 | 2632 | 161779 | 4025 | 2.488
|  | 51183 | 595 | 51778 | 1026 | 1.9815
|  | 31844 | 199 | 32043 | 687 | 2.144
|  | 85520 | 584 | 86104 | 1753 | 2.0359
|  | 96222 | 420 | 96642 | 2224 | 2.3013
|  | 55744 | 172 | 55916 | 933 | 1.6686
|  | 138431 | 1112 | 139543 | 4202 | 3.0113
|  | 71959 | 476 | 72435 | 1681 | 2.3207
|  | 1029349 | 7315 | 1036664 | 22952 | 2.214

## 007
Performa SoP 007: Failure of Power Transformer
Sr. No. | Name of Area/Circle | No. of existing Power Transformers at the start of the quarter / year | no. of Power Transformers added during the quarter / year | Total number of Power Transformers | Total number of Power transformer failed | % failure rate of Power transformer
|  | A | B | C=A+B | D | H = (D)*100/C
1 | RJC | Not Applicable
| RJR | Not Applicable
| MRB | Not Applicable
| PBR | Not Applicable
| JMN | Not Applicable
| BHJ | Not Applicable
| ANJ | Not Applicable
| JND | Not Applicable
| BVN | Not Applicable
| BTD | Not Applicable
| AMR | Not Applicable
| SNR | Not Applicable

## Sheet1 (hidden)
add | rep |  |  | pen
5532 | 5283 |  |  | 1399
1829 | 1829 | 1829 | 1829 | 0
8542 | 8855 |  |  | 6434
1324 | 1083 | 1324 | 1083 | 744
7369 | 10688 |  |  | 7564
569 | 598 | 569 | 598 | 222
8950 | 16365 |  |  | 12125
530 | 1110 | 530 | 1110 | 709
4115 | 4205 |  |  | 8514
232 | 232 | 232 | 232 | 0
13485 | 8807 |  |  | 12511
887 | 868 | 887 | 868 | 24
13152 | 18190 |  |  | 24335
378 | 348 | 378 | 348 | 85
8197 | 7971 |  |  | 7458
1179 | 1193 | 1179 | 1193 | 24
3737 | 5953 |  |  | 7568
386 | 892 | 386 | 892 | 1104
73079 | 86317 |  |  | 87908
7314 | 8153 | 7314 | 8153 | 2912

## Accident (2) (hidden)
PASCHIM GUJARAT VIJ COMPANY LIMITED REGD. & CORPORATE OFFICE, RAJKOT
ACCIDENT DETAILS | [9 empty] | 2010-03-05
No | CIRCLE | DIVISION | Nos. of accidents(victim) during Month | [7 empty] | Cummulative | [8 empty] | Previous Month |  |  |  | 2006-04-01 |  |  | 2006-05-01 |  |  | 2006-06-01 |  |  | 2006-07-01 |  |  | 2006-08-01 |  |  | 2006-09-01 |  |  | 2006-10-01 |  |  | 2006-11-01 |  |  | 2006-12-01 |  |  | 2007-01-01 |  |  | 2007-02-01 |  |  | 2007-03-01 |  |  | Cumulative since mayil-05
| 1 | 3 | Department |  | Outsider |  |  | Total |  |  | Department |  | Outsider |  |  | Total |  |  |  | FH | FA | NFH |  | Total |  |  | Total |  |  | Total |  |  | Total |  |  | Total |  |  | Total |  |  | Total |  |  | Total |  |  | Total |  |  | Total |  |  | Total |  |  | Total |  |  | Total
| 1 | 3 | FH | NFH | FH | FA | NFH | FH | FA | NFH | FH | NFH | FH | FA | NFH | FH | FA | NFH |  |  |  |  | 18 | FH | FA | NFH | FH | FA | NFH | FH | FA | NFH | FH | FA | NFH | FH | FA | NFH | FH | FA | NFH | FH | FA | NFH | FH | FA | NFH | FH | FA | NFH | FH | FA | NFH | FH | FA | NFH | FH | FA | NFH | FH | FA | NFH
1 | RJC | RAJKOT C-1 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 1 | 2 | 7 | 4 | 2 | 7 | 5 | 14 | 2 | 7 | 4 |  | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 5 | 0 | 0 | 2 | 1 | 0 | 0 | 0 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 1
2 |  | RAJKOT C-2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 7 | 1 | 1 | 8 | 10 | 1 | 1 | 8 |  | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 3 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 1 | 3
3 |  | RAJKOT C-3 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 1 | 5 | 7 | 11 | 5 | 7 | 12 | 24 | 5 | 7 | 11 |  | 0 | 0 | 0 | 1 | 0 | 1 | 0 | 2 | 1 | 2 | 3 | 2 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 2 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 1 | 2 | 2 | 6
1 |  | CIRCLE-TOTAL | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 3 | 8 | 15 | 22 | 8 | 15 | 25 | 48 | 8 | 15 | 23 |  | 0 | 0 | 2 | 1 | 0 | 2 | 1 | 7 | 4 | 2 | 5 | 3 | 0 | 0 | 1 | 1 | 0 | 3 | 0 | 2 | 1 | 0 | 0 | 0 | 0 | 1 | 3 | 3 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 3 | 3 | 10 | 16
1 | RJR | GONDAL | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 1 | 0 | 7 | 8 | 5 | 8 | 8 | 5 | 21 | 8 | 8 | 4 |  | 1 | 0 | 0 | 0 | 0 | 1 | 0 | 3 | 1 | 1 | 3 | 0 | 1 | 1 | 0 | 1 | 0 | 1 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 2 | 0 | 0 | 0 | 0 | 1 | 4 | 1 | 2
2 |  | DHORAJI | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 5 | 11 | 23 | 6 | 12 | 23 | 11 | 46 | 12 | 23 | 11 |  | 2 | 0 | 0 | 0 | 1 | 1 | 3 | 6 | 2 | 1 | 8 | 2 | 2 | 0 | 2 | 1 | 6 | 2 | 1 | 0 | 2 | 0 | 2 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 3 | 2 | 2
3 |  | JASDAN | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 | 6 | 2 | 2 | 6 | 3 | 11 | 2 | 6 | 3 |  | 0 | 1 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 4 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1
4 |  | RAJKOT RURAL | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3 | 6 | 3 | 3 | 6 | 4 | 13 | 3 | 6 | 4 |  | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 3 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2 |  | CIRCLE-TOTAL | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 2 | 7 | 23 | 43 | 16 | 25 | 43 | 23 | 91 | 25 | 43 | 22 |  | 4 | 1 | 2 | 0 | 1 | 2 | 4 | 10 | 3 | 3 | 18 | 3 | 3 | 3 | 3 | 3 | 7 | 4 | 1 | 0 | 4 | 1 | 3 | 0 | 1 | 0 | 0 | 1 | 0 | 1 | 4 | 0 | 0 | 0 | 0 | 1 | 8 | 3 | 6 | 17
3 | MRB | MORBI | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 8 | 8 | 4 | 8 | 8 | 6 | 22 | 9 | 10 | 6 |  | 0 | 2 | 0 | 0 | 0 | 1 | 1 | 1 | 0 | 4 | 3 | 1 | 0 | 1 | 0 | 1 | 1 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 2 | 0 | 3
4 |  | HALVAD | 0 | 1 | 3 | 4 | 1 | 3 | 4 | 2 | 0 | 2 | 5 | 12 | 1 | 5 | 12 | 3 | 20 | 1 | 6 | 1 |  | 1 | 1 | 0 | 1 | 0 | 0 | 1 | 3 | 0 | 0 | 5 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 | 1 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 0 | 2 | 2 | 3
4 |  | CIRCLE-TOTAL | 0 | 1 | 3 | 4 | 1 | 3 | 4 | 2 | 0 | 4 | 13 | 20 | 5 | 13 | 20 | 9 | 42 | 10 | 16 | 7 |  | 1 | 3 | 0 | 1 | 0 | 1 | 2 | 4 | 0 | 4 | 8 | 1 | 0 | 2 | 0 | 1 | 1 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 1 | 2 | 1 | 0 | 1 | 0 | 0 | 2 | 1 | 1 | 1 | 4 | 2 | 6 | 12
1 | PBR | PBR CITY | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 2 | 6 | 12 | 1 | 6 | 12 | 3 | 21 | 5 | 12 | 3 |  | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 2 | 0 | 0 | 6 | 2 | 2 | 3 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 2 | 0 | 0
2 |  | PBR RURAL | 0 | 0 | 3 | 0 | 3 | 3 | 0 | 3 | 0 | 2 | 8 | 15 | 5 | 8 | 15 | 7 | 30 | 5 | 15 | 4 |  | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 4 | 1 | 0 | 5 | 0 | 1 | 3 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 1 | 2 | 0 | 1 | 1 | 0 | 1 | 0 | 1 | 0 | 0 | 0 | 3 | 0 | 3 | 6 | 3 | 5
3 |  | KESHOD-1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 6 | 0 | 2 | 6 | 0 | 8 | 2 | 6 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 4 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0
4 |  | KESHOD-2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 17 | 3 | 8 | 17 | 3 | 28 | 8 | 17 | 3 |  | 0 | 0 | 0 | 1 | 0 | 0 | 3 | 3 | 0 | 1 | 11 | 3 | 0 | 2 | 0 | 3 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0
4 |  | CIRCLE-TOTAL | 0 | 0 | 4 | 0 | 3 | 4 | 0 | 3 | 0 | 4 | 24 | 50 | 9 | 24 | 50 | 13 | 87 | 20 | 50 | 10 |  | 0 | 0 | 0 | 2 | 0 | 1 | 4 | 10 | 1 | 2 | 26 | 5 | 3 | 9 | 0 | 4 | 1 | 1 | 0 | 1 | 1 | 1 | 2 | 0 | 1 | 1 | 0 | 2 | 0 | 1 | 1 | 0 | 0 | 4 | 0 | 3 | 9 | 4 | 5 | 18
1 | JMN | JMN CITY-1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 5 | 5 | 2 | 5 | 5 | 3 | 13 | 4 | 5 | 3 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 0 | 1 | 1 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 3 | 2 | 1
2 |  | JMN CITY-2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 12 | 6 | 2 | 12 | 6 | 20 | 2 | 12 | 6 |  | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 | 1 | 0 | 4 | 1 | 0 | 1 | 2 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 3 | 0 | 0 | 2 | 1 | 0 | 0 | 0 | 1 | 5 | 2
3 |  | JAMNAGAR | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 2 | 14 | 6 | 2 | 14 | 7 | 23 | 2 | 14 | 6 |  | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 4 | 1 | 1 | 3 | 0 | 0 | 4 | 4 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 2
4 |  | KHAMBHALIA | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 2 | 10 | 18 | 10 | 10 | 18 | 12 | 40 | 10 | 17 | 12 |  | 1 | 0 | 0 | 1 | 0 | 0 | 2 | 4 | 4 | 1 | 7 | 2 | 1 | 4 | 1 | 0 | 2 | 2 | 1 | 0 | 3 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 4 | 1 | 3
|  | JAMJODHPUR | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0
5 |  | CIRCLE-TOTAL | 0 | 1 | 3 | 1 | 0 | 3 | 1 | 1 | 0 | 4 | 21 | 49 | 24 | 21 | 49 | 28 | 98 | 18 | 48 | 27 |  | 1 | 0 | 0 | 1 | 2 | 0 | 3 | 11 | 7 | 3 | 15 | 3 | 2 | 10 | 7 | 0 | 2 | 3 | 3 | 2 | 4 | 2 | 0 | 0 | 0 | 1 | 1 | 1 | 3 | 1 | 2 | 2 | 1 | 1 | 1 | 1 | 9 | 9 | 8 | 26
1 | BHJ | BHUJ | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 6 | 5 | 4 | 7 | 5 | 4 | 13 | 22 | 4 | 4 | 13 |  | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 2 | 2 | 1 | 2 | 0 | 0 | 0 | 2 | 2 | 0 | 1 | 0 | 0 | 4 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 2 | 0 | 6
2 |  | MANDVI | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 2 | 2 | 13 | 5 | 2 | 13 | 7 | 22 | 2 | 13 | 6 |  | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 7 | 1 | 0 | 1 | 1 | 0 | 4 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 4
3 |  | ANJAR | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 5 | 3 | 4 | 5 | 3 | 4 | 12 | 4 | 3 | 4 |  | 0 | 0 | 1 | 1 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 3 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 3 | 1 | 0
4 |  | GANDHIDHAM | 0 | 0 | 3 | 0 | 0 | 3 | 0 | 0 | 0 | 1 | 15 | 2 | 2 | 15 | 2 | 3 | 20 | 12 | 2 | 3 |  | 1 | 0 | 0 | 1 | 0 | 1 | 2 | 1 | 0 | 4 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 2 | 0 | 0 | 3 | 0 | 0 | 7 | 0 | 1
6 |  | CIRCLE-TOTAL | 0 | 0 | 5 | 0 | 1 | 5 | 0 | 1 | 0 | 9 | 27 | 22 | 18 | 27 | 22 | 27 | 76 | 22 | 22 | 26 |  | 1 | 0 | 3 | 2 | 0 | 2 | 4 | 11 | 3 | 5 | 4 | 5 | 0 | 4 | 2 | 2 | 1 | 1 | 2 | 0 | 6 | 0 | 0 | 0 | 0 | 1 | 3 | 4 | 1 | 1 | 2 | 0 | 0 | 5 | 0 | 1 | 13 | 2 | 11 | 26
1 | JND | JUNAGADH CITY | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 3 | 2 | 1 | 3 | 3 | 7 | 1 | 3 | 3 |  | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 2
2 |  | JUNAGADH DN-1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 5 | 5 | 4 | 12 | 5 | 4 | 17 | 26 | 5 | 4 | 16 |  | 0 | 0 | 3 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 3 | 4 | 1 | 0 | 2 | 1 | 0 | 2 | 1 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 1 | 0 | 4
3 |  | JUNAGADH DN-2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 9 | 3 | 1 | 9 | 3 | 13 | 1 | 9 | 3 |  | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 7 | 1 | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
4 |  | VERAVAL | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 8 | 27 | 5 | 8 | 27 | 7 | 42 | 8 | 27 | 7 |  | 0 | 0 | 0 | 0 | 0 | 2 | 2 | 6 | 0 | 1 | 7 | 0 | 0 | 8 | 5 | 0 | 0 | 0 | 1 | 3 | 0 | 0 | 1 | 0 | 1 | 2 | 0 | 1 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 5 | 6 | 0
7 |  | CIRCLE-TOTAL | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 8 | 15 | 43 | 22 | 15 | 43 | 30 | 88 | 15 | 43 | 29 |  | 0 | 1 | 3 | 0 | 0 | 4 | 3 | 8 | 1 | 3 | 18 | 5 | 1 | 10 | 7 | 1 | 0 | 3 | 3 | 3 | 1 | 0 | 1 | 3 | 1 | 2 | 0 | 1 | 0 | 1 | 2 | 0 | 1 | 0 | 0 | 1 | 7 | 6 | 7 | 20
1 | BVN | BVN CITY-1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 2 | 0 | 0 | 2 | 0 | 3 | 5 | 2 | 0 | 3 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 2
2 |  | BVN CITY-2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2 | 1 | 1 | 2 | 2 | 5 | 1 | 2 | 2 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1
3 |  | Bhavnagar | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 12 | 15 | 2 | 13 | 15 | 2 | 30 | 13 | 15 | 2 |  | 0 | 0 | 0 | 1 | 1 | 0 | 1 | 5 | 2 | 2 | 4 | 0 | 2 | 4 | 0 | 2 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 5 | 1 | 0
4 |  | MAHUVA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 2 | 6 | 2 | 2 | 6 | 5 | 13 | 2 | 6 | 5 |  | 0 | 1 | 2 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 2 | 1 | 1 | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 2
5 |  | PALITANA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 6 | 10 | 0 | 6 | 10 | 2 | 18 | 6 | 10 | 2 |  | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 4 | 0 | 1 | 2 | 0 | 0 | 1 | 0 | 0 | 3 | 1 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 1
8 |  | CIRCLE-TOTAL | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 9 | 23 | 33 | 5 | 24 | 33 | 14 | 71 | 24 | 33 | 14 |  | 1 | 1 | 2 | 1 | 1 | 0 | 2 | 10 | 3 | 4 | 10 | 1 | 4 | 6 | 0 | 2 | 4 | 2 | 1 | 1 | 1 | 2 | 0 | 0 | 1 | 0 | 1 | 5 | 0 | 2 | 1 | 0 | 2 | 0 | 0 | 0 | 10 | 1 | 6 | 17
1 | BTD | BOTAD | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 3 | 0 | 3 | 3 | 0 | 6 | 3 | 3 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 | 0 | 0 | 1 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0
2 |  | GADHDA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3 | 3 | 1 | 3 | 3 | 7 | 1 | 3 | 3 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 2 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0
9 |  | CIRCLE-TOTAL | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 6 | 3 | 4 | 6 | 3 | 13 | 4 | 6 | 3 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 1 | 4 | 0 | 0 | 2 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 2
1 | AMR | AMRELI -1 | 0 | 1 | 1 | 0 | 2 | 1 | 0 | 3 | 0 | 4 | 5 | 8 | 11 | 5 | 8 | 15 | 28 | 4 | 8 | 12 |  | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 2 | 0 | 1 | 3 | 2 | 1 | 3 | 1 | 1 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 | 0 | 0 | 1 | 0 | 3 | 2 | 0 | 6
2 |  | SAVAR KUNDLA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 9 | 6 | 6 | 9 | 6 | 7 | 22 | 9 | 6 | 7 |  | 0 | 0 | 0 | 0 | 0 | 1 | 3 | 1 | 0 | 3 | 2 | 4 | 0 | 2 | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 2 | 1 | 2
3 |  | UNA | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 5 | 20 | 0 | 6 | 20 | 1 | 27 | 6 | 20 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 3 | 0 | 2 | 10 | 0 | 0 | 4 | 0 | 1 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 | 2 | 1
4 |  | AMRELI-2 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 8 | 15 | 1 | 8 | 15 | 1 | 24 | 7 | 15 | 1 |  | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 2 | 0 | 2 | 7 | 0 | 0 | 4 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 3 | 1 | 1
10 |  | CIRCLE-TOTAL | 0 | 2 | 2 | 0 | 2 | 2 | 0 | 4 | 1 | 6 | 27 | 49 | 18 | 28 | 49 | 24 | 101 | 26 | 49 | 20 |  | 0 | 0 | 0 | 1 | 0 | 6 | 6 | 8 | 0 | 8 | 22 | 6 | 1 | 13 | 1 | 3 | 2 | 1 | 1 | 1 | 2 | 0 | 1 | 0 | 1 | 1 | 1 | 3 | 1 | 2 | 2 | 0 | 1 | 2 | 0 | 4 | 9 | 4 | 10 | 23
1 | SNR | S'NAGAR-1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 2 | 9 | 3 | 2 | 9 | 5 | 16 | 2 | 9 | 6 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 5 | 2 | 0 | 3 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 1 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 2
2 |  | S'NAGAR-2 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 5 | 8 | 4 | 5 | 8 | 5 | 18 | 3 | 11 | 5 |  | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2 | 2 | 5 | 1 | 0 | 2 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 2 | 0 | 1
3 |  | DHANGADHARA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 5 | 6 | 10 | 6 | 6 | 10 | 22 | 7 | 6 | 9 |  | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 0 | 9 | 2 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 1 | 9
0 |  | CIRCLE-TOTAL | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 3 | 12 | 23 | 17 | 13 | 23 | 20 | 56 | 12 | 26 | 20 |  | 1 | 0 | 0 | 1 | 1 | 0 | 1 | 6 | 4 | 3 | 12 | 1 | 0 | 2 | 1 | 0 | 1 | 2 | 1 | 1 | 0 | 1 | 0 | 11 | 3 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 7 | 1 | 12 | 20
|  | PGVCL | 0 | 5 | 18 | 5 | 10 | 18 | 5 | 15 | 5 | 57 | 197 | 353 | 159 | 202 | 353 | 216 | 771 | 184 | 351 | 201 | 0 | 9 | 6 | 12 | 10 | 5 | 18 | 30 | 85 | 29 | 38 | 142 | 33 | 14 | 61 | 22 | 18 | 19 | 21 | 13 | 11 | 20 | 8 | 7 | 14 | 9 | 8 | 12 | 23 | 5 | 12 | 14 | 2 | 9 | 14 | 2 | 14 | 81 | 35 | 81 | 197 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | Rajkot City |  | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 3 | 8 | 15 | 22 | 8 | 15 | 25 | 48 | 8 | 15 | 23 | 0 | 0 | 0 | 2 | 1 | 0 | 2 | 1 | 7 | 4 | 2 | 5 | 3 | 0 | 0 | 1 | 1 | 0 | 3 | 0 | 2 | 1 | 0 | 0 | 0 | 0 | 1 | 3 | 3 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 3 | 3 | 10 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | Rajkot Rural |  | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 2 | 7 | 23 | 43 | 16 | 25 | 43 | 23 | 91 | 25 | 43 | 22 | 0 | 4 | 1 | 2 | 0 | 1 | 2 | 4 | 10 | 3 | 3 | 18 | 3 | 3 | 3 | 3 | 3 | 7 | 4 | 1 | 0 | 4 | 1 | 3 | 0 | 1 | 0 | 0 | 1 | 0 | 1 | 4 | 0 | 0 | 0 | 0 | 1 | 8 | 3 | 6 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | Morbi |  | 0 | 1 | 3 | 4 | 1 | 3 | 4 | 2 | 0 | 4 | 13 | 20 | 5 | 13 | 20 | 9 | 42 | 10 | 16 | 7 | 0 | 1 | 3 | 0 | 1 | 0 | 1 | 2 | 4 | 0 | 4 | 8 | 1 | 0 | 2 | 0 | 1 | 1 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 1 | 2 | 1 | 0 | 1 | 0 | 0 | 2 | 1 | 1 | 1 | 4 | 2 | 6 | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | Porbandar |  | 0 | 0 | 4 | 0 | 3 | 4 | 0 | 3 | 0 | 4 | 24 | 50 | 9 | 24 | 50 | 13 | 87 | 20 | 50 | 10 | 0 | 0 | 0 | 0 | 2 | 0 | 1 | 4 | 10 | 1 | 2 | 26 | 5 | 3 | 9 | 0 | 4 | 1 | 1 | 0 | 1 | 1 | 1 | 2 | 0 | 1 | 1 | 0 | 2 | 0 | 1 | 1 | 0 | 0 | 4 | 0 | 3 | 9 | 4 | 5 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | Jamnagar |  | 0 | 1 | 3 | 1 | 0 | 3 | 1 | 1 | 0 | 4 | 21 | 49 | 24 | 21 | 49 | 28 | 98 | 18 | 48 | 27 | 0 | 1 | 0 | 0 | 1 | 2 | 0 | 3 | 11 | 7 | 3 | 15 | 3 | 2 | 10 | 7 | 0 | 2 | 3 | 3 | 2 | 4 | 2 | 0 | 0 | 0 | 1 | 1 | 1 | 3 | 1 | 2 | 2 | 1 | 1 | 1 | 1 | 9 | 9 | 8 | 26 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | Bhuj |  | 0 | 0 | 5 | 0 | 1 | 5 | 0 | 1 | 0 | 9 | 27 | 22 | 18 | 27 | 22 | 27 | 76 | 22 | 22 | 26 | 0 | 1 | 0 | 3 | 2 | 0 | 2 | 4 | 11 | 3 | 5 | 4 | 5 | 0 | 4 | 2 | 2 | 1 | 1 | 2 | 0 | 6 | 0 | 0 | 0 | 0 | 1 | 3 | 4 | 1 | 1 | 2 | 0 | 0 | 5 | 0 | 1 | 13 | 2 | 11 | 26 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | Junagadh |  | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 8 | 15 | 43 | 22 | 15 | 43 | 30 | 88 | 15 | 43 | 29 | 0 | 0 | 1 | 3 | 0 | 0 | 4 | 3 | 8 | 1 | 3 | 18 | 5 | 1 | 10 | 7 | 1 | 0 | 3 | 3 | 3 | 1 | 0 | 1 | 3 | 1 | 2 | 0 | 1 | 0 | 1 | 2 | 0 | 1 | 0 | 0 | 1 | 7 | 6 | 7 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | Bhavnagar |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 9 | 23 | 33 | 5 | 24 | 33 | 14 | 71 | 24 | 33 | 14 | 0 | 1 | 1 | 2 | 1 | 1 | 0 | 2 | 10 | 3 | 4 | 10 | 1 | 4 | 6 | 0 | 2 | 4 | 2 | 1 | 1 | 1 | 2 | 0 | 0 | 1 | 0 | 1 | 5 | 0 | 2 | 1 | 0 | 2 | 0 | 0 | 0 | 10 | 1 | 6 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | Botad |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 6 | 3 | 4 | 6 | 3 | 13 | 4 | 6 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 1 | 4 | 0 | 0 | 2 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | Amreli |  | 0 | 2 | 2 | 0 | 2 | 2 | 0 | 4 | 1 | 6 | 27 | 49 | 18 | 28 | 49 | 24 | 101 | 26 | 49 | 20 | 0 | 0 | 0 | 0 | 1 | 0 | 6 | 6 | 8 | 0 | 8 | 22 | 6 | 1 | 13 | 1 | 3 | 2 | 1 | 1 | 1 | 2 | 0 | 1 | 0 | 1 | 1 | 1 | 3 | 1 | 2 | 2 | 0 | 1 | 2 | 0 | 4 | 9 | 4 | 10 | 23 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | Surendranagar |  | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 3 | 12 | 23 | 17 | 13 | 23 | 20 | 56 | 12 | 26 | 20 | 0 | 1 | 0 | 0 | 1 | 1 | 0 | 1 | 6 | 4 | 3 | 12 | 1 | 0 | 2 | 1 | 0 | 1 | 2 | 1 | 1 | 0 | 1 | 0 | 11 | 3 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 7 | 1 | 12 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| PGVCL Total → |  | 0 | 5 | 18 | 5 | 10 | 18 | 5 | 15 | 5 | 57 | 197 | 353 | 159 | 202 | 353 | 216 | 771 | 184 | 351 | 201 | 0 | 9 | 6 | 12 | 10 | 5 | 18 | 30 | 85 | 29 | 38 | 142 | 33 | 14 | 61 | 22 | 18 | 19 | 21 | 13 | 11 | 20 | 8 | 7 | 14 | 9 | 8 | 12 | 23 | 5 | 12 | 14 | 2 | 9 | 14 | 2 | 14 | 81 | 35 | 81 | 197 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0

## Accident (hidden)
Performa – SoP 002: Action taken report for safety
measures complied for the accidents occurred
Circle | DFH | DNFH | OFH | OFA | ONFH | sum | count 002 | Difference | yearly
RJC | [5 empty] | 0 | #REF! | #REF!
Circle | [5 empty] | 0 |  | 0
RJR | [5 empty] | 0 | #REF! | #REF!
Circle | [5 empty] | 0 | #REF! | #REF!
MRB | [5 empty] | 0 | #REF! | #REF!
Circle | [5 empty] | 0 |  | 0
PBR | [5 empty] | 0 | #REF! | #REF!
Circle | [5 empty] | 0 |  | 0
JMN | [5 empty] | 0 | #REF! | #REF!
Circle | [5 empty] | 0 | #REF! | #REF!
BHJ | [5 empty] | 0 | #REF! | #REF!
Circle | [5 empty] | 0 | #REF! | #REF!
JND | [5 empty] | 0 | #REF! | #REF!
Circle | [5 empty] | 0 |  | 0
BVN | [5 empty] | 0 | #REF! | #REF!
Circle | [5 empty] | 0 | #REF! | #REF!
BTD | [5 empty] | 0 | #REF! | #REF!
Circle | [5 empty] | 0 | #REF! | #REF!
AMR | [5 empty] | 0 | #REF! | #REF!
Circle | [5 empty] | 0 |  | 0
SNR | [5 empty] | 0 | #REF! | #REF!
Grand Total | 0 | 0 | 0 | 0 | 0 | 0
RJC | 0 | 0 | 2 | 1 | 6
RJR | 1 | 5 | 6 | 8 | 4
PBR | 1 | 0 | 5 | 1 | 0
JMN | 0 | 2 | 6 | 7 | 1
BHJ | 1 | 2 | 4 | 15 | 8
JND | 0 | 4 | 4 | 11 | 11
BVN | 0 | 6 | 5 | 7 | 3
AMR | 0 | 5 | 4 | 6 | 5
SNR | 0 | 0 | 9 | 4 | 1

## accd-2 (hidden)
PASCHIM GUJARAT VIJ COMPANY LIMITED REGD & CORP OFFICE, RAJKOT
ELECTRICAL ACCIDENTS DETAIL (Cummulative) | [11 empty] | 39508
No. | CIRCLE | DIVISION | S/div | Name of Victim | Date Of Accident | Details of accidents |  |  |  |  | Cause of Accident | Saftery Tools utilised or not? | Action taken against the defaulter
| 1 | 3 |  |  |  | Deprt |  | Outsider |  | FA
| 1 | 3 |  |  |  | FH | NFH | FH | NFH
1 | RJC | RCD-3 | RSD | Jasubhai Bhagwatsinh Rana | 28.04.07 |  | 1 |  |  |  | During restringing of broken LT wire of Ag. Group, suddely return power came and victim got shocked. | N.A. | N.A.
2 | RJC | RCD-1 | Prahlad Plot | L.Z.Goswami | 27.05.07 |  | 1 |  |  |  | While fixing of standard D.O. fuse in place of non standard D.O. fuse, victim got shocked. | N.A. | Disciplinary action against L.I. who was supervising the work is under process.
3 | RJC | RCD-3 | RSD | Buffalow | 10.05.07 |  |  |  |  | 1 | Snapping of Conductor | N.A. | N.A.
4 | RJC | RCD-1 | Prahlad Plot | Rajesh N. Sagathiya | 02.06.2007 |  |  | 1 |  |  | Victim climbed on pole for light repairing unauthorisedly. | N.A. | N.A.
5 | RJC | RCD-2 | Udhyognagar | Shaileshbhai D. Patadiya | 20.06.07 |  |  | 1 |  |  | Victim climbing on iron ladder came in contact with short circuited ceiling fan and got shocked. | N.A. | N.A.
6 | RJC | RCD-2 | Pradhuymannagar | Kushal Pankajbhai Darji | 23.06.07 |  |  | 1 |  |  | Victim came in contact with short circuited street light fixure and got shocked. | N.A. | N.A.
7 | RJC | RCD-2 | Bedinaka | Chandulal D. Prajapati | 23.06.07 |  |  |  | 1 |  | Victim came in contact with street light conductor snapped and got shocked. | N.A. | N.A.
8 | RJC | RCD-3 | Mavdi Road | Durlabhji Sambhubhai Agola & a cow | 18.06.07 |  |  | 1 |  | 1 | Snapping of LT conductor due to heavy wind and rain. | N.A. | N.A.
9 | RJC | RCD-3 | Kalawad Road | Poojaben B. Rajpara | 21.06.07 |  |  | 1 |  |  | Victim was drying clothes on iron wire which came in direct contact with open joint of flexible wire extended in her own house. | N.A. | N.A.
10 | RJC | RCD-3 | Mavdi Road | Cow | 02.06.07 |  |  |  |  | 1 | Snapping of Conductor | N.A. | N.A.
11 | RJC | RCD-3 | Madhapar | Buffalow | 19.06.07 |  |  |  |  | 1 | Snapping of Conductor | N.A. | N.A.
12 | RJC | RCD-3 | RSD | Cow | 21.06.07 |  |  |  |  | 1 | Snapping of Conductor | N.A. | N.A.
13 | RJC | RCD-3 | Mavdi Road | Cow | 22.06.07 |  |  |  |  | 1 | Snapping of Conductor | N.A. | N.A.
14 | RJC | RCD-3 | MRSD | Rameshbhai Madhabhai Sagathiya | 30.7.2007 |  | 1 |  |  |  | A Mechanical Accident, While working he fell down form the PSC pole due to Slip of legs. | NO | NO
15 | RJC | RCD-3 | MRSD | CALF | 2.7.2007 |  |  |  |  | 1 | Snapping of Conductor | N.A. | N.A.
16 | RJC | RCD-3 | MRSD | BUFFALO | 2.7.2007 |  |  |  |  | 1 | Leakage current in guarding wire passed through earthing to pole pit. A buffalow nearby wondering came in contact. | N.A. | N.A.
17 | RJC | RCD-3 | RSD | BUFFALO(RAVA GELA LAMBARIYA) | 8/07/2007. |  |  |  |  | 1 | Leakage Current Flow in Earthing G.I.Wire. | N.A. | T.C.Maint with Earthing
18 | RJC | RCD-3 | RSD | COW(BHARATBHAI SAMATBHAI KOLI) | 25/07/2007. |  |  |  |  | 1 | SNAPPING OF L.T.CONDUCTOR | N.A. | L.T.Maintenance
19 | RJC | RCD-3 | RSD | MAHESH CHHAGANBHAI KOLI | 30/07/2007. |  |  | 1 |  |  | Accidental contact with live electric wire / equipment | N.A. | N.A.
20 | RJC | RCD-2 | MCSD | Ragh ubhai Gobarbhai Bharvad | 13/08/07 |  |  | 1 |  |  | Victim came in contact with short circuited motor in his premises and got shocked. | N.A. | N.A.
21 | RJC | RCD-2 | BNSD | Rajubhai Nagjibhai Parmar | 18/08/07 |  |  | 1 |  |  | Victim came in contact with short circuited ceiling fan while repairing and met with F.A. | N.A. | N.A.
22 | RJC | RCD-3 | RSD | A buffalow | 10/08/07 |  |  |  |  | 1 | Snapping of Conductor | N.A. | N.A.
23 | RJC | RCD-3 | RSD | Sumitaben Chanabhai Uteriya | 31/07/07 |  |  | 1 |  |  | Due to Leakage power from faulty TV - Disc cable in the cabin of ironsheets. | N.A. | N.A.
24 | RJC |  |  | Vijaybhai Chanabhai Uteriya | -do- |  |  |  | 1 |  | -do- | N.A. | N.A.
25 | RJC | RCD-3 | RSD | A cow | 31.08.07 |  |  |  |  | 1 | Victim came in contact with GI wire in which leakagte currenmt flown due to heavy rain and wind. | N.A. | N.A.
26 | RJC | RCD-3 | KRSD | A cow | 31.08.07 |  |  |  |  | 1 | Victim came in contact with GI wire in which leakagte currenmt flown due to heavy rain and wind. | N.A. | N.A.
27 | RJC | RCD-3 | KRSD | Mustaq Ahmed Malik | 31.08.07 |  |  |  | 1 |  | Vic5tim came in contact with MMB which was installed on PSC pole. On account of cable insulations, biting by squirrels during rainy season, short circuit has occurred. Victim came in contact with MMB and got shocked due to induction. | N.A. | N.A.
28 | RJC | RCD-1 | MPSD | A cow | 24.09.07 |  |  |  |  | 1 | Victim came in contact with GI wire in which leakagte currenmt flown due to heavy rain and wind. | N.A. | N.A.
29 | RJC | RCD-2 | UNSD | Rajubhai keshabhai Parmar | 09.11.07 |  |  | 1 |  |  | While opening of mail female pin of flexcible extension wire of the motor which is in running condition, victim came in contact with live part of male pin portion and got shocked, result in fatal accident | N.A. | N.A.
30 | RJC | RCD-2 | UNSD | Nirubhai R Mehta | 12.11.07 |  | 1 |  |  |  | While attending complaint of three phase service, victim was fell down from LT pole (girder) as his grip of hand and leg to the pole was left and fell down hence got injured to both legs. | Yes | N.A.
31 | RJC | RCD-2 | UNSD | Diptiben Viralbhai Patel | 08.01.2008 |  |  | 1 |  |  | While using the domestic heater (immersion type), victim touched the water and got shocked | N.A. | N.A.
32 | RJC | RCD-3 | MPSD | 1. Gordhanbhai Sakhiya, | 12.01.2008 |  |  | 1 |  |  | Leakage current was passing through the fencing wire and victim came in contact with fencing wire. | N.A. | N.A.
32 | RJC | RCD-3 | MPSD | Lalitbhai Sakhiya | 12.01.2008 |  |  | 1 |  |  | Leakage current was passing through the fencing wire and victim came in contact with fencing wire. | N.A. | N.A.
33 | RJC | RCD-2 | UNSD | 1. Vimlaben S. Jaishwal | 19.02.2008 |  |  |  | 1 |  | While carrying out Iron cot on terrace, victim came in contact with live 11 KV line and got shocked. | N.A. | N.A.
33 | RJC | RCD-2 | UNSD | Sharmilaben P. Jaishwal | 19.02.2008 |  |  |  | 1 |  | While carrying out Iron cot on terrace, victim came in contact with live 11 KV line and got shocked. | N.A. | N.A.
34 | RJC | RCD-1 | KOTHARIYA ROAD | 1. Smt. Hansaben Harkantbhai Chauhan | 02.03.2008 |  |  | 1 |  |  | While spraying water to renovated own house, victim came in contact with electric board which was removed from wall. Victim tried to repair the same and by mistake, he came in live contact with the supply. | N.A. | N.A.
1 | RJR | Morbi | Shanala | Rameshbhai Bhaijibhai Tadvi | 24/04/2007 | 1 | 0 | 0 | 0 | 0 | Unbalance from Pole & Hence fall down to earth due to mechanical Injury accident occurred.
2 | RJR | Morbi | WT | Bhaveshbhai D Sitapara | 28/04/2007 | 0 | 1 | 0 | 0 | 0 | PSC Pole get broken from the bottom level & person fall down & hence accident occurred.
3 | RJR | Morbi | MT-1 | Lalitaben Natvarlal Nakum | 2007-01-05 | 0 | 0 | 0 | 1 | 0 | Leakage current through street light fixture.
4 | RJR | Morbi | WT | Bhikhalal Kanjibhai Makvana | 23/05/2007 | 0 | 1 | 0 | 0 | 0 | Reverse Current came in line from unknown appliance(Generator)/place & hence accident occurred.
5 | RJR | Morbi | MR | Bipinpal Sahdevprasad Gardia | 2007-01-06 | 0 | 0 | 1 | 0 | 0 | Short Circuit in internal premises of victim
6 | RJR | Morbi | Shanala | Buffallow | 2007-03-06 | 0 | 0 | 0 | 0 | 1 | Conductor Snapping
7 | RJR | Morbi | MR | Buffallow | 2007-05-06 | 0 | 0 | 0 | 0 | 1 | Leakage Current through LT Pole due to rubbibng of buffallow's horn
8 | RJR | Morbi | WT | Cow | 2007-05-06 | 0 | 0 | 0 | 0 | 1 | Short Circuit of Street Light Fixture of LT Pole
9 | RJR | Morbi | MR | Revuben Naranbhai Tundia | 2007-07-06 | 0 | 0 | 1 | 0 | 0 | Short Circuit in internal premises of victim
10 | RJR | Morbi | MT-1 | Cattle Bull 2 No (ધણ ખૂંટ) | 2007-07-06 | 0 | 0 | 0 | 0 | 1 | Leakage current through street light fixture.
11 | RJR | Morbi | MR | Asif Habib Sandhi | 15/06/2007 | 0 | 0 | 1 | 0 | 0 | Accidental contact with live wire while installing dish TV cable
12 | RJR | Morbi | MT-1 | Kesha Kuka Parmar | 16/06/2007 | 0 | 0 | 1 | 0 | 0 | Short Circuit in internal premises of victim
13 | RJR | Morbi | MT-1 | Cattle Bull 1 No (ધણ ખૂંટ) | 16/06/2007 | 0 | 0 | 0 | 0 | 1 | leakage current through earthing due to broken LT wire from T/C & neutral touched to the fabriction.
14 | RJR | Morbi | MT-2 | M.H.Shilu | 2007-08-07 | 0 | 1 | 0 | 0 | 0 | Mechanical Unbalance while coming down from pole & hence accident occurred.
15 | RJR | Morbi | MR | Buffallow | 2007-11-07 | 0 | 0 | 0 | 0 | 1 | Conductor Snapping
16 | RJR | Morbi | WR | Buffallow | 22/7/2007 | 0 | 0 | 0 | 0 | 1 | Leakage Current Through earth. (PM Report avaited)
17 | RJR | Morbi | TKR | He-Buffallow | 26/7/2007 | 0 | 0 | 0 | 0 | 1 | Leakage Current Through Earthing wire of T/C
18 | RJR | Morbi | WT | Buffallow | 28/7/2007 | 0 | 0 | 0 | 0 | 1 | Leakage Current Through Earthing wire of T/C
19 | RJR | Morbi | MR | Sukhabhai Tejabhai | 30/7/2007 | 0 | 0 | 1 | 0 | 0 | Insulation of service get damaged & leakage current flown through earthing wire
20 | RJR | Morbi | WT | Buffallow | 31/7/2007 | 0 | 0 | 0 | 0 | 1 | Bird Fault on 11 KV & leakage current flown through earth
21 | RJR | Morbi | WT | Buffallow | 2007-01-08 | 0 | 0 | 0 | 0 | 1 | Leakage Current Through earthing wire of T/C Centre
22 | RJR | Morbi | WT | Buffallow | 2007-03-08 | 0 | 0 | 0 | 0 | 1 | Leakage Current Through earthing wire of T/C Centre
23 | RJR | Morbi | MR | Buffallow | 2007-03-08 | 0 | 0 | 0 | 0 | 1 | Conductor Snapping
24 | RJR | Morbi | MR | Buffallow - 2 Nos. | 2007-05-08 | 0 | 0 | 0 | 0 | 1 | Conductor Snapping
25 | RJR | Morbi | MR | Buffallow | 2007-05-08 | 0 | 0 | 0 | 0 | 1 | Conductor Snapping
26 | RJR | Morbi | WR | Bullock | 17/8/2007 | 0 | 0 | 0 | 0 | 1 | Leakage Current Through T/c earthing
27 | RJR | Morbi | WT | Buffallow | 17/8/2007 | 0 | 0 | 0 | 0 | 1 | Leakage current Pass through Guy Wire Which Is Damaged By Buffalo
28 | RJR | Morbi | TKR | Buffallow | 30/08/2007 | 0 | 0 | 0 | 0 | 1 | due to heavy wind phase wire get detached from binding & touched to the c clamp of neutral wire & leakage current flown through earth wire due to wet land.
29 | RJR | Morbi | TKR | Buffallow | 21/09/2007 | 0 | 0 | 0 | 0 | 1 | An electric motor of pumping the water in house of Shri Shamji Moti Vishodiya get its body Short, a return power flows thro' a neutral wire & reaches at a T/C & from it the current flows thro' earth wire to a gnd. level of land & also due to moisture in a
30 | RJR | Morbi | W® | Sh. Bhupatbhai Khodabhai Bambhva | 3.10.2007 | 0 | 0 | 1 | 0 | 0 | While cutting branch of tree accidantly came in contact with near by 11 KV Line & get electric shock.
31 | RJR | Morbi | TKR | Cow | 21/11/2007 | 0 | 0 | 0 | 0 | 1 | 11 kv Chhattar (JGY) Feeders Top Clamp Conductor Snapped And Fall Down On Land (Between Loc. No.306,307) & That Time One No.Of Cow of Sh. Gajera Vijay D. At-Prabhunagar Pass- Out From That Place And Comes In To Contact With Live Wire
32 | RJR | RRD | Jasdan | Devram Devabhai Nakum | 2007-08-05 | 0 | 0 | 1 | 0 | 0 | Victim i.e. labour of contractor of GETCO while doing stringing of new 66KV line, climed live 11KV Kanpar Ag fdr & got Elect. Shock & fall down. | Yes | Accidental contect with live wire
33 | RJR | RRD | Shapar Veraval | Abuben Daudbhai Riyami | 2007-10-05 | 0 | 1 | 0 | 0 | 0 | Victim was checking DO fuse by taking line clear of 11KV Balaji fdr but return power came & he got Elect. Shock. | Yes | Any other Reson
34 | RJR | RRD | Shapar Veraval | Valiben Charan | 21/6/07 | 0 | 0 | 0 | 0 | 1 | Leakage in TC earthing |  | Accidental contect with live wire
35 | RJR | RRD | Vinchhiya | Amra Bhura Bharvad | 23/6/07 | 0 | 0 | 0 | 0 | 1 | Leakage in TC earthing |  | Accidental contect with live wire
36 | RJR | RRD | Vinchhiya | Raziyaben Hanifbhai Lohiya | 23/6/07 | 0 | 0 | 1 | 0 | 0 | Victim came in contact with water pump in his own premises
37 | RJR | RRD | Vinchhiya | Savshibhai Sondabhai | 25/6/07 | 0 | 0 | 0 | 0 | 1 | Cond. Snapping of 11KV Gadhala fdr |  | Snapping of Cond
38 | RJR | RRD | Paddhari | Khimabhai Raodevbhai | 30/6/07 | 0 | 0 | 0 | 0 | 1 | Leakage in TC earthing |  | Accidental contect with live wire
39 | RJR | RRD | Paddhari | Bavanjibhai Karmanbhai | 2007-01-07 | 0 | 0 | 0 | 0 | 1 | In heavy wind & rain LT line cable used as dropper & GI wire touched to c-clamp. & other end of cable broken & touched to lower end of guy wire & cow came in contact with guy wire. |  | Snapping of Cond
40 | RJR | RRD | Shapar Veraval | Jaluben Surabhai Tolia | 2007-05-07 | 0 | 0 | 0 | 0 | 1 | Leakage in TC earthing |  | Accidental contect with live wire
41 | RJR | RRD | Jasdan | Nathu chanabhai Chirodiya | 12.08.08 | 0 | 0 | 0 | 0 | 1 | Leakage in TC earthing |  | Accidental contect with live wire
42 | RJR | RRD | Jasdan | Veljibhai Kalubhai Kaviyad | 23.08.08 | 0 | 1 | 0 | 0 | 0 | Victim slept from the pole |  | Mechanical Accident
43 | RJR | RRD | Jasdan | Laghrabhai Sadurbhai Bharvad | 31.08.07 | 0 | 0 | 0 | 0 | 1 | Return Power came in T/C neutral and earthing due to deffective wiring of near by Industrial connection.
44 | RJR | RRD | Jasdan | Dipakbhai Ladhabhai Nagdadkiya | 8.09.07 | 0 | 0 | 1 | 0 | 0 | Victim eas doing some mischief with earthing wire climbing DP of Polarpar feeder & earthing wire touched jumper od DP. |  |  | Any other Reson
45 | RJR | RRD | Paddhari | Nagajibhai Haribhai Vala | 04.10.07 | 0 | 0 | 0 | 0 | 2 | Metalic fencing wire of the farm house touched Un authorised exteneded wire of AG connection at Targhadi village |  |  | Un authorised work
46 | RJR | RRD | Paddhari | Khengarbhyai Dayabhai Dafada | 09.10.07 | 1 | 0 | 0 | 0 | 0 | On request by victim JE has taken LCP of 11KV Sanosara feeder.but actually work was taken on hand on 11 KV water works feeder. Hence victim touched live wire of 11 KV ww fdr. |  |  | Accidental contect with live wire
47 | RJR | RRD | Jasdan | Vinodbhai A Vaniya | 15.10.07 | 0 | 1 | 0 | 0 | 0 | To attend jumper fault of Kamalpur AG fdr by mistake GO switch of other side was made OFF on main line,while power was ON,from 66 Kv kamaalpur S/S. Victime came in contact with live wire and Fell fown. |  |  | Accidental contect with live wire
48 | RJR | RRD | Jasdan | Panch Uka Gholakiya | 16.10.07 | 0 | 0 | 0 | 0 | 2 | Snapping of Conductor at Jungvad village. |  |  | Snapping of Cond
49 | RJR | RRD | Jasdan | Kum. Jalpaben Vinodrai Mehta | 13.11.07 | 0 | 0 | 0 | 1 | 0 | Because of Extended Balcony. Distance Bet. Balcony and 11 Kv line is less. Victim Came in Contact with this line.
50 | RJR | RRD | Shapar Veraval | Hansraj Savji Solanki | 10.8.07 | 0 | 1 | 0 | 0 | 0 | Acci took place due to leakage current of Neutral.
51 | RJR | RRD | Jasdan | Sh.Rajesh bhai.Vibha bhai Vakatar | 7.12.07 | 0 | 0 | 1 | 0 | 0 | Victim lifted Galvenised pipe upward & This pipe came in contact with 11 kv Virnagar Ag feeder |  |  | Any other Reson
52 | RJR | Dhoraji | Dhoraji (R) | Dinesh Ruda Manvar | 26.03.07 | 0 | 0 | 1 | 0 | 0 | Labour of civil contractor when taking iron pipe from machdo touch the 11 KV line and leakage current pass through body of victim
53 | RJR | Dhoraji | Upleta (T) | Rajendra Babubhai Gadiyal | 07.04.07 | 0 | 1 | 0 | 0 | 0 | Victim claimb another feeder for which line clear was not taken by his own mistake.
54 | RJR | Dhoraji | Jetpur (T) | Jyotsnaben Hakabhai Bhadeliya | 08.04.07 | 0 | 0 | 0 | 1 | 0 | Due to sparking between two conductors it was broken and fallen on wires of the clothes drying. Hence a leakage current passes through this cloth drying wire.Victim contact with this wire and FA occurred.(In Private Premises)
55 | RJR | Dhoraji | Jetpur (R) | Sonalben Kamleshbhai Dobariya | 20.05.07 | 0 | 0 | 1 | 0 | 0 | Accident in private premises
56 | RJR | Dhoraji | Jetpur (R) | FA to bullock of Sh. Ramnikbhai Mandanbhai Radadiya | 20.06.07 | 0 | 0 | 0 | 0 | 1 | Due to snapping of conductor
57 | RJR | Dhoraji | Jetpur (T) | FA to Cow of Sh. Bhikhabhai Bhurabhai | 20.06.07 | 0 | 0 | 0 | 0 | 1 | Leackage of earthing in TC
58 | RJR | Dhoraji | Bhayavadar | FA to Cow without owner | 21.06.07 | 0 | 0 | 0 | 0 | 1 | Due to Burning of insulation of street light wire and touch to socate and leackage current passes through girder pole.
59 | RJR | Dhoraji | Dhoraji (R) | FA to bullock of Sh. Subhashbhai Laljibhai | 27.06.07 | 0 | 0 | 0 | 0 | 1 | Due to heavy wind pressure LT line pole was broken & fallen on earth with broken LT line wire & bullock contact with this LT line wire.
60 | RJR | Dhoraji | Dhoraji (T) | Ashwin I. Chauhan (Helper) | 05.07.07 | 0 | 1 | 0 | 0 | 0 | Installation of terminal of CT's ACB deteriorated & came in contact to the structure, dead short circuit occurred resulted into heavy flesh. Face of victim was near ACB influenced that place & met with not fatal accident.
61 | RJR | Dhoraji | Jetpur (R) | Chhaganbhai R. Kochhra (Helper) | 11.07.07 | 0 | 1 | 0 | 0 | 0 | Fall down from PSC pole while stringing of 11 KV cond. At village Bava-Pipaliya
62 | RJR | Dhoraji | Jamkandorana | Smt. Raliyatben Hansrajbhai Dhanani | 14.07.07 | 0 | 0 | 1 | 0 | 0 | Contact with live snapped conductor
63 | RJR | Dhoraji | Jamkandorana | Smt. Labhuben Nathabhai | 14.07.07 | 0 | 0 | 0 | 1 | 0 | While trying to save Smt. Raliyatben Hansrajbhai who was already contct with live snapped conductor
64 | RJR | Dhoraji | Jamkandorana | Sh. Mahesh Ranchhod | 30.07.07 | 0 | 0 | 1 | 0 | 0 | An outsider person Shri Ramnikbhai Bhikhabhai Savaliya Was fixing 11K D.O. Fuse wire with the help of bamboo at that time 11 Kv main jumper was blowing off and touched to the pole channel of D.P.Structure and leakage current passes through earthing of DP.
65 | RJR | Dhoraji | Jamkandorana | FA to bull of Sh. Pramukh Gauseva Samaj Charel | 08.08.07 | 0 | 0 | 0 | 0 | 1 | R-Phase cable of LT line was burnt and melt which was touched to iron C-clamp, so the returned leakage current passing through T/C earthling wire,(there was rain fall at that time) the bull while passes near T/C structure and contact with earthling wire a
66 | RJR | Dhoraji | Upleta Rural | Sh. Naran Hamir | 03.08.07 | 0 | 0 | 1 | 0 | 0 | In agriculture farm while victim was working near T/C, his hand contact with earthing wire of T/C which was broken inside the ground and not seen out side ground , in this way due to return leakage current flowing through the earthing wire FA occurred to
67 | RJR | Dhoraji | Dhoraji Rural | FA to bullock of Sh. Devshi Ukabhai Paradava | 12.08.07 | 0 | 0 | 0 | 0 | 2 | Due to heavy wind and rain LT line conductor was broken and fallen down on earth while Sh. Devshibhai Ukabhai Paradva passes with his cart near this LT line and his both bullocks came in contact with the live conductor and got an electric shock and died.
68 | RJR | Dhoraji | Dhoraji Rural | Sh. C.S. Bhut (Helper) | 14.08.07 | 0 | 1 | 0 | 0 | 0 | For restringing of LT line conductor, victim climbed on P.S.C. pole for removing of binding at that time pole is breaks & fall down. Hence accident is occurred.
69 | RJR | Dhoraji | Upleta Rural | FA to Buffalo of Sh. Rajesh Jeraj | 17.08.07 | 0 | 0 | 0 | 0 | 1 | Earthing wire of T/C was broken from earthing plate at under ground level buffalo of Sh. Rajeshbhai Jerambhai Ardeshana while passes near this T/C and came in contact with this broken earthing wire from which leakage current flow and got an electric shock
70 | RJR | Dhoraji | Jetpur Town | FA to buffalo of Sh. Naran Vira | 22.08.07 | 0 | 0 | 0 | 0 | 1 | LT cable burned on top of PSC pole so live cable terminal touched to the GI wire which is earthing of PSC pole so leakage current passed through the GI wire while buffalo of Sh. Naran Vira Rabari came in contact with this GI wire and got an electric shock
71 | RJR | Dhoraji | Jetpur Rural | FA to buffalo of Sh. Pragji Mohan | 05.09.07 | 0 | 0 | 0 | 0 | 1 | Transformer neutral failed hence leakage current flowing through the transformer centre earth wire and buffalo of Sh. Pragaji Mohan Paghdar while passes near the T/C and came in contact with earth wire of T/C and got an electric shock and died.
72 | RJR | Dhoraji | Dhoraji Rural | FA to buffalo of Sh. Amra Ala | 14.09.07 | 0 | 0 | 0 | 0 | 1 | On one LT line pole,10 span away from T/C, one LT line conductor, fall down from insulator & touch to "C"clamp, & earthed. Which make a leakage current flow from T/C earthing to that pole earthing. As the earth are watery & Buffalo came in contact with th
73 | RJR | Dhoraji | Dhoraji Town | FA to cow of Sh. Khodabhai Bhutabhai | 20.09.07 | 0 | 0 | 0 | 0 | 1 | Thread/Rag pulled by any resident of multistory building or may be flying of kite guide wire and L.T. live wire was wrilling to each other hence a leakage current flowing through the guide wire to the girder pole while a cow of Sh. Khodabhai Bhutabhai Bha
74 | RJR | Dhoraji | Bhayavadar | FA to Cow of Sh. Menshi Ramshi | 24.09.07 | 0 | 0 | 0 | 0 | 1 | On 11 KV pole of first span ahead agriculture T/C. A pin insulator was becomes faulty and broke out. Due to this 11 KV line conductor snapped from the binding of pin insulator and fallen on the V X Arm and due to shot circuit conductor was broken & fallen
75 | RJR | Dhoraji | Jetpur Rural | FA to bullock of Sh. Arafebbhai Ladhabhai | 25.09.07 | 0 | 0 | 0 | 0 | 1 | Due to deterioration of agriculture LT line conductor one of the phase conductor was broken near the C Clamp and fallen down on the ground. While Sh. Arfebbhai Ladhabhai passes with his bullock-cart near this LT line a bullock came in contact with live LT
76 | RJR | Dhoraji | Upleta ® | FA to bullock of Sh. Nandalal Dharamshi at Vill. Mervadar | 30.9.07 | 0 | 0 | 0 | 0 | 1 | A Big flying bird called "Varvangdu" was found in touching possition between P-P in Ag. LT Line hence P-P Short Circuit was occurred in LT line, Wire was broken and falling on the earth, Shri Nandlal passong with his bullock cart near this LT line and one
77 | RJR | Dhoraji | Dhoraji (R) | NFH to outsider Shri Keshavbhai Naranbhai Rathod at Vill. Kalana | 6.10.07 | 0 | 0 | 0 | 1 | 0
78 | RJR | Dhoraji | Jetpur Rural | NFH to human outsider Sh. Dinesh Lakharam Vanad at Vill: Thanagalol | 13.11.07 | 0 | 0 | 0 | 1 | 0 | Victim climbed on 11 KV pole for tapping work from existing 11 KV line, at that time victim has loosed his balance and fall down from this 11 KV line pole. Hence mechanical accident occurred.
79 | RJR | Dhoraji | Jetpur Rural | NFH to Human outsider Kum. Amita Haribhai Barvadia at vill: Mevasa | 16.11.07 | 0 | 0 | 0 | 1 | 0 | There is a residence building of Sh. Haribhai Parsotambhai Barvadia at village Mevasa. One 11 KV line is passing about 4 feet apart from the wall of this residence Sh. Haribhai Parsotambhai has constructed and extended three feet "RAVES" near the terrace.
80 | RJR | Dhoraji | Upleta Rural | NFH to Helper Sh. Amishkumar Maganlal ghodasara at vill : Khakhi - jalia | 27.12.07 | 0 | 1 | 0 | 0 | 0 | When victim climbed on LT line PSC pole for maintenance work at that time PSC pole was broken and fall down. Hence accident is occurred.
81 | RJR | Dhoraji | Jamkandorana | NFA to Bullock of Sh.Najubhai Bijalbhai Rabari at vill: Tarvada | 15.02.08 | 0 | 0 | 0 | 0 | 1 | 11 KV conductor broke down from load side of 11 KV Sanala JGY feeder and fell down on the earth. Due to this return power flew in the conductor. While shri Najubhai Bijalbhai were passing with his cart, his one no. of bullock came in contact with this bro
82 | RJR | GONDAL | TOWN | RAMBAHADUR LAKHAN MUKHIYA | 2007-01-30 | 0 | 0 | 1 | 0 | 0 | IT WAS OCCURRED DUE TO TRUCK STRIKE WITH LT LINE NUTRAL CONDUCTOR & THE LABOUR FALL DOWN FROM THE TRUCK
83 | RJR | GONDAL | TOWN | SONUBHAI NANDRAM VAGHELA | 2007-04-17 | 0 | 0 | 0 | 1 | 0 | THE VICTIM WAS DOING PAINTING WORK AND TOUCHED TO 11 KV LINE DURING WHILE PAINTING
84 | RJR | GONDAL | VASAVAD | SOMABHAI BHANABHAI | 2007-02-13 | 0 | 0 | 0 | 0 | 1 | DUE TO CONDUCTOR FALL DOWN AND TOUCHED TO C CLAMP AND IT POLE WAS EARTH. THE ANIMAL TOUCHED THE POLE
85 | RJR | GONDAL | VASAVAD | CHANDULAL UMIYASHANKAR | 2007-05-05 | 0 | 0 | 0 | 0 | 1 | DUE TO DROP OF CONDUCTOR FROM SHACKLE INSULATOR & CONDUCTOR TOUCHED THE COW
86 | RJR | GONDAL | KOTDA | Popatbhai Dungarbhai Kakadiya | 2007-05-20 | 0 | 0 | 1 | 0 | 0 | due person repairedd starter on his premises and touch to live wire
87 | RJR | GONDAL | KOTDA | Panchabhai Bachubhai Choriya | 2007-06-04 | 0 | 0 | 0 | 0 | 5 | due to leakage of earthing current at LST transformer
88 | RJR | GONDAL | RURAL | C.J.Jadeja (Helper) | 2007-06-12 | 0 | 1 | 0 | 0 | 0 | man was working on LT line and at that time LT line Touched to 11KV line at crossing of both line
89 | RJR | GONDAL | RURAL | Khenga Machha Ghodasara | 2007-06-28 | 0 | 0 | 0 | 0 | 1 | LT line touched to garding and due to that leakage current accident occured
90 | RJR | GONDAL | LODHIKA | Rupabhai Dayabhai Lal | 2007-07-02 | 0 | 0 | 0 | 0 | 1 | For Changing Faulty Transformer, While Line Inspecor Taking The L.C. the contractor's worker W/O. any Instruction climb on D.P. for removal of LT cable etc. (D.O. fuse was already removed at the time of T/C. fault) and victim (Contractor's worker ) touch
91 | RJR | GONDAL | RURAL | M.G. PAMBHAR(HELPER) | 2007-07-11 | 0 | 1 | 0 | 0 | 0 | While working on pole he fall down from pole
92 | RJR | GONDAL | LODHIKA | MANSUKH PREMJI RAKHOLIYA | 2007-06-26 | 0 | 0 | 1 | 0 | 0 | While Stringing ofL.T.line
93 | RJR | GONDAL | LODHIKA | ATUL PARSHOTAM LILA | 2007-06-26 | 0 | 0 | 1 | 0 | 0 | While Stringing ofL.T.line
94 | RJR | GONDAL | LODHIKA | Mansukh Batuk Vora | 2007-06-26 | 0 | 0 | 0 | 1 | 0 | While Stringing ofL.T.line
95 | RJR | GONDAL | LODHIKA | KantilalBatuk Vora | 2007-06-26 | 0 | 0 | 0 | 1 | 0 | While Stringing ofL.T.line
96 | RJR | GONDAL | LODHIKA | D.M.Damor | 2007-06-26 | 0 | 1 | 0 | 0 | 0 | While Stringing ofL.T.line
97 | RJR | GONDAL | RURAL | MANISHBHAI JAGDISHBHAI CHAUHAN | 2007-06-19 | 0 | 0 | 0 | 1 | 0 | Boy named manish climbed on pole to Catch dove & Shocked
98 | RJR | GONDAL | RURAL | BABU BHANU SARVAIA | 2007-07-31 | 0 | 0 | 0 | 0 | 1 | Shackle insulator of 3 phase 3wireL.t Line Broken & that's why conductor scrap occures. Buffallow puts its leg on it & died at the place
99 | RJR | GONDAL | RURAL | Bhalani Jiva Kachad | 2007-08-10 | 0 | 0 | 0 | 0 | 2 | There is a100 kva transformer for royal cement industries LT connection. Due to any how reason in consumers premises, leakage current flows in transformers earthing.there is a mud and water near transformer surrounding area,buffalow & cow passes near it ,
100 | RJR | GONDAL | RURAL | Gulab Klayan Jadeja | 2007-08-11 | 0 | 0 | 0 | 0 | 1 | IN LT LINE OF W.W. CONNECTION, LT LINES CEMENT POLE BECOME CROSS DUE TO HEAVY WIND, THAT’S WHY LT LINE LIVE WIRE & ITS GUARDING FROM AGLT LINE TOUCHED & LEAKAGE CURRENT PASSES THROUGH POLE'S EARTHINGMUD & WATER LYING NEAR POLES SURROUNDING, COW PUT ITS
101 | RJR | GONDAL | RURAL | Sava Sura Khit | 2007-08-15 | 0 | 0 | 0 | 0 | 1 | in L.T. Line of 25kv Shivarajgadh feeder at ninth pole from T/C L.T. Conductor slip down from shackle insulator to C - Clamp that’s why leackage current flows through transformer earthing Buffallow Goes near transformer & touched with earthing & Get elect
102 | RJR | GONDAL | Kotda | Bhada Ravji Savaliya | 2007-09-05 | 0 | 0 | 0 | 0 | 1 | Load Side Jumper touched to tapping angle & leakage Current Passed
103 | RJR | GONDAL | Lodhika | Raniben Tikhabhai Charan | 2007-09-16 | 0 | 0 | 1 | 0 | 0 | Accident Occurred Due to LT shackle pole guy is released from ground because of rain season the LT line span being loosed Distance from ground is about 3to 4feet it may be possible the victim touch to lt line & accident may be occurred.
104 | RJR | GONDAL | Lodhika | Praful Bhai Vasantji Vyas | 2007-09-25 | 0 | 0 | 0 | 0 | 1 | L.T. Line Main Wire Of Fuse Box is Breaked & Touched to Guy Clamp. Guy Wire is Bound to Telephone Pole with wire so Telephone pole is shocked . Horse touched to telephone pole & Shocked.
105 | RJR | GONDAL | LABORATORY | DHIRUBHAI MODHAVANIYA | 2007-08-17 | 0 | 1 | 0 | 0 | 0 | Blast due to shortening of PT link whil e working
106 | RJR | GONDAL | VASAVAD | BHARATBHAI KESHABHAI KHUNT | 2007-09-02 | 0 | 0 | 0 | 0 | 2 | Due to break down of conductor which falls on earth and two bullocks are passed through it and so due to shock two bullocks has been died
107 | RJR | GONDAL | LODHIKA | Rameshbhai Paru | 10.9.2007 | 0 | 0 | 1 | 0 | 0 | Due to snapping of conductor
108 | RJR | GONDAL | KOTDA | Nareshbhai Mangaldas Asari | 12.10.2007 | 0 | 1 | 0 | 0 | 0 | While carrying out the work on the transformer center he might have fell down to the land.
109 | RJR | GONDAL | GONDAL (T) | Salimbhai Pathan | 17.11.07 | 0 | 1 | 0 | 0 | 0 | During Maintenance work by mistake retain is contect with 11 KV Line and he was socked
110 | RJR | GONDAL | GONDAL (T) | Maganbhai Dayabhai Savaliya | 17.11.07 | 0 | 0 | 0 | 0 | 1 | Because of conductor failed on bufallow by mistake of children playing with thread which was shock on LT line
111 | RJR | GONDAL | KOTDA | Laljibhai Devshibhai Mevada | 25.11.07 | 0 | 0 | 1 | 0 | 0 | At the time of shock this son with jumping hence of victim where such the with live 11 Kv conductor and we volt shock
112 | RJR | GONDAL | GONDAL (T) | Vinod Ashokbhai Solanki | 07.12.07 | 0 | 0 | 0 | 1 | 0 | At the time of cutting leavs of tree victim was touched with live 11 KV conductor and he was shocked
113 | RJR | GONDAL | KOTDA | Kanubhai Jivabhai Makwana |  | 1 | 0 | 0 | 0 | 0 | To Avoid Bird fault problem on 11 Kv Nana Mandwa Ag. Feeder, it was planned to provide 11 Kv support pin below jumpers of Girder D.P. After switching off the feeder, victim climbed Gurder pole DP along with safety belt and helmet. While sitting on DP stru
114 | RJR | MORBI | SHANALA | Sh. JETHABHAI RUDABHAI | 16-3-2008 | 1 | 0 | 0 | 0 | 0 | In The LT Circuit of Modern Hall T/C Between Two LT Pole There is Guarding provided under LT Line. Below this LT Line’s guarding Dish TV Cable is crossing at mid span. This Dish TV cable was found tight at the time of inspection (visiting the site) & due | - | -
1 | PBR | KSD-I | Malia | Sarman Ram Khambhala | 2007-04-09 |  |  |  | 1 |  | Non Fatal Accident Due To Brekage Of T/C Dp At Village Amrapur
2 | PBR | PBR (O&M) | Coastal | Maliben Chanabhai Makwana | 2007-05-02 |  |  |  | 1 |  | Non Fatal Accidentl Occured Due Leakage Current In Wiring In Her Premises At Village Baradia.
3 | PBR | PBR (O&M) | Coastal | Jisgnesh Shivram Joshi | 2007-05-07 |  |  |  | 1 |  | Non Fatal Accidentl Occured At Time Of Attending Lt Service Fault By Private Person At Village Khapat
4 | PBR | PBR (O&M) | Bantwa | Prafulbhai Babubhai Chorvada | 2007-05-08 |  |  | 1 |  |  | Accidently Touching With 11 Kv Line During Unloading Of Marriage Luggage From The Truck At Vill. Limbuda.
5 | PBR | KSD-I | KeshodR-1 | Harsukh Ruda Chhelavada | 2007-05-09 |  |  | 1 |  |  | Suspicious (Reason Under Investigation) At Villagerangpur
6 | PBR | KSD-I | KeshodR-2 | Buffalow - Sh. Haja J. Kangad | 2007-05-11 |  |  |  |  | 1 | Leakage Current In T/C Earth Wire
7 | PBR | PBR (O&M) | Kutiyana | Bullock of Shri Rambhai P. Babariya | 2007-05-27 |  |  |  |  | 1 | Snapping Of Conductor
8 | PBR | PBR (O&M) | Bagvadar | Buffalow - Sh. Rambhai Rajabhai | 2007-06-05 |  |  |  |  | 1 | Snapping Of Conductor
9 | PBR | KSD-I | Keshod-R-2 | Bullock of Safeb Haja Movadia | 2007-06-21 |  |  |  |  | 1 | Leakage Current In Lt Line Earth Wire
10 | PBR | KSD-I | Keshod-R-1 | Buffalow - Jagmal Vajshi Maru | 2007-06-21 |  |  |  |  | 1 | Leakage Current In Lt Line Earth Wire
11 | PBR | KSD-I | Keshod-T | Jayesh Hamirbhai Solanki | 2007-06-24 |  |  |  | 1 |  | Non Fatal Accident Due To Accidental Touching Of 11 Kv By Rod At Keshod Town
12 | PBR | KSD-I | Keshod-R-2 | Buffalow - Rasik Ramji Hadwani | 2007-06-24 |  |  |  |  | 1 | Leakage Current In Lt Line Earth Wire
13 | PBR | PBR (O&M) | Ranavav | Cow - Sh. Polabhai B. Rabari | 2007-06-25 |  |  |  |  | 1 | Snapping Of Conductor
14 | PBR | PBR (City) | PBR City | Babubhai Pamabhai Bardarshahi | 2007-06-26 |  |  | 1 |  |  | In Private Premises While Switching On Electric Motor
15 | PBR | KSD-I | KeshodR-1 | Parbatbhai Masribhai Chocha | 2007-06-26 |  |  | 1 |  |  | Fatal Accident Due To Snapping Of Lt Conductor At Village Revdra
16 | PBR | KSD-II | Chorwad | Buffalow - Bachu Jetha | 2007-06-28 |  |  |  |  | 1 | Leakage Current In Lt Line Earth Wire | NA | NA
17 | PBR | KSD-II | Chorwad | Hasmukhbhai Bachubhai Chauhan | 2007-06-22 |  | 1 |  |  |  | Nfh (Dep.) Occurred Due To Sliping Of Hand During At The Time Of Climbing Of Lt Line Girder Pole
18 | PBR | PBR (O&M) | Kutiyana | Rama Sarman Ratiya | 2007-07-03 |  |  | 1 |  |  | Fatal Human Accident (Os) Occurred At The Time Of Unauthorisedly Climbing Lt Line For Lungar Purpose
19 | PBR | KSD-I | Malia | Bullock (2 Nos.) - Harilal Thakarshi Bhoot | 2007-07-03 |  |  |  |  | 1 | Conductor Snapped
20 | PBR | PBR (O&M) | Kutiyana | Buffalo - Jinabhai Ranabhai Rathod | 2007-07-03 |  |  |  |  | 1 | Leakage Current
21 | PBR | KSD-II | Madhavpur | Buffalo - Tulsibhai Nanabhai | 2007-07-05 |  |  |  |  | 1 | Conductor Snapped | NA | NA
22 | PBR | PBR (O&M) | Coastal | Rambhai N. Ranavaya | 2007-07-07 |  | 1 |  |  |  | Non Fatal Mechnical Accidentl Occured At Time Of Maintenance Of Dist. Transformer Due To Self Unbalancing
23 | PBR | KSD-I | KSD-R-1 | Buffalow (2 Nos.) - 1. Ram Govind Bhuva 2. Mandan Devdan Herbha | 2007-07-08 |  |  |  |  | 1 | Conductor Snapped
24 | PBR | PBR (City) | PBR City | Nilesh Chandrakant Pandya | 2007-07-21 |  | 1 |  |  |  | Non Fatal Mechinical Accident Occurred To Departmental Person (Applm) Sliping Of Lags While Handing Over Tools To Lineman At The Time Of Climbing Of Psc Poles
25 | PBR | PBR (O&M) | Bagvadar | Shantiben Ranavaya | 2007-07-21 |  |  | 1 |  |  | Fatal Human Accident (Os) Occurred In Her Premises At The Time Of Using Own Electrical Applincies (Valona)
26 | PBR | KSD-II | Mangrol® | Dhansukh Ramji Vaja | 2007-07-22 |  |  | 1 |  |  | Fatal Accident Occurred To Os On Account Of Leackage Current In Private Premises Victim Came In To Contact With Leackage Area | NA | NA
27 | PBR | KSD-I | KSD-R-1 | Buffalo - Kanaksinh Ranbir Dodia | 2007-07-22 |  |  |  |  | 1 | Conductor Snapped
28 | PBR | PBR (O&M) | Bagvadar | Vinja Ranmal Chellar | 2007-07-28 |  |  |  | 1 |  | Leakage Current
29 | PBR | PBR (O&M) | Bagvadar | Bullock - Vinja Ranmal | 2007-07-28 |  |  |  |  | 1 | Leakage Current
30 | PBR | PBR (City) | PBR City | Bullock-Shri Deva parbat Kodiyatar | 2007-08-23 |  |  |  |  | 1 | Leakage Current
31 | PBR | KSD-II | Madhavpur | Kanajibhai M. Chamadiya | 2007-08-05 | 1 |  |  |  |  | BY mistake SBO switch "ON" Pata JGY Feeder on which victim was working after taking line clear.
32 | PBR | KSD-II | Chorwad | Bullock-Haji Gani Dosa Tawani | 2007-08-12 |  |  |  |  | 1 | LT Conductor Snapped
33 | PBR | KSD-II | Chorwad | Bufallow-Nagaji Naran | 2007-08-22 |  |  |  |  | 1 | LT Conductor Snapped
34 | PBR | PBR (O&M) | Ranavav | Manoj Rameshchandra | 2007-08-04 |  |  | 1 |  |  | Accident occurred due to defective wiring in private premises
35 | PBR | PBR (O&M) | Kutiyana | Shri Babulal Ravjibhai Tank | 2007-08-04 |  | 1 |  |  |  | while making "ON" 11 KV AB Switch, one bare strand of Cable wire damaged handgloves and current passes through palm.
36 | PBR | PBR (O&M) | Ranavav | Cow-Sh. Bharat Arfeb Karavadara | 2007-08-07 |  |  |  |  | 1 | Leakage Current
37 | PBR | PBR (O&M) | Ranavav | Buffalow-Sh. Vishal Lakha Kodiyatar | 2007-08-09 |  |  |  |  | 1 | LT Pole of village TC tillted , buffalow came in to contact with live wire
38 | PBR | PBR (O&M) | Coastal | Govindbhai Rajshibhai Solanki | 2007-08-10 |  |  | 1 |  |  | Fatal Accident Due To Snapping Of Lt Conductor At Village Miyani
39 | PBR | PBR (O&M) | Ranavav | Bufallow-Sh. Ruda Parbat Mori | 2007-08-10 |  |  |  |  | 1 | LT Pole tillted , buffalow came in to contact with live wire
40 | PBR | PBR (O&M) | Ranavav | Buffallow-Sh. Duda Karshan Odedara | 2007-08-10 |  |  |  |  | 1 | Leakage Current
41 | PBR | PBR (O&M) | Coastal | Smt. Jethiben Bhikhabhai Odedara | 2007-08-11 |  |  | 1 |  |  | Fatal Accident Due To Snapping Of Lt Conductor At Village Navagam
42 | PBR | PBR (O&M) | Coastal | Buffalow-Sh. Bhimbhai Menand Modhavadiya | 2007-08-11 |  |  |  |  | 1 | Leakage Current
43 | PBR | PBR (O&M) | Kutiyana | Bullock-Savdas Govind Bheda | 2007-08-21 |  |  |  |  | 1 | Leakage Current
44 | PBR | KSD-I | KSD-R-1 | Buffalow-Mansing Jivabhai Dodiya | 2007-08-04 |  |  |  |  | 1 | Leakage Current
45 | PBR | KSD-I | Malia | Buffalow-Harsukh Oghadbhai | 2007-08-07 |  |  |  |  | 1 | Leakage Current
46 | PBR | KSD-I | KSD-R-2 | Buffalow-Natha Bhaga Chavda | 2007-08-06 |  |  |  |  | 1 | Leakage Current
47 | PBR | KSD-I | Malia | Buffalow-Karsan Ruda | 2007-08-10 |  |  |  |  | 1 | Leakage Current
48 | PBR | PBR (O&M) | Coastal | Sheep (7 Nos.) - Lakha Parbat Mori | 2007-08-31 |  |  |  |  | 1 | Snapping Of Conductor
49 | PBR | KSD-I | KSD-R-1 | Bullok- Sh. Rama Bhikha | 2007-09-01 |  |  |  |  | 1 | Leakage Current
50 | PBR | KSD-I | KSD-R-1 | Buffalo-Sh. Mukesh Rata Jafara | 2007-09-01 |  |  |  |  | 1 | Snapping Of LT Conductor
51 | PBR | KSD-I | KSD-R-1 | Bullock- Sh. Bhima Vala Solanki | 2007-09-02 |  |  |  |  | 1 | Leakage Current
52 | PBR | KSD-I | KSD-R-1 | Bullock-Rambhai Karnabhai Dangar | 2007-09-11 |  |  |  |  | 1 | Leakage Current
53 | PBR | PBR (O&M) | Ranavav | Buffalo - Sh. Lakhaman Rana Odedara | 2007-09-21 |  |  |  |  | 1 | Leakage Current in earthing
54 | PBR | PBR (O&M) | Ranavav | Buffalo- Sh. Dhana Bhikhu Kodiyatar | 2007-09-22 |  |  |  |  | 1 | Snapping Of LT Conductor
55 | PBR | PBR (O&M) | Ranavav | Buffalo - Sh. Deva jetha Kodiyatar | 2007-09-24 |  |  |  |  | 1 | Leakage Current in load side wiring of Temp. Connection.
56 | PBR | PBR (O&M) | Coastal | Sh. Budhiya Khandu Thakare | 2007-09-27 |  |  | 1 |  |  | Insulation open in consumer's load side wiring. Victim may came in contcat with bare wire electrocuted.
57 | PBR | Keshod-II | Chorwad | Buffalo- Sh. Ramsinh Uka Barad | 2007-09-27 |  |  |  |  | 1 | Leakage Current
58 | PBR | PBR (City) | PBR (City) | Sh. Savajibhai Govindbhai Gadher | 2007-09-27 |  |  | 1 |  |  | accident occurred to Load side of the consumer switch board was as electrical motor was shot circuted the victim came in contact with said shot circuted switch board and got electrotuted
59 | PBR | PBR (O&M) | Ranavav | Sh. Karabhai Gigabhai Godhania | 14/10/07 |  |  | 1 |  |  | In victim's shop STD/PCO printer was short and that printer thouched to freeze hence current flow through body of freeze i.e. freeze short (As there is no any earthing of freeze) and victim touched the freeze and electrocuted.
60 | PBR | KSD-I | KeshodR-1 | Bullock-Shri Bharatbhai Haribhai Goriya | 24/10/07 |  |  |  |  | 1 | Leakage Current
61 | PBR | KSD-II | Mangrol (T) | Sh. B. B. Garchar | 26/10/07 |  | 1 |  |  |  | Telephonically line clear taken by Lineman of 11 KV Dudh talawadi Ag. Dom Feeder for repairing of TC lugs. By mistake 66 KV Mangrol S/S (GETCO) staff has taken out trolly of 11 KV Datar Manzil Ag. Dom. Feeder. Sh. B. B. Garchar (Victim) came in to contac
62 | PBR | PBR (O&M) | Bantwa | Harsur Lakhman Dangar -- Outsider Human | 30.10.07 |  |  | 1 |  |  | Existing Tatkal Connection of shri Harsur Lakhman Danger in vithal ruda mendapara AG group, As per letter of Police department on date 2/11/07 Site visit by DE Bantwa and investigate no any leakage current found in our installation but as per report of e
63 | PBR | KSD-I | Keshod(T) | 3 Nos. Cow --- 2 nos. of shri Narandas Gandhi Gaushala 1nd 1 no. Rovery | 06.11.07 |  |  |  |  | 1 | Due to Rain and wind pressure, L.T Line conductor snapped. All 3 nos Cow came in contact with live wire and electrocuted
64 | PBR | PBR(CITY) | Udyognagar | Out Sider Human - Jaynarayan Shukala | 05.11.07 |  |  | 1 |  |  | Accident occurred while reparing the single phase motor by victim in his premises.
65 | PBR | PBR(O&M) | Coastal | 3 Nos. Cow- 1). Shri Jaga Raja Shamla, 2). Shri Rama Gova Kodiyatar 3). Shri Kisa Bhikha Makwana | 17.11.07 |  |  |  |  | 1 | Due to failure of 11 KV Pin Insulator, 11 KV Conductor Snapped.
66 | PBR | Keshod-1 | Keshod(T) | Out Sider Human - Shri Dhirubhai Mavjibhai (Bhikhabhai) Pipaliya | 19.11.07 |  |  | 1 |  |  | Diring Checking of 3 Phase Power Supply in Kit Kat Fuse by victim in his Private Premises (Agriculture Installation)
67 | PBR | PBR(O&M) | Bagvadar | Departmental - Person - Shri Jagdish M. Vasava - Helper -- Age 40 Years | 22.11.07 |  | 1 |  |  |  | Mechanical Accident Occurred to him due to broken down of LT Psc Pole.
68 | PBR | Keshod-1 | KeshodR-2 | Out Sider Human - Shri Nalinbhai Parshotam Gajera (Age Approx.:- 34 Years) | 24.11.07 |  |  | 1 |  |  | Diring Checking of Power Supply in Kit Kat Fuse by victim in his Private Premises (Agriculture Installation)
69 | PBR | PBR(O&M) | Ranavav | Buffalo - of Shri Bhima Foga Khunti at Village Adityana | 12.12.07 |  |  |  |  | 1 | Leakage Current
70 | PBR | Keshod-1 | Malia | Buffalo of Shri Vikram Rambhai at Village Malia Hatina | 08.01.08 |  |  |  |  | 1 | Leakage Current
71 | PBR | PBR(O&M) | Bagvadar | Outsider Human - Shri Safeb Raja Odedara at Village Bhetakadi | 21.11.07 Reported by EE(O&M) on dated 08.01.08 |  |  | 1 |  |  | Un- Authorised work on Live LT Line by Victim
1 | JMN | kmbl | Bhatia | A Bullock | 2007-04-11 | - | - |  |  | 1 | Due to snapping of neutral conductor from 'c' clamp the conductor falls on bullock and acci. occurred.
2 | JMN | City-2 | Rural S/dn | Shri S.V.Solanki | 2007-05-08 | - | 1 |  |  |  | Burnt 11 kv jumper touched to nearby live 11 kv line due to heavy wind.
3 | JMN | City-1 | Sat Rasta | A Bullock | 2007-05-20 | - | - |  |  | 1 | Leakage current flows, buffalo came in contact with live wire & accident occurred.
4 | JMN | City-2 | Sikka | Goat | 2007-05-20 | - | - |  |  | 1 | Due to Snapping of LT conductor, accident occurred.
5 | JMN | rural | J.J.(E) | A Bullock | 2007-06-01 | - | - |  |  | 1 | Due to Snapping of LT conductor, accident occurred
6 | JMN | rural | Lalpur | Jayantibhai Pithadbhai Chavda | 03.06.07 | - | 1 |  |  |  | During the repairing work on electrical line the deteriorated v-cross arm, clamp broken & victim lost his balance from pole & fall down to earth
7 | JMN | kmbl | Kmbl(T) | Rasiklal Damji | 2007-06-04 | - | - | 1 |  |  | While curing on newly constructed house, victim came in contact with LT line passing above the house ceiling due to wet surface
8 | JMN | City-2 | Ind | A Bullock | 05.06.07 | - | - |  |  | 1 | Due to the fault in 70 mm2 cable which was tied with top angle, leakage current flow through girder pole and earth wire.
9 | JMN | City-2 | Ind | Two Cows | 05.06.07 | - | - |  |  | 1 | Due to heavy wind and rain live joints of service came in contact with connection and leakage current passed through metal fuse box and victim came in contact with stay of girder pole and accident occurred
10 | JMN | rural | Lalpur | Nalinbhai R.Chauhan | 07.06.07 | - | 1 |  |  |  | Made mistake in isolating the line during maintenance work on 11 kv Arikhana feeder he isolated 11 kv Gafeba feeder instead of 11kv Arikhana feeder
11 | JMN | City-1 | Hapa | Shri Haribhai & Smt. Nathiben | 07.06.07 | - | - | 1 |  |  | While unknown vehicle passes under the HT line it pulled & damage the line, there by reducing clearance between ground and 11kv wire. During this period, bullock cart has also passed beneath the line and while passing has touched 11kv line & accident occu
12 | JMN | City-1 | Hapa | Two Bullock | 2007-06-07 | - | - |  |  | 1
13 | JMN | City-1 | Sat Rasta | A Cow | 2007-06-16 | - | - |  |  | 1 | Due to falling of tree on LT line, conductor snapped.
14 | JMN | City-1 | Hapa | Shri Mamta Vijaybhai | 19.06.07 | - | - | 1 |  |  | Direct wire tapped by Ashoksinh from LT line, the joint of unauthorized wire touches with fencing of Ag. farm while playing victim she touches with fancying wire and accident occurred
15 | JMN | kmbl | Dwarka | Aanandi Dhanjibhai | 20.06.07 | - | - |  | 1 |  | Due to defective internal house wiring, victim got electric shock
16 | JMN | rural | Lalpur | A Buffalo | 21.06.07 | - | - |  |  | 1 | One phase-wire was broken at a place where cable comes out from dist-Box, Buffalo came in contact with that T/C and accident occurred.
17 | JMN | City-2 | Sikka | A Cow | 21.06.07 | - | - |  |  | 1 | A cow passed near broken conductor and touched and accident occurred
18 | JMN | rural | Kld(E) | A Bullock | 23.06.07 | - | - |  |  | 1 | LT conductor snapped. Bullock came in contact with conductor and accident occurred
19 | JMN | City-2 | Sikka | A Bullock & A Calf | 23.06.07 | - | - |  |  | 1 | Snapping of LT conductor
20 | JMN | kmbl | Bhanvad | A Bullock | 24.06.07 | - | - |  |  | 1 | From Transformer bushing neutral lug found disconnected and due to same leakage current flow in earthing wire
21 | JMN | rural | Kld(E) | Bharatsinh | 26.06.07 | - | - | 1 |  |  | While giving jumper on 11 kV line after completion of line work, the victim got shock on 11 kv line
22 | JMN | City-2 | Rural | Mahesh Trikambhai Bhadra | 28.06.07 | - | - | 1 |  |  | Due to snapping of LT conductor accident occurred
23 | JMN | kmbl | Okha | A Buffalo | 03.07.07 |  |  |  |  | 1 | Leakage of TC earthing
24 | JMN | City-2 | Rural | Two Buffalo | 05.07.07 |  |  |  |  | 1 | Damage of LT line due to heavy rain and accd. Occurred.
25 | JMN | City-2 | Sikka | A Buffalo | 05.07.07 |  |  |  |  | 1 | Snapping of LT conductor
26 | JMN | City-2 | Sikka | febvi Bharatbhai | 05.07.07 |  |  | 1 |  |  | Snapping of LT conductor
27 | JMN | kmbl | Kalyanpur | A Bullock | 09.07.07 |  |  |  |  | 1 | Snapping of LT conductor
28 | JMN | kmbl | Bhanvad | Ramesh Kana | 09.07.07 |  |  | 1 |  |  | Snapping of LT conductor
29 | JMN | kmbl | Rural | Kababhai Rajsinh | 11.07.07 |  |  | 1 |  |  | Victim climbed on live LT line at his own wish and met with fatal accd.
30 | JMN | City-1 | HT | Atul Bhagvanji Kapuria | 14.07.07 |  |  |  | 1 |  | While touching to 11 kv line from extended Gallery on Road from Building.
31 | JMN | kmbl | Kalyanpur | Hardasbhai Rabari | 14.07.07 |  |  | 1 |  |  | Victim has tried to take unauthorized power supply from existing overhead village L.T. line.
32 | JMN | rural | Kalavad(E) | N.K.Jadeja | 20.07.07 |  | 1 |  |  |  | Mechanical Accident.
33 | JMN | kmbl | Dwarka | A Bullock | 24.07.07 |  |  |  |  | 1 | Snapping of LT conductor
34 | JMN | City-2 | Kmbl Gate | Yunus Dosa | 25.07.07 |  |  | 1 |  |  | Supprot GI wire connected between LT pole and street light fixture fixed on private premises, was came in contact with live phase junction on LT Pole, consequently leakage current passed through said GI wire.Thus electrocution was took place when victim c
35 | JMN | City-1 | Hapa | A Buffalo | 31.07.07 |  |  |  |  | 1 | Snapping of LT conductor
36 | JMN | rural | Lalpur | A Buffalo | 31.07.07 |  |  |  |  | 1 | Earthing is not provide proper, hence leakage flows from earth to earth. When she buffalo came in contact with earth surface and accd. Occurred.
37 | JMN | Rural | Jodia/Rural | Uttam Savji Dudhagara | 01.08.07 |  |  | 1 |  |  | There is no anyposibility of electrical accident.
38 | JMN | kmbl | Bhatia S/dn./Kmbl | Shri Ghanshyam K. Solanki | 02.08.07 |  | 1 |  |  |  | for the operation of GO switch while climbing on 11 kv pole, the victim slipped and fall down mechanical accident.
39 | JMN | kmbl | Bhatia S/dn./Kmbl | Umeshbhai N.Manek | 04.08.07 |  |  | 1 |  |  | The building was constructed Nr. LT line and clearance not maintained while victim climbed on tarace for some work, came in contact with live LT line & accd. Occurred.
40 | JMN | rural | Kld(E)/Jam®dn. | A Cow | 07.08.07 |  |  |  |  | 1 | Due to unbinding of live phase wire from shackle ins. & touching with c-clamp. As it is rainy season whole pole was completely wet and thus pole was shorted. Cow came in contact with the pole and got ele. Shock.
41 | JMN | City-I | Ptl S/dn./City Dn. | A Buffalo | 09.08.07 |  |  |  |  | 1 | A Buffalo was shocked due to transformer's leakage current of neatural earthing.
42 | JMN | rural | J.J'pur(E)/Rural | Shri Arvind Chakubhai | 10.08.07 |  |  | 1 |  |  | while repairing tapping 11 kv line privately way. Victim fall from the pole and died due to hamerage.
43 | JMN | kmbl | Bhatia/Kmbl | A Buffalo | 10.08.07 |  |  |  |  | 1 | Phase cond. binding with sheckle insulator was loosen and conductor touches to angle of pole. Water is surrounded to pole as the buffalo fall in water it electrolucted.
44 | JMN | rural | Dhrol S/dn./Rural dn. | A Buffalo | 10.08.07 |  |  |  |  | 1 | T/C was surrounded by water due to leakage current from LT dist.Box as buffalo fall in water it electrolucted.
45 | JMN | kmbl | Kmbl(R)/Kmbl. | Smt. Manjuben Karubhai Mokaria | 12.08.07 |  |  | 1 |  |  | Due to heavy wind, and rain binding of LT shackle insulator broken and LT live phase conductor touched PSC pole due to which leakage current was passing through earthing wire and victim came in contact with earthing wire and met with accd.
46 | JMN | kmbl | Bhatia/Kmbl | A Bullock | 12.08.07 |  |  |  |  | 1 | fault the cable touches the angle of LT line pole and through angle earthwire energized and as bullock came in contact with pole , accd. Occurred.
47 | JMN | kmbl | Kmbl(R)/Kmbl. | A Buffalo | 13.08.07 |  |  |  |  | 1 | Due to T/C body leakage current passed to earthing wire and animal came in contact with wire of transformer body.
48 | JMN | kmbl | Bhatia/Kmbl | A Buffalo | 14.08.07 |  |  |  |  | 1 | The LT phase conductor loosen from shackle binding it touches cross arm and thus pole earthwire energized while buffalo came in contact with pole earthwire and accd. Occurred.
49 | JMN | kmbl | Kmbl(R)/Kmbl. | Smt. Valiben Karsanbhai Chuchhar | 14.08.07 |  |  | 1 |  |  | Due to breaking of shackle insulator, of LT line pole due to rain and wi9nd presence LT line conductor fall down from pole to ground level. The victim came in contact with this LT conductor and accd. Occurred.
50 | JMN | kmbl | Kmbl(R)/Kmbl. | She Buffalo | 15.08.07 |  |  |  |  | 1 | LT phase wire Ag. Line broken and snapped. Buffalo came in contact with snapped cond. And met with accident.
51 | JMN | rural | Kld(E)/Rural | A Bullock | 16.08.07 |  |  |  |  | 1 | while bullock coming back after drinking from river, it came in contact with live LT wire which were laying on earth due to broken pole by heavy rain and flood. Got ele. Shock and accd. Occurred.
52 | JMN | rural | Kld(E)/Rural | A Buffalo | 16.08.07 |  |  |  |  | 1 | while buffalo was grazing near bank of small river, it came in contact with live LT wire which were laying on earth due to broken pole by heavy rain and flood.
53 | JMN | City-II | Rural S/dn/City-2 | A Buffalo | 16.08.07 |  |  |  |  | 1 | Snappinf of LT conductor
54 | JMN | kmbl | Okha/Kmbl | A Camel | 16.08.07 |  |  |  |  | 1 | Due to heavy rain pole slipped and bend 11 kv line from foundation and hence clearance between ground and conductor reduces as the camel came in contact with wire and accd. Occurred.
55 | JMN | kmbl | Kmbl(T)S/dn./Kmbl | Shri D.D.Parmar | 17.08.07 |  | 1 |  |  |  | The victim was alloted to attend the complain of Jalin Petrol pump while attending the complain on transformer , LT line side the victim came in vicinity of HT line passing above LT line and electrocuted and fall from T/C.
56 | JMN | City-II | Rural S/dn/City-2 | Shri Ahir R.J. | 21.08.07 |  |  |  | 1 |  | Due to heavy rain the pole was fall down and the live LT wires were fall on the victim she
57 | JMN | kmbl | Bhatia/Kmbl | A Buffalo | 22.08.07 |  |  |  |  | 1 | Due to leakage of LT wire and earth wire, buffalo came in contact with leakage wire and got shocked.
58 | JMN | rural | Kld(E)/Rural | Shri Samji Valji Vasoya | 23.08.07 |  |  | 1 |  |  | Internal wiring fault at consumer's premises.
59 | JMN | City-II | Rural/City-II | A Buffalo | 23.08.07 |  |  |  |  | 1 | Due to T/C body leakage current passed to earthing wire and animal came in contact with wire of transformer body.
60 | JMN | kmbl | Dwarka/ Khambhalia | A Buffalo | 24.08.07 |  |  |  |  | 1 | Snapping of LT Conductor.
61 | JMN | City-II | Sikka/City-II | A Buffalo | 25.08.07 |  |  |  |  | 1 | Due to leakage of earth wire buffalo came in contact with earth wire and accd. Occurred.
62 | JMN | City-II | Sikka/City-II | (1)Uttamshinh, (2) Raijibhai | 25.08.07 |  |  |  | 1 |  | Due to heavy rain and wind pin H/W of D.P. touch to other JGY pipali feeder and both are getting shock.
63 | JMN | kmbl | Bhatia/Kmbl | Kanabhai Rajabhai Odedara | 26.08.07 |  |  | 1 |  |  | suspected case of electrical accident. The victim was covering the material of truck parked under 11 kv line. He might have come in visinity of line and fall down from truck.
64 | JMN | rural | J.J(E)/Rural | A Buffalo | 28.08.07 |  |  |  |  | 1 | Due to leakage current of T/C earthing, buffalo came in contact with wire and accd. Occurred.
65 | JMN | rural | Dhrol S/dn./Rural dn. | Lakhman Keshavji Mungra | 28.08.07 |  |  | 1 |  |  | Internal wiring fault at consumer's premises.
66 | JMN | City-II | Rural/City-II | A Buffalo | 28.08.07 |  |  |  |  | 1 | Snapping of HT line buffalo came in contact with wire and accd. Occurred.
67 | JMN | City-I | Ptl S/dn./City Dn. | A Cow | 29.08.07 |  |  |  |  | 1 | cable shorted, leakage current pass through earthing wire, cow came in contact with leakage wire accd. Occurred.
68 | JMN | rural | Kld(E) | A Bullock | 05.09.07 |  |  |  |  | 1 | Snapping of LT conductor
69 | JMN | kmbl | Dwarka | 3 nos. of Buffalo | 05.09.07 |  |  |  |  | 1 | illegally Power tapped from an unauthorised persons through bambu & cable system, as the buffalo rubbed,its body with pole,its body came in contact with illegally tapped cable & Electrolux
70 | JMN | kmbl | Kalyanpur | Ramde Jaga Bhadarka | 08.09.07 |  |  | 1 |  |  | in the premise of victim, when victim goes to start hils ele. Motor at open covered starter, in a room, one phase comes in contact with fingers of the hand and he got ele. Shocked.
71 | JMN | City-II | Sikka | Two Cows | 08.09.07 |  |  |  |  | 1 | Snapping of LT Conductor
72 | JMN | kmbl | Bhanvad | Buffalo | 14.09.07 |  |  |  |  | 1 | Snapping of LT Conductor
73 | JMN | City-II | Rural S/dn | An ox | 15.09.07 |  |  |  |  | 1 | Snapping of LT Conductor
74 | JMN | City-II | Sikka | A Buffalo | 25.09.07 |  |  |  |  | 1 | Earthing leakage of T/C.Water was surrounded by T/C and as Buffalo fall in water it Electro lux
75 | JMN | kmbl | Kmbk® | A Bufflao | 27.09.07 |  |  |  |  | 1 | Leakage current drawn in GI earth wire, buffalo came in contact with wire & accd. Occurred.
76 | JMN | Rural | J.J.(E) | Dipak Ramji | 28.09.07 |  |  |  | 1 |  | While isolating G.O switch forT/C replacement, switch goes to earth and fire arc took place and acc. Occurred.
77 | JMN | Rural | J.J. | Two Buffalo | 29.09.07 |  |  |  |  | 1 | due to line fault 11 kv power flow in earthing as the land was wet and 2 nos buffalo were in water nearby above pole then electrolux.
78 | JMN | Rural | Lalpur | An ox | 29.09.07 |  |  |  |  | 1 | Snapping of LT Conductor
79 | JMN | rural | Lalpur | An ox | 02.10.07 |  |  |  |  | 1 | Snapping of LT conductor
80 | JMN | kmbl | Bhatia | A Cow | 07.10.07 |  |  |  |  | 1 | Snapping of LT conductor
81 | JMN | kmbl | Kmbl(R)/Kmbl. | Kariben Dhanabhai Gamar | 12.10.07 |  |  | 1 |  |  | Victim climbing for green tree cutting at village sutaria. An overhead 11 kv mota gunda ag feeder passing over the above neem tree. Due to that victim touches the live conductor of the 11 kv line. Hence, electric shock passing through her body and died at
82 | JMN | City-I | Hapa S/Dn./City-1 | A Buffalo | 24.10.07 |  |  |  |  | 1 | Snapping of LT conductor
83 | JMN | kmbl | Kmbl(R)/Kmbl. | Jodhabhai Karabhai | 27.10.07 |  |  | 1 |  |  | Victim touches live conductor of inclined LT line conductor hence electric current passes through the body of the boy and died at that time.
84 | JMN | kmbl | Kmbl(R)/Kmbl. | 5 nos.of buffalo | 27.10.07 |  |  |  |  | 1 | A Buffalo came for drinking water in lake after drinking water buffalo passed nearby land due to that buffalo touches live conductor of inclined LT line and accd. Occurred.
85 | JMN | City-I | Hapa S/Dn./City-1 | A Buffalo | 27.10.07 |  |  |  |  | 1 | Snapping of LT conductor
86 | JMN | City-I | Hapa S/Dn./City-1 | Rajesh Balvant Khat | 30.10.07 |  |  |  | 1 |  | Erection of Ag group for road crossing instead of 11 kv nagarsim feeder L/C asked/ issued for vijarkhi feeder hence victim got ele.shock(explanation asked from concern.)
87 | JMN | Kmbl | Kalyanpur | Jethiben Arfebbhai Khandhar | 05.11.07 |  |  |  | 1 |  | At the time of accident flow was single phasing and snapped cond. Was not live but the victim got ele. Shock due to induction of power in snapped cond.
88 | JMN | Rural | Kld.(E) | 4 nos. of Goats | 07.11.07 |  |  |  |  | 1 | Breakage of LT conductor from circuit pole. Mischief made by unknown person by cutting another side of broken conductor which was touching the live wire, goat came in contact with live wire & accd. Occurred.
89 | JMN | Kmbl | Bhanvad | Shri Nahim | 09.11.07 |  |  | 1 |  |  | A Fisherman named Nahim died when 11 kv conductor snapped on a boat in river Triveni Bhanvad.
90 | JMN | Kmbl | Dwarka | A Camel | 10.11.07 |  |  |  |  | 1
91 | JMN | Rural | J.J.(E) | A Buffalo | 19.11.07 |  |  |  |  | 1
92 | JMN | Rural | Kalavad(E) | Smt Kasurben Samsurbhai | 6.12.07 |  |  | 1 |  |  | Motor switch was foud opened during inspection in private premises
93 | JMN | Rural | Kalavad(E) | J B Damor | 5.1.08 |  | 1 |  |  |  | During the repalacement work of service wire on PSC pole, while stringing G.I.wire,victim lost his balance from pole & fall down to earth
94 | JMN | kmbl | Kalyanpur | Lakhman Devsi Gorania | 13.1.08 |  |  |  | 1 |  | Victim by self work to check power in kit-kat fuse of T/C and by mistake his hand touch accidentally live phase of kit-kat fuse and accident occurred
94 | JMN | City-1 | HT | Shri Jayrajsinh Vijaysinh | 14.01.08 |  |  |  | 1
95 | JMN | Kmbl | Kalyanpur | Shri Manishaben Keshubhai Solanki | 04.02.08 |  |  | 1 |  |  | In her home, victim was making tea in vessal on hot plate that time flow of tea occurred and she touch the vessal and she got electric shock & accident took place.
96 | JMN | kmbl | Bhatia | A Cow | 07.02.08 |  |  |  |  | 1 | Due to one current leading to breaking of coductor, which fall on cow & accd. Occurred.
97 | JMN | City-II | Rural | A Buffalo | 16.02.08 |  |  |  |  | 1 | Snapping of Conductor
98 | JMN | City-II | Sikka | Shri Nathabhai Karabhai Karamata | 21.02.08 |  |  | 1 |  |  | While cutting tree branches for food of his animals with the help of iron Rod, he came in contact with 11 kv phase wire through that rod and electrolux and died.
100 | JMN | Rural | JJ(W) | 3-nos. of Bufffalo | 01.03.08 |  |  |  |  | 1 | Snapping of Conductor
101 | JMN | kmbl | Bhatia | Ullasba Jayendra Sinh Jadeja | 03.03.09 |  |  | 1 |  |  | Victim was trying to start house floormill & accidently got electric shock
1 | BHJ | Anjar | Anjar® | Babu jesang Khungal | 2007-04-04 |  | 1 |  |  |  | Mechanical accident, fall down from Pole
2 | BHJ | Mandvi | Mundra | V.P.Siyani | 06.4.07 |  |  | 1 |  |  | Came in contact with live HT line
3 | BHJ | G'DHAM | Adipur | Nitin Arafebdas Kapta | 09.04.07 |  |  |  | 1 |  | Snapped cond. Lying on road victim on motorcycle, he applied the breaks & slipped. | NA | snapped cond. Joined
4 | BHJ | Bhuj | NAKHATRANA | RAJESH NARSHI NUT | 25/06/2007 | - | - | 1 | - | - | Due to heavy wind pressure tree branch Fall down on L.T. circuit,phase & neutral short circuited & conductor snapped on the victim, resulted into fatal accident | Not Applicable | Not Applicable
5 | BHJ | Bhuj | NAKHATRANA | COW | [5 empty] | 1 | Snapping of Conductor | Not Applicable | Not Applicable
6 | BHJ | Bhuj | BHUJ CITY-2 | COW | 26/06/07 |  |  |  |  | 1 | Leakage current flow through trans.center earthing | Not Applicable | Not Applicable
7 | BHJ | Anjar | Rapar | Cow & Ox | 2007-06-05 |  |  |  |  | 1 | May be induction with girder Pole
8 | BHJ | Anjar | Rapar | Savjibhai P Bhutak | 2007-06-12 |  |  | 1 |  |  | Reparing service line on the Pole
9 | BHJ | Anjar | Anjar® | Manjulaben P Goyal | 2007-06-12 |  |  | 1 |  |  | Private Premises(In Bathroom came in contact with wet switch Board
10 | BHJ | Mandvi | Mandvi(T) | Mukesh Meghji Marvada | 07.06.07 |  |  | 1 |  |  | He was trying to cut the earth wire of LST and got shock and died.
11 | BHJ | Mandvi | Mandvi(T) | Ajmal K.Maheshwari | 26.6.07 |  |  |  | 1 |  | Victim climbed on pole and caught the live LT line to attend the private complaint fell down and non fatal accident occured.
12 | BHJ | Mandvi | Kothara | Calf | 23.06.07 |  |  |  |  | 1 | Due to heavy wind pressure & rain there is leakage current passes through earth wire of transformer centre the calf passes near the t/c came in contact with earth wire resulted into fatal accident
13 | BHJ | Mandvi | Dahinsara | Two Cow | 26.06.07 |  |  |  |  | 1 | Due to Disk fault current pass through earthing wire.
14 | BHJ | G'DHAM | Gandidham | G. D. Chavda (Lineman) | 13.06.07 |  | 1 |  |  |  | Attending the service line on roof Loosing his balance & slipped | YES | concern instructed to follow safety rules
15 | BHJ | G'DHAM | Adipur | Kamal Jagdish Dagad | 26.06.07 |  |  | 1 |  |  | Victim climbed on overhighted truck Accidently coming in contact with 11kv line | NA | NA
16 | BHJ | BHUJ | BHUJ CITY-2 | FULCHAND DWARKAPRASAD | 2007-02-07 | - | - | 1 | - | - | The Victim had tied the string for drying wel clothes with the service support angle and due to bad climate condition and heavy rain fall, there was leakage of power in service suport angle.while removing wet clothes from the string,victim got electrocat | Not Applicable | Not Applicable
17 | BHJ | BHUJ | DESHALPAR | ALPESH K. SAGARPUTRA | 16/07/07 |  | 1 |  |  |  | Line staff was carring out LT line maint. Agter switching off LT supply.Single LT wire of dead span at HT line crossing came in contact with HT line, which resulted into Non Fatal Accident. | Utilised | Not Applicable
18 | BHJ | BHUJ | NAKHATRANA | HUSSAIN SIDDIK | 20/07/07 |  |  | 1 |  |  | While the victim was removing broken tree branch lying on 1 phase S/L in front yard of his house, the GI wire broken and one end of it came in contact with live L.T.line, the second end of GI wire was in contact with the victim, hense got electrocuted & r | Not Applicable | Not Applicable
19 | BHJ | BHUJ | BHUJ RURAL | SIDDIK SUMAR NODE | 22/07/07 |  |  | 1 |  |  | No any avidence is found, which lead to leakage of current resulted into accident. | Not Applicable | Not Applicable
20 | BHJ | BHUJ | Bhachau | Buffalo & Calf | 2007-07-01 |  |  |  |  | 1 | Due to snapping of conductor as Pin Blast
21 | BHJ | BHUJ | Anjar© | Bharat R Parmar | 2007-07-03 |  | 1 |  |  |  | Although lin was cleared power came in 11KV Line and victim fallen down from 11KV Girder Pole
22 | BHJ | BHUJ | Bhimasar | Ramehsbhai K Koli | 2007-07-08 |  |  | 1 |  |  | Taking direct power supply form existing LT Line
23 | BHJ | BHUJ | Anjar© | Pushpaben Dabhi | 2007-07-28 |  |  | 1 |  |  | Electrocuted by electric motor while sprinkling water to newly built house.(Pribvate Premises)
24 | BHJ | Mandvi | Dahinsara | C.N.Kharadi | 01.07.07 |  | 1 |  |  |  | carelessness of isolation in power
25 | BHJ | Mandvi | Mundra | 1-buffalow | 04.07.07 |  |  |  |  | 1 | conductor snapping
26 | BHJ | Mandvi | Dahinsara | 1-cow | 11.07.07 |  |  |  |  | 1 | conductor snapping
27 | BHJ | Mandvi | Kothara | Salemamad Osman Kunbhar | 22.07.07 |  |  | 1 |  |  | conductor snapping
28 | BHJ | Mandvi | Kothara | Manjulaben R.Dalit | 14.07.07 |  |  | 1 |  |  | accident took place in Private primises
29 | BHJ | Anjar | Anjar® | P. J. Kharadi | 20.8.07 |  | 1 |  |  |  | Victim fell down from LT pole while attending complain at vill. Sapeda | Yes | N.A.
30 | BHJ | Mandvi | Mandvi® | 1-buffalow | 01.08.07 |  |  |  |  | 1 | conductor snapping
31 | BHJ | Mandvi | Mandvi® | 4-cow and 2-calf | 05.08.07 |  |  |  |  | 6 | conductor snapping
32 | BHJ | Mandvi | Naliya | 1-cow | 02.08.07 |  |  |  |  | 1 | Leakage current
33 | BHJ | Mandvi | Mandvi(T) | 1-buffalow | 13.08.07 |  |  |  |  | 1 | conductor snapping
34 | BHJ | Mandvi | Naliya | Kirtikumar A.Patel | 25.08.07 | 1 |  |  |  |  | Without isolating the LT power he climbed on pole to repair jumper fault and died due to elecric shock. | No
35 | BHJ | Mandvi | Mundra | 1-buffalow | 29.08.07 |  |  |  |  | 1 | conductor snapping
36 | BHJ | Bhuj | Bhuj City-1 | Cow | 2007-03-08 |  |  |  |  | 1 | LT Conductor Snapping | Not Applicable | Not Applicable
37 | BHJ | Bhuj | Bhuj Rural | Buffallo | 25/08/07 |  |  |  |  | 2 | 11 KV Pole broken | Not Applicable | Not Applicable
38 | BHJ | Bhuj | Bhuj City-2 | Ali Asgar | 2007-07-08 | 0 | 0 | 1 | 0 | 0 | Defective appliances at consumer's premises | Not Applicable | Not Applicable
39 | BHJ | Anjar | Bhachau | Koli Ranchhod U | 2007-09-15 |  |  | 1 |  |  | A Trailor carrying logs of wood was passing on the road the rear side of the logs touch the LT Line pole. As a result the LT Pole fell down and the LT Line touch the victim | N.A. | Party has lodged FIR Against the driver of Trailor
40 | BHJ | Anjar | Bhimasar | Laxman Arfeb Parmar | 2007-09-24 |  |  |  | 1 |  | Due to heavy rain and wind pressure a very old PSC Pole broken down and victim passing nearby that pole got injured | N.A. | N.A.
41 | BHJ | Bhuj | Bhuj Rural | Cow | 2007-06-09 | 0 | 0 | 0 | 0 | 1 | Power leckage in earthing of TC center the cow came in contact of pole and get electrocuted and spot dead. | Not Applicable | Not Applicable
42 | BHJ | Bhuj | Nakhatrana | Cow | 20/09/07 | 0 | 0 | 0 | 0 | 2 | Due to Pin Insulator's fault 11 KV conductor of Jetavira feeder was stupped and fallen on two nos of cow passing under line and cowa got electrocuted and spot dead. | Not Applicable | Not Applicable
43 | BHJ | G'DHAM | Gandidham | Two cows | 23.09.07 |  |  |  |  | 1 | Due to snapping of B-phase of LT Line, the live wire come in contact of 2nos. Cows. | NA | LT cond. Replaced, losse jumpers replaced by the new.
44 | BHJ | Mandvi | Mundra | Two Buffelow | 24.09.07 |  |  |  |  | 2 | LT line of 11 KV Fdr is broken & two buffelows were came in contact with live LT wire | NA | LT span replaced & maint. Carried out
45 | BHJ | Mandvi | Mundra | Sajid Sadgu Khan | 24.09.07 | 0 |  | 1 |  |  | Trolly of Dumper touched to 11 KV Fdr & the men maintaning the gear box got shocked & died. | NA | NA
46 | BHJ | Anjar | Rapar | Mansukh B Sadhu | 2007-10-03 |  |  | 1 |  |  | Victim was covering the truck with tarpouline(Talpatri), while doing so he touch 11KV line and got electrocuted | N.A. | N.A.
47 | BHJ | BHUJ | Bhuj Rural | 3 nos of Buffalo | 2008-10-01 | 0 | 0 | 0 | 0 | 3 | 11 KV pole broken | NA | NA
48 | BHJ | G'DHAM | Adipur | Haresh N. Jethva | 08.02.08 |  | 1 |  |  |  | slipped from pole | YES
49 | BHJ | Anjar | Anjar-R | Shri Kantibhai V. Baria | 15.03.08 |  |  |  | 1 |  | Victim(Unauthorized person) was doing some illegal work on X'mer Centre and met with electrical accident. |  | Notice given to Victim & villagers has been warned for not do unauthorized and illegal work on lines & T/C
50 | BHJ | BHUJ | Bhuj Rural | Rajendra Trivedi | 2008-03-03 | 0 | 1 | 0 | 0 | 0 | While attending fault, on 11KV Medisar JGY feeder, person got electric sock. Due to tuching of 11 conductor of 11 KV sumarasar feeder to 11 KV Medisar JGY feeder. | Yes | NIL
51 | BHJ | BHUJ | Deshalpar | Viththal Mithu Maheshwari | 8.03.08 | 0 | 0 | 1 | 0 | 0 | Person was climed on tree branches & came in contact of live conductor | NIL | NIL
1 | JND | City Division | GIDC JND | Sh. Suresh Ravaji Chauhan | 2007-04-17 |  |  | 1 |  |  | In Private premises of Kiran Traders, The victim came in contact with the electric circuited iron roof which arranged by the factory holder to prevent theft of material. He got the shock and met with the fatal accident in premises of Kiran traders | Not Applicable | Not Applicable
2 | JND | Rural Division-1 | Bhesan | Sh. S.P.Joshi | 2007-04-04 |  | 1 |  |  |  | While taking details on TC. came in to induction zone | No | EE, Rural Divison-1 has been asked to inquire the victim
3 | JND | Rural Division-1 | Visavadar-2 | Sh. Ramesh Bhanubhai | 2007-04-04 |  |  | 1 |  |  | LT Line shock doubtful may be in private premises | Not Applicable | Not Applicable
4 | JND | Rural Division-1 | Junagadh(R) | Buffalo | 2007-04-12 |  |  |  |  | 1 | Due to leakage of current in TC Earthing | Not Applicable | Not Applicable
5 | JND | Rural Division-1 | Visavadar-1 | Sh.Babubhai Parbatbhai | 2007-04-18 |  |  |  | 1 |  | 11 KV DO Fuse operation with wet rod | No | Not Applicable
6 | JND | Veraval | Veraval Town | Anonymous Person | 2007-03-31 |  |  |  | 1 |  | Due to touching of live line while carrying out construction below live 11 KV line | Not Applicable | Not Applicable
7 | JND | Rural Division-1 | Bilkha | Ms. Nikita B Shapariya | 2007-05-03 |  |  | 1 |  |  | Come into the direct touch to live holder in private premises | Not Applicable | Not Applicable
8 | JND | Rural Division-1 | Visavadar-2 | Sh. Bhavesh M Trivedi (VS-HLP) | 2007-05-05 |  | 1 |  |  |  | Slipping from PSC pole mechanical accident | Safety Belt was not allocated | Not Applicable
9 | JND | Rural Division-1 | Bilkha | Sh. Bhagaram Banaram | 2007-05-09 |  |  |  | 1 |  | Electrocuted from another supply while working | Not Applicable(Unauthorized Operation by consumer) | Not Applicable
10 | JND | Rural Division-1 | Visavadar-2 | Sh. Gagjibhai Jinabahi | 2007-05-16 |  |  | 1 |  |  | In private premises while removing electric motor from bore well | Not Applicable | Not Applicable
11 | JND | Veraval | Veraval Town | Sh. Varshben M Goswami | 2007-05-02 |  |  | 1 |  |  | Accident is occurred in her premises when she was going to remove pin from plug. The live wire of the pin may come in contact with her & this accident may occurred | Not Applicable | Not Applicable
12 | JND | Veraval | Talala | Sh. Parshbhai Sigala & Sh. Mansukh M Kachhadiya | 2007-05-07 |  |  |  | 1 |  | Accident is occurred when they were working on TC for cabling work. | Not Applicable | Not Applicable
13 | JND | City Division | Central | Mrs. Shahina Iiyas Shekh | 2007-06-12 |  |  | 1 |  |  | The GI wire which is used to hang the wet clothes, that wire came into contact with the phase of load side wiring. The load side owner was too old and deterioted. So its insulation broke down and its phase came into contact with GI wire n current passed t | Not Applicable | Not Applicable
14 | JND | City Division | GIDC JND | Sh. Hardik Naran | 2007-06-23 |  |  |  | 1 |  | Accident occurred due to heavy rainfall with more wind pressure so that LT pole is tilted, hence the live phase was touched the guard wire and was earthed through pole earthing and at that time victim had touched the earthing lead and victim was electrocu | Not Applicable | Not Applicable
15 | JND | City Division | GIDC JND | Sh. Ashok Kishorchand | 2007-06-25 |  |  | 1 |  |  | Accident was occurred during laying of illegal wiring for un-authorized power taking from nearby house in private premises. | Not Applicable | Not Applicable
16 | JND | City Division | GIDC JND | Buffalo | 2007-06-08 |  |  |  |  | 1 | Accident was occurred due to snapping of LT conductors which was snapped due to frequently jumping of monkeys from nearby tree. | Not Applicable | Not Applicable
17 | JND | Rural Division-1 | Visavadar-2 | Sh. Kesubhai Gokalbhai | 2007-06-09 |  |  |  | 1 |  | Unauthorized climbing on pole on LT pole | Not Applicable | Not Applicable
18 | JND | Rural Division-1 | Visavadar-1 | Sh. Lalji Arfeb | 2007-06-11 |  |  |  | 1 |  | Due to leakage current of TC earthing | Not Applicable | Not Applicable
19 | JND | Rural Division-1 | Bhesan | Buffalo | 2007-06-22 |  |  |  |  | 1 | LT conductor snapped | Not Applicable | Not Applicable
20 | JND | Rural Division-1 | Junagadh(R) | Sh. D D Pandya (Helper) | 2007-06-25 |  | 1 |  |  |  | Leakage current in service line | Not Applicable | Not Applicable
21 | JND | Rural Division-1 | Junagadh(R) | Sh. M G Parmar (ALM) | 2007-06-25 |  | 1 |  |  |  | Mechanical NFA at the time of tree cutting in 11kV vadal feeder. | Not Applicable | Not Applicable
22 | JND | Rural Division-2 | Manavadar-2 | Smt. Manishaben Rajeshkumar Trambaliya | 2007-06-06 |  |  | 1 |  |  | A fatal accident occurred to Victim due to her wiring short circuit. | Not Applicable | Not Applicable
23 | JND | Rural Division-2 | Mendarda | Sh. Karsanbhai Mulubhai Vala | 2007-06-20 |  |  | 1 |  |  | A fatal accident occurred to victim when he is climbing the LT line on his own risk in the farm of Sh. Rambhai Safebbhai Gal | Not Applicable | Not Applicable
24 | JND | Rural Division-2 | Mendarda | Buffalo | 2007-06-23 |  |  |  |  | 1 | A fatal accident occurred to A buffalo at Vill: Mendarda due to leakage current of telephone galvanized pole & current pass nearby LT to a buffalo. | Not Applicable | Not Applicable
25 | JND | Veraval | Prabhas Patan | Buffalos | 2007-06-17 |  |  |  |  | 1 | Due to leakage of jumper in 11kV line | Not Applicable | Not Applicable
26 | JND | Veraval | GIDC VRL | Buffalo | 2007-06-21 |  |  |  |  | 1 | Due to leakage of current in TC DP | Not Applicable | Not Applicable
27 | JND | Veraval | Talala | Bullok | 2007-06-23 |  |  |  |  | 1 | This accident is occurred in railway premises. | Not Applicable | Not Applicable
28 | JND | City Division | GIDC JND | Mrs. Rekhaben Bharatbhai Lathiya | 2007-07-06 |  |  |  | 1 |  | The victim come in contact with steel stair rail which charged through short- defective ceiling fan of her neighbor of row houses with minor injury in private premises. | Not Applicable | Not Applicable
29 | JND | City Division | Satellite | Cow | 2007-06-26 |  |  |  |  | 1 | The 1Ø service line has jointed near at pole. The insulation of 1Ø service joints was rusted and broken and contacting with the supporting GI wire. Hence, the leakage current was passed through the GI wire, LT X-arm ,earth wire of PSC pole to earth. At th | Not Applicable | Not Applicable
30 | JND | Rural Division-1 | Bhesan | Shri. Hitesh Vithalbhai | 2007-07-01 |  |  | 1 |  |  | Leakage in Private premises at the time of replacing Electric motor in Bore | Not Applicable | Not Applicable
31 | JND | Rural Division-1 | Visavadar-1 | Smt. Hansaben Vithalbhai | 2007-06-29 |  |  |  | 1 |  | Unauthorized construction below 11kV line touched to it. | Not Applicable | Not Applicable
32 | JND | Rural Division-1 | Junagadh(R) | Cow | 2007-07-03 |  |  |  |  | 1 | Leakage in TC Earthing | Not Applicable | Not Applicable
33 | JND | Rural Division-1 | Visavadar-2 | Cow | 2007-07-07 |  |  |  |  | 1 | Leakage in TC Earthing | Not Applicable | Not Applicable
34 | JND | Rural Division-2 | Mendarda | Smt. Hemiben Vinubhai Vaghasiya | 2007-06-27 |  |  | 1 |  |  | A fatal accident occurred to Smt. Hemi Ben Vinbhai Vaghasiiya due to leakage current passes through meter body to leakage and touched victim in private premises | Not Applicable | Not Applicable
35 | JND | Rural Division-2 | Manavadar-2 | Sh. Arfeb Chhagan Rathod | 2007-06-30 |  |  | 1 |  |  | A fatal accident occurred at ag group lighting lamp wiring insulation damage and touched with cloth hanging wire angle and leakage current pass and meet fatal accident | Not Applicable | Not Applicable
36 | JND | Rural Division-2 | Mendarda | Sh. Rameshbhai Somabhai Sahiya | 2007-07-02 |  |  | 1 |  |  | Due to heavy rain and wind when victim passes on road nearby LT line conductor breakdown and touches the LT cross arm & accident occurred | Not Applicable | Not Applicable
37 | JND | Rural Division-2 | Mendarda | Sh. Sanjaybhai Lalubhai Makvana | 2007-07-24 |  |  |  | 1 |  | During TC replacement working on 11kV Alidhra feeder line clear returned by Sh. G. G. Kalola, Mendarda Sub-division
38 | JND | Rural Division-2 | Mendarda | Buffalo | 2007-07-14 |  |  |  |  | 1 | Due to snapping of LT conductor | Not Applicable | Not Applicable
39 | JND | Veraval | Veraval Town | Cow | 2007-07-02 |  |  |  |  | 1 | Due to touching flexible wire to sign board and through sign board leakage was passing in the door | Not Applicable | Not Applicable
40 | JND | Veraval | Veraval Town | Cow | 2007-07-02 |  |  |  |  | 1 | Due to leakage of current at T/C D.P. earthing | Not Applicable | Not Applicable
41 | JND | Veraval | Talala | Smt. Hemiben Bhaya Balash | 2007-07-12 |  |  |  | 1 |  | The LT Line cond.was snapped due to Lungaries | Not Applicable | Not Applicable
42 | JND | Veraval | Talala | Buffalo | 2007-07-13 |  |  |  |  | 1 | Jumper was broken and touching to pole earth wire | Not Applicable | Not Applicable
43 | JND | Veraval | Talala | Buffalo | 2007-07-18 |  |  |  |  | 1 | Due to broken binding from LT Shackle, Cond. Was lying on "U" Clamp and so leakage was passing through pole | Not Applicable | Not Applicable
44 | JND | Rural Division-1 | Bilkha | Sh. Chandubhai Raghav Vaghela | 2007-07-25 |  |  |  | 1 |  | Due to jerk in neutral wire at the time of fixing street light | Not Applicable | BEING A GRAM PANCHAYAT PERSON Not Applicable
45 | JND | Rural Division-1 | Bilkha | A Calf & A Cow | 2007-07-28 |  |  |  |  | 1 | LT line leakage in earthing | Not Applicable | Not Applicable
46 | JND | Rural Division-1 | Bhesan | Smt. Vliben Ravajibhai & Pankaj Ravaji | 2007-08-04 |  |  |  | 1 |  | Due to heavy rain and wind pressure conductor binding damage and LT line conductor fall on c clamp | Not Applicable | Not Applicable
47 | JND | Rural Division-1 | Bilkha | Buffalo | 2007-08-08 |  |  |  |  | 1 | Due to heavy rain and wind pressure LT line conductor snapped. | Not Applicable | Not Applicable
48 | JND | Rural Division-1 | Visavadar-1 | Smt. Rasilaben Ratibhai | 2007-08-10 |  |  |  | 1 |  | Due to internal wiring leakage in private premises | Not Applicable | Not Applicable
49 | JND | Rural Division-1 | Bhesan | Bullock | 2007-08-10 |  |  |  |  | 1 | Due to heavy rain and wind pressure conductor binding damage and LT line conductor fall on c clamp | Not Applicable | Not Applicable
50 | JND | Rural Division-1 | Bhesan | Cow | 2007-08-12 |  |  |  |  | 1 | Leakage in insulation of 1 phase service wire | Not Applicable | Not Applicable
51 | JND | Rural Division-1 | Visavadar-2 | Buffalo | 2007-08-17 |  |  |  |  | 1 | Due to heavy rain and wind pressure conductor binding damage and LT line conductor fall on c clamp | Not Applicable | Not Applicable
52 | JND | Rural Division-1 | Bhesan | Ku. Monikaben Vinubhai & Ku. Bhumikaben Kamleshbhai | 2007-08-19 |  |  |  | 1 |  | Due to touching of live 11 kV line passes near terrace | Not Applicable | Not Applicable
53 | JND | Rural Division-1 | Bilkha | 2 Nos Of Buffalo | 2007-08-20 |  |  |  |  | 1 | Due to touching of LT phase wire with neutral wire. Neutral wire was fall on c clamp. | Not Applicable | Not Applicable
54 | JND | Rural Division-1 | Visavadar-1 | Buffalo | 2007-08-22 |  |  |  |  | 1 | Due to touching of LT phase wire with guard wire, bird fault | Not Applicable | Not Applicable
55 | JND | Rural Division-2 | Shapur | One Buffalo | 2007-07-29 |  |  |  |  | 1 | Due to came to contact with the Kit Kat fuse on LT side of TC | Not Applicable | Not Applicable
56 | JND | Rural Division-2 | Shapur | Sh. Arfebgar Dhangar Aparnathi | 2008-08-02 |  | 1 |  |  |  | Due to broke down of 11kV Line pole when he was working on line | Not Applicable | Not Applicable
57 | JND | Rural Division-2 | Manavadar-1 | A Calf | 2007-08-06 |  |  |  |  | 1 | Due to rain situation minor leakage current passed through earthing and at that time victim came to contact with the earthing wire and electrocuted. | Not Applicable | Not Applicable
58 | JND | Rural Division-2 | Mendarda | A Buffalo | 2007-08-15 |  |  |  |  | 1 | Due to leakage current passed through 100kVA transformer earthing | Not Applicable | Not Applicable
59 | JND | Rural Division-2 | Mendarda | A Cow | 2007-08-18 |  |  |  |  | 1 | Due to snapping of LT Conductor when victim passing near 63kVA TC named Mohan Manji Pansuriya Group and came to contact with live wire. | Not Applicable | Not Applicable
60 | JND | Rural Division-2 | Mendarda | A Buffalo | 2007-08-22 |  |  |  |  | 1 | Due to leakage current passed through transformer earthing and victim rubs its body and met to accident. | Not Applicable | Not Applicable
61 | JND | Veraval | GIDC VRL | Sh. Mohmadsahid Mohmadkarim Bhadarka | 2007-07-27 |  |  | 1 |  |  | Due to leakage current passed through the earthing of the PSC LT pole due to breaking of the service line and touched to earthing wire of the pole, | Not Applicable | Not Applicable
62 | JND | Veraval | Veraval Town | Kum. Fazilat Altaf Bhoda | 2007-08-03 |  |  |  | 1 |  | Due to leakage current passed through the earthing of the PSC LT pole due to breaking of the service line and touched to earthing wire of the pole, | Not Applicable | Not Applicable
63 | JND | Veraval | Prabhas Patan | A Buffalo | 2007-08-04 |  |  |  |  | 1 | Due to snapping of the neutral wire in 1Ø service line. | Not Applicable | Not Applicable
64 | JND | Veraval | Talala | A Cow | 2007-08-07 |  |  |  |  | 1 | Due to leakage current in TC earthing | Not Applicable | Not Applicable
65 | JND | Veraval | Prabhas Patan | Sh. Bodu Abdul Sidi | 2007-08-12 |  |  | 1 |  |  | Due to broken of LT line pole | Not Applicable | Not Applicable
66 | JND | Veraval | GIDC VRL | Sh. Raghubhai K Padhiyar | 2007-08-18 |  | 1 |  |  |  | Due to cracking of the boarder of the PSC pole while climbing the pole. so he loose his balance and fall down to the earth and met the mechanical accident. | Not Applicable | Not Applicable
67 | JND | Veraval | Prabhas Patan | A Cow | 2007-08-23 |  |  |  |  | 1 | Due to leakage current in LT pole earthing. | Not Applicable | Not Applicable
68 | JND | Veraval | Pranchi | A Bullock | 2007-08-05 |  |  |  |  | 1 | Due to leakage current in TC earthing | Not Applicable | Not Applicable
69 | JND | Veraval | Talala | A Buffalo | 2007-08-04 |  |  |  |  | 1 | Due to touching of scratched cable to guy wire and buffalo has come in contact with this guy wire | Not Applicable | Not Applicable
70 | JND | Veraval | Talala | A Buffalo | 2007-08-04 |  |  |  |  | 1 | Due to snapping of LT line wire and both the Buffalo passed near the snapped cond. & come in contact and electrocuted. | Not Applicable | Not Applicable
71 | JND | Veraval | Prabhas Patan | A Cow | 2007-08-17 |  |  |  |  | 1 | Due to Pin puncture leakage current was passing in pole | Not Applicable | Not Applicable
72 | JND | Veraval | Pranchi | A Buffalo | 2007-08-18 |  |  |  |  | 1 | Due to leakage of current in earthing of service pole | Not Applicable | Not Applicable
73 | JND | Veraval | Prabhas Patan | A Cow | 2007-08-20 |  |  |  |  | 1 | Snapping og conductor in LT line ph. wire | Not Applicable | Not Applicable
74 | JND | Rural Division-1 | Visavadar-2 | CALF | 2007-08-28 |  |  |  |  | 1 | Due to heavy rain and wind LT. line conductor snapped | Not Applicable | Not Applicable
75 | JND | Rural Division-1 | Bilkha | SHRI LAKHABHAI LALABHAI | 2007-05-09 |  | 1 |  |  |  | Line clear was taken but feedback owner supply came due to another source. Un authorized operation by outsider | Not Applicable | Not Applicable
76 | JND | Rural Division-1 | Visavadar-2 | BULLOCK | 2007-09-23 |  |  |  |  | 1 | Due to heavy rain and wind LT. line conductor snapped | Not Applicable | Not Applicable
77 | JND | Rural Division-2 | Mendarda | Two Buffalo | 2007-08-30 |  |  |  |  | 1 | Due to heavy rain and wind LT. line conductor snapped | Not Applicable | Not Applicable
78 | JND | Veraval | Talala | A Cow | 2007-09-01 |  |  |  |  | 1 | Due to leakage of current in T/C. Earthing | Not Applicable | Not Applicable
79 | JND | Veraval | Pranchi | Sh. Pithabhai Rambhai Rathod | 2007-08-29 |  |  | 1 |  |  | Leakage of Current in 1 PG motor due to some problem in his premises | Not Applicable | Not Applicable
80 | JND | Veraval | Talala | Sh. Ramesh Vira Chudasama | 2007-09-07 |  |  |  | 1 |  | During cutting work in monsoon period victim may came in vicinity of 11 KV line & met with N.F.A. | Not Applicable | Not Applicable
81 | JND | Veraval | Talala | A Buffalo | 2007-09-09 |  |  |  |  | 1 | T/C earthing was leakage in monsoon period victim might came in contact with T/C and met with F.A. | Not Applicable | Not Applicable
82 | JND | Veraval | Talala | A Buffalo | 2007-09-12 |  |  |  |  | 1 | Due to minor leakage current in T/C earthing and buffalo accidently came in contact and electrocuted. | Not Applicable | Not Applicable
83 | JND | Veraval | Veraval Town | A Buffalo | 2007-09-13 |  |  |  |  | 1 | Victim while passes near the 11 KV pole Loc. № MTH/BLP/38 broken the guy wire & upper wire of guy came in contact with live D.O. Jumper through which victim come in contact and got electrocuted | Not Applicable | Not Applicable
84 | JND | Veraval | GIDC VRL | Sh. Maheshbhai Karshan Gadhiya | 2007-09-17 |  |  |  | 1 |  | Due to broken and fall down of LT Line PSC Pole he fall down on earth | Not Applicable | Not Applicable
85 | JND | Veraval | Prabhas Patan | Sh. Ashok Gokaldas Solanki (Helper) | 2007-09-21 |  | 1 |  |  |  | Due to climbing of 11 KV DP where two feeders are passing namely Deva & Vidyutnagar on which only one line L.C. was taken (Devka) & another line was in live condition, so during jumpering work on Devka Feeder Jumper wire may touched to the live wire and t | Not Applicable | Not Applicable
86 | JND | Veraval | Pranchi | A Cow | 2007-09-21 |  |  |  |  | 1 | Due to snapping of LT line conductor. | Not Applicable | Not Applicable
87 | JND | Veraval | Pranchi | Sh. Dhirubhai Mandanbhai Solanki | 2007-09-22 |  |  | 1 |  |  | Victim may come in contact with live broken service wire | Not Applicable | Not Applicable
88 | JND | Veraval | Talala | A Buffalo | 2007-09-24 |  |  |  |  | 1 | Due to broken of AG LT line in monsoon period victim might came in contact and met with F.A. | Not Applicable | Not Applicable
89 | JND | Veraval | Talala | A Buffalo | 2007-09-24 |  |  |  |  | 1 | Due to T/C earthing was leakage in monsson period victim might have came in contact with F.A. | Not Applicable | Not Applicable
90 | JND | City Division | Satellite | A Buffalo's Calf | 2007-09-25 |  |  |  |  | 1 | Due to snapping of LT line conductor. | Not Applicable | Not Applicable
91 | JND | Rural Division-1 | Visavadar-1 | A Cow | 2007-09-27 |  |  |  |  | 1 | Due to snapping of LT line conductor. | Not Applicable | Not Applicable
92 | JND | Rural Division-1 | Visavadar-2 | Shri Manilal Somabhai | 2007-09-27 |  | 1 |  |  |  | DUE TO PSC POLE BROKEN. MECHANICAL ACCIDENT | Not Applicable | Not Applicable
93 | JND | Rural Division-1 | Bilkha | Shri Yunus Ismail Savan | 2007-09-28 |  |  |  | 1 |  | DIRECT TOUCHING TO LIVE 11 K.V. LINE | No | Not Applicable
94 | JND | Rural Division-1 | Visavadar-2 | Shri Bharatsinh Chhatrasinh | 2007-10-14 |  | 1 |  |  |  | DUE TO UN ISOLATION OF G.O. SWITCH CONTACT | No | No
95 | JND | Rural Division-1 | Bilkha | BUFFALO | 2007-10-16 |  |  |  |  | 1 | DUE TO SNAPPING OF L.T. LINE COND. | Not Applicable | Not Applicable
96 | JND | Rural Division-2 | Mendarda | BUFFALO | 2007-09-30 |  |  |  |  | 1 | Due to leakage current of TC earthing | Not Applicable | Not Applicable
97 | JND | Rural Division-2 | Manavadar-1 | Sh. Bholabhai Merubhai Kamariya | 2007-09-29 |  |  |  | 1 |  | When Victim was trying to connect VCD Player wire in Stereo wire in private primises at that time due to short circuit of VCD player victim Electrocuted and met with Non Fatal Accidedent. | Not Applicable | Not Applicable
98 | JND | Rural Division-2 | Mendarda | Sh. Anantrai Laxmanbhai Bhimani | 2007-10-09 |  |  | 1 |  |  | Due to Electric Shock while he was switching off hos motor in his farm room where meter was attached and met with Human Fatal Accident. | Not Applicable | Not Applicable
99 | JND | Rural Division-2 | Mendarda | Sh. Shaileshbhai Rupabhai Palas Vill. Helper VS | 2007-10-18 |  | 1 |  |  |  | Due to 11 KV Deterioted Angle of Karavalu Ag Group. To Sh. Shaileshbhai Rupabhai Palas Vill. Helper (V/S) | Yes | Not Applicable
100 | JND | Veraval | Pranchi | A Bullock | 2007-09-26 |  |  |  |  | 1 | Due to Broken incoming LT Line and Bullock was came in contact with broken wire and met with electrical accident | Not Applicable | Not Applicable
101 | JND | Veraval | Prabhas Patan | A Buffalo | 2007-09-29 |  |  |  |  | 1 | Due to unauthorised wiring done by the farmer in his fancing of the farm | Not Applicable | Not Applicable
102 | JND | Veraval | Talala | A Buffalo | 2007-09-30 |  |  |  |  | 1 | Due to leakage current passing from T/C earthing when buffalo passwed and came in contact with T/C earthing it may be electro- cuted | Not Applicable | Not Applicable
103 | JND | Veraval | GIDC VRL | Sh. Dineshbhai Jagmalbhai Pampania | 2007-10-03 |  |  | 1 |  |  | Due to touching the 11 KV Live Line on load side DP after Gangswitch | Not Applicable | Not Applicable
104 | JND | Veraval | Prabhas Patan | Sh. Laxmanbhai Malabhai Solanki | 2007-10-20 |  |  | 1 |  |  | When victim repaired TV in his own house contact with live open wire of his house wiring and got shocked and met with accident | Not Applicable | Not Applicable
105 | JND | City Division | Satellite | A Buffalo | 2007-11-04 |  |  |  |  | 1 | Due to falling the tree in the heavy rain and high wind pressure atmosphere snapping of the LT Conductor on the buffalo | Not Applicable | Not Applicable
106 | JND | Rural Division-1 | Junagadh(R) | Sh. Munnabhai Urfe Muneshvar Mahavir | 2007-11-05 |  |  |  | 1 |  | Come into the induction zone of 11kV line | Not Applicable | Not Applicable
107 | JND | Rural Division-1 | Visavadar-1 | Sh. Viththalbhai Kalabhai | 2007-11-06 |  |  | 1 |  |  | Due to snapping of LT conductor | Not Applicable | Not Applicable
108 | JND | Rural Division-1 | Junagadh(R) | Sh. Ranjit Vikram Mandaviya | 2007-11-24 |  |  | 1 |  |  | Come to contact with the 11kV line. | Not Applicable | Not Applicable
109 | JND | Veraval | Pranchi | A Cow | 2007-11-05 |  |  |  |  | 1 | Due to broken of inside LT line when cow passed near this broken line and got electrical accident | Not Applicable | Not Applicable
110 | JND | Rural Division-2 | Manavadar-1 | Sh. Abdulkhan Ibrahim Belim | 2007-12-03 |  |  |  | 1 |  | Due to come in induction zone of the 66kV. | Not Applicable | Not Applicable
111 | JND | Veraval | Prabhas Patan | Sh. Ibrahim Pira Thobhat | 2007-11-30 |  |  | 1 |  |  | Due to conductor snapping, but not clear reason found yet. | Not Applicable
112 | JND | City Division | Gandhigram | Mansukh Tulsidas Vaghela | 2007-12-28 |  |  |  | 1 |  | The victim slept his leg while he was fixing a junction box on L.T. line Girder pole and fall down from the girder and meet with non-fatal mechanical accident | Not Applicable | Not Applicable
113 | JND | Rural Division-2 | Manavadar-1 | Smt. Kanchanben Harsukhbhai Parmar | 2008-01-25 |  |  | 1 |  |  | We haven't informed by party.The rojkam is done after Newspaper Sandesh pressnote on 30.01.08.The accident has been occurred near HT-LT circuit line.Still no-strong reason has been found but came to know that victim tryed to connect lungaria to 11KV line | Not Applicable | Not Applicable
114 | JND | Rural Division-2 | Manavadar-1 | smt. Narmadaben Bavanjibhai Maradiya | 2008-01-28 |  |  | 1 |  |  | Due to short circuit of 1-Ph.Motor in private premises | Not Applicable | Not Applicable
115 | JND | Veraval | Pranchi | Sh Rajesh Bachubhai Barad | 2008-01-07 |  |  | 1 |  |  | During change of loads in service at his primises | Not Applicable | Not Applicable
116 | JND | Rural Division-1 | Bhesan | Sh.Bharat Jasyantkant Dave(Helper) | 2008-03-07 |  | 1 |  |  |  | While Victim was attending the new release of connection and installing the meter, slipped down leg from the stool table and met to mechanical accident | Not Applicable | Not Applicable
117 | JND | Veraval | Prabhas Patan | Sh.Kaushik Kana Pampaniya | 2008-03-05 |  |  | 1 |  |  | We have not informed by party. The information received from daily News paper “Divya Bhaskar” press note on 07.03.08. The accident has been occurred in Private premises. During starting of his motor-might have come in contact with live wire | Not Applicable | Not Applicable
1 | BVN | City-1 | HT | Manoj Ravishankar Joshi | 23-6-07 | 1 |  |  |  |  | Sliping from PSC pole mecahnical accident | Meeting arranged for use of safety belt at s/dn.
2 | BVN | City-1 | Power House | Urvashi Manaji Dhakhara | 18-6-07 |  |  | 1 |  |  | Come into the direct touch to live holder in private primises
3 | BVN | City-1 | Kalanala | Rahil Rahim Dariya | 25-6-07 |  |  |  | 1 |  | Come into the direct touch to live holder in private primises
4 | BVN | City-2 | Hill Drive | S.S.MAHIDA | 2007-06-25 |  | 1 |  |  |  | Electrocuted due to common neutral | necessary action taken
5 | BVN | City-2 | Kalvibid | M.J.VAGHELA | 2007-06-25 |  | 1 |  |  |  | Due while repairing of comaplatins of consumer , he felt jerk and fall down from compound wall | necessary action taken
6 | BVN | BVN-R | Dhola | Sh. P.D.Parmar (App. L.M.) | 2007-05-21 |  | 1 |  |  |  | Electrocuted from another supply while working due to crossing of line | Necessary action taken
7 | BVN | BVN-R | Sihor-R | Sh. Girish D Solanki (VS-HLP) | 2007-06-21 |  | 1 |  |  |  | After isolating A.B. Switch of 11 KV Line tim has short line with piece of conductor and due to sparking met with N.F.A. | Necessary action taken
8 | BVN | BVN-R | Vallabhipur | Sh. Vinodbhai Haribhai Jadvani | 22/6/2007 |  |  | 1 |  |  | Come into the direct touch to live holder in private primises | Necessary action taken
9 | BVN | Mahuva | Jesar | Ghanshyambhai Jasmatbhai Jethava | 2007-04-16 |  |  | 1 |  |  | Tempo was struck to the LT PSC Pole and psc pole fallen on victim with live conductor | Necessary action taken
10 | BVN | Mahuva | Rural-2 | Bachubhai kanabhai Hadiya | 2007-06-10 |  |  | 1 |  |  | Victim has try to fix-up DO fuse of TC and came in contact with live 11 KV line and met with F.A | Necessary action taken
11 | BVN | Mahuva | Rural-2 | Gumanbhai Umedsangbhai | 2007-04-28 |  |  |  | 1 |  | accident was occurred on 28-4-07, but our official was informed by party on 21-5-07, on investigation no evidence found at place of accident about accident occurred by our network | Necessary action taken
12 | BVN | Palitana | Palitan -R | Manubhai Lakhabhai Parmar | 2007-05-03 |  |  | 1 |  |  | Unaothorised climbing on pole LT | Necessary action taken
13 | BVN | Palitana | Gariyadhar | Ishwarbhai Jivabhai Kharadi App LM | 2007-04-20 |  | 1 |  |  |  | While working on 11 KV line, PSC pole was tilted and lost his balance' hence fall down on ground | Necessary action taken
14 | BVN | Palitana | Gariyadhar | Mukesh Ratilal Dodiya Helper | 2007-06-27 |  | 1 |  |  |  | While working on 11 KV line, PSC pole was broken hence fall down on ground | Necessary action taken
15 | BVN | Botad | Dhasa | Dhiru Vallabh Kathiriya | 2007-04-11 |  |  | 1 |  |  | Try to work on TC un athorised | Not Applicable
16 | BVN | Botad | Paliyad | Jeram Ladha prajapati | 2007-04-17 |  |  |  | 1 |  | Try to work on TC un athorised | Not Applicable
17 | BVN | Botad | Town-2 | Sandip jayesh Kosiya | 2007-04-21 |  |  | 1 |  |  | leakage current flow from ideal pole of TC to earth, due deterioted PVC cable. | LT PVC Cable replace
18 | BVN | Botad | Barwala | J.V.Chavda | 2007-04-25 | 1 |  |  |  |  | While working on line by taking tripping, due to one pole of breaker was not isolated and victim got shock | Necessary action taken
19 | BVN | Botad | Gadhada | C.K.Makwana | 2007-06-06 |  | 1 |  |  |  | While working on line of 11 KV, another 11 KV line touch to line on which work taken on hand due to wind pressure | Proper guarding done and clearance increased
20 | BVN | Mahuva |  | 1 Cow & 1 Calf | 2007-06-15 |  |  |  |  | 2 | LT Conductor was snapped and was touch to LT shackle, so leakage current was flow in pole earthing and victim got shock.
21 | BVN | Palitana |  | Bufallow | 2007-06-10 |  |  |  |  | 1 | Unauthoried line extension by unknown person
22 | BVN | Palitana |  | Bufallow | 2007-05-21 |  |  |  |  | 1 | Snapping of LT conductor
23 | BVN | Palitana |  | Cow | 2007-06-04 |  |  |  |  | 1 | Leakage current passed through guy wire of TC
24 | BVN | Palitana |  | Cow | 2007-06-25 |  |  |  |  | 1 | Snapping of LT conductor
25 | BVN | BVN-R |  | Cow | 2007-06-22 |  |  |  |  | 1 | Leakage Current through the earth wire of tc
26 | BVN | BVN-R |  | Bullock | 2007-06-24 |  |  |  |  | 1 | Came in direct contact with live conductor
27 | BVN | City-1 |  | Female Buffalo | 2007-06-22 |  |  |  |  | 1 | Electrocuted from another supply while Waking
28 | BVN | BVN-R | Sihor-R | Animal | 2007-07-02 | 0 |  |  |  | 1 | Snapping of Conductor
29 | BVN | BVN-R | Vall'pur | Mohansing Udesing Ravat | 2007-07-11 |  |  | 1 |  |  | Snapping of Conductor
30 | BVN | Palitana | Gariyadhar | Animal | 2007-07-04 |  |  |  |  | 1 | Neutral was touching with C-Clamp and the neutral was common with t/c earth. Animal touch with earthing wire.
31 | BVN | Palitana | Gariyadhar | Animal | 2007-07-04 |  |  |  |  | 1 | Meter was provided on T/c. It was provided with MMB. The neutral was touching with MMB. The MMB was also earthed with T/c. earth and the ani,mal thouhed with earting.
32 | BVN | Palitana | Palitana _-T | Animal | 2007-07-03 |  |  |  |  | 1 | Snapping of Conductor
33 | BVN | Palitana | Trapaj | Animal | 2007-07-12 |  |  |  |  | 1 | LT jumper touched with Guy wire. Guy insulator was broken. Animal thouched with guy wire and it get shock.
34 | BVN | Palitana | Talaja | Animal | 2007-07-29 |  |  |  |  | 1 | Due to heavy rain and wind LT jumper touched with C-clamp and Current pass thorugh earting of GI Wire at PSC Pole.
35 | BVN | Mahuva | Jesar | Jaysukhbhai Somatbhai Parmar | 2007-07-02 |  |  | 1 |  |  | Snapping of Conductor
36 | BVN | Mahuva | Mahvua R-2 | Animal | 2007-07-08 |  |  |  | 1 |  | Snapping of Conductor
37 | BVN | Botad | Paliyad | Animal | 2007-07-01 |  |  |  |  | 1 | The earthing of the T/c. was leakage. Due to rain the water was clogging in surrounding area. So the leakage current was passing in the water. The animal came in contact with the was water and it get shock.
38 | BVN | Botad | Gadhada | Anil H. Badhia | 2007-07-26 |  | 1 |  |  |  | The DE Gadhada has demanded the line clear of Tatam JGY for to reconnect the DO Fuse of Nana Sakhpar Section. So the SBO of 66KV Tatam S/s. had give the line clear of Nana Sakhpar Ag. feeder instead of Tatam JGY Feeder. The line clear was demanded on C | Yes
39 | BVN | Mahuva | Mahvua R-2 | Animal | 2007-08-01 |  |  |  |  | 1 | The B-phase of out going cable from D. B. was deteriorated and it was thouching with distribution box. The animal came in contact with this D.B. hence it got shock and it died.
40 | BVN | Mahuva | Jesar | Animal | 2007-08-05 |  |  |  |  | 1 | Snapping of LT conductor
41 | BVN | Palitana | Gariyadhar | Animal | 2007-08-08 |  |  |  |  | 1 | Leakage Current was passing through earthing wire. The current was passing in surrounding area. The animal came in contact with the earhing wire and it get shock and it ided
42 | BVN | BVN-R | Vartej | Animal | 2007-08-05 |  |  |  |  | 1 | A truck was struck with the girder pole. Hence the accident is Occurred
43 | BVN | Mahuva | Mahvua R-2 | Human | 2007-08-28 |  |  |  | 1 |  | The victim was working on the Khadsaliya Ag. Feeder. Due number of crossing of 220KV line, 66KV line and Malvav JGY feeder the victim meight have feel the induction. Hence the accident is only due to induction of the other feeder.
44 | BVN | Botad | Dhasa | Animal | 2007-08-15 |  |  |  |  | 1 | Snapping of LT conductor
45 | BVN | Mahuva | Mahvua R-1 | Human | 2007-08-31 |  |  | 2 | 1 |  | At anandjibhai Kalyanjibhai trust Ag. Land Chhapariyali village, PGVCL's LT Line has been passed. Under this line direct connection taken (illegally) by the victim's parents for electrification of one lamp in the hut under the farm. As per the statement o
46 | BVN | Botad | Paliyad | Animal | 2007-08-31 |  |  |  |  | 1 | Leackage current from the earthing of the DTC.
47 | BVN | Palitana | Gariyadhar | Animal | 2007-08-20 |  |  |  |  | 1 | The cable of the DTC was deteriorated and it was thouching with the DB. The animal came in contact with this DB and it get shcock and died.
48 | BVN | Palitana | Talaja | Human | 2007-08-24 |  |  | 1 |  |  | Snapping of LT Conductor
49 | BVN | Palitana | Talaja | Human | 2007-08-30 |  |  | 1 |  |  | Snapping of coatted conductor due to heavy rain.
50 | BVN | City-1 | Diaimond Chowk | Human ALM Name : Bipinbhai Kanajibhai Undaviya. | 2007-09-14 |  | 1 |  |  |  | Street light phase was ON. The victim came in contact with the strreet light phase and he got shock.
51 | BVN | BVN-R | Vallabhipur | Animal | 2007-09-21 |  |  |  |  | 1 | Snapping of LT conductor
52 | BVN | BVN-R | Dhola | Animal | 2007-09-22 |  |  |  |  | 1 | The LT guard wire was touching with the LT phase wire. Hence the current was pssing through the guard wire and the Girder pole. The animal came in contact with this girder and it got shock and it died.
53 | BVN | BVN-R | Dhola | Animal | 2007-08-30 |  |  |  |  | 1 | The conductor was touching with the LT X-arm due to the damage of binding wire of the shackle insulater. So the path was completed through the x-zrm and the girder pole. The animal came in contact with this girder and it got shock and it died.
54 | BVN | BVN-R | Sihor (R) | Animal | 2007-09-05 |  |  |  |  | 1 | Snapping of LT conductor
55 | BVN | Mahuva | Jesar | Animal | 2007-09-22 |  |  |  |  | 1 | Snapping of LT conductor
56 | BVN | Botad | Dhasa | Animal | 2007-09-19 |  |  |  |  | 1 | The load side cable of the transformer i.e. LT side cable was deterirated and the animal came in contact with this cable and it got shock and it died.
57 | BVN | Botad | Dhasa | Animal | 2007-09-22 |  |  |  |  | 1 | Due to brken of binding wire and deteriorated jumper the conductor was touching with the c-clamp and the current was passing through the c-clamp and the earthing wire. The animal came in contact with this earthing wire and it got shock and it died.
58 | BVN | Palitana | Palitana -R | Fatal Human Nikunj Kanajibhai | 2007-09-05 |  |  | 1 |  |  | The 11 KV line was passing over the house at village Bharatimba. The victim was on the tarrace and accidently he came in contact with the feeder wire and he got shock and he died.
59 | BVN | Palitana | Palitana-T | Animal | 2007-09-28 |  |  |  |  | 1 | Due to weak earthing tof the T/c the current was pssing through the earth of DP structure. The cow was passing near the DP and came in contct with the DP and it got shock and died. | The earthing is reactivated
60 | BVN | Palitana | Palitana-T | Non Fatal Human (Girl) Komalben Ramahibhai | 2007-10-10 |  |  |  | 1 |  | The accident is occured at Baharpara, Adpur Road, jurisdiction of the Palitna-T, the victim meight ahve in contact with the joint of broken single phase service line and she got shock. But there is no any evidance like black spot or blood on the service l | The deteriorated service is replaced.
61 | BVN | Palitana | Palitana-T | Animal | 2007-10-10 |  |  |  |  | 1 | Due to snapping of the street light conductor was fall down. The cow came in contact and it get shock and died. | Necessary maitenance is carried out
62 | BVN | Botad | Barwala | Bherumal Jethalal Bhil | 2007-10-11 |  |  |  | 1 |  | Due to electrocution the victim fall down and get injured. The victim is labourman of a contractor, he and co-worker are not giving any statement regarding the occrance of the accident. | Due to non giving statement of the coworker the factual reason is not coming out.
63 | BVN | Botad | Lakhavad (Dhol) | Animal | 2007-10-18 |  |  |  |  | 2 | Due to snapping of the conductor the animals came in contact with this snapped conductor and got shock and they died. | Necessary maitenance is carried out
64 | BVN | Palitana | Palitana-R | Non Fatal Human(Boy) Prakash Raghavbhai Chauhan | 2007-10-23 |  |  |  | 1 |  | Due to snapping of HT conductor the load side of the conductor was fall down and it was touching eith the fancing. The fancing was binded with the main iron gate of the temple. The victim came in contact with the gate and he got shock. | The three span to the HT line is replaced.
65 | BVN | BVN-R | Vallabhipur | Animal | 2007-10-28 |  |  |  |  | 1 | As per party's information PSC Pole was broken and fall downon buffallow and due to live wire of the pole the animal got shock and it died. But as per the rojkam there is no wire on the pole and the animal was 10' away from the broken pole.
66 | BVN | Palitana | Palitana-Rural | Fatal Human - Shri Bhupatbhai Shamjibhai Varsadiya | 2007-11-06 |  |  | 1
67 | BVN | City - 1 | Khargate | Non Fatal Human to Staff |  |  | 1
68 | BVN | BVN-R | SHIHOR-R | Fatal human | 2007-12-01 |  |  | 1 |  |  | Wire extended from nearby house to use electricity.It touched G I Wire used for drying cloths. Victim touched the G I Wire & got shocked & dead.
69 | BVN | BVN-R | SHIHOR-T | Fatal Animal-buffalow | 2007-12-20 |  |  |  |  | 1 | Phase cond of dead line of 11 kv nesda feeder are snapped and fall on 11kv shakun feeder and this dead line became live.Buffalow passing nearby came in contact with this live wire and shocked and died.
70 | BVN | city-1 | Diaimond Chowk | C N SOLANKI | 2008-01-08 |  | 1 |  |  |  | Main switch of streetlight fired due to earth fault when he switched on the main switch after attending fault
71 | BVN | palitana | palitana-r | Pravinbhai Govindbhai | 2008-01-09 |  |  | 1 |  |  | Victim was climbed on ag t/c and he touch live conductor and got shocked
72 | BVN | city-1 | Diaimond Chowk | Bhupatbhai Bachubhai Chauhan | 2008-01-09 |  | 1 |  |  |  | While climbing round pole he lost balance and fell down on ground
73 | BVN | BOTAD | BOTAD T-2 | Fatal Animal-buffalow | 2008-01-15 |  |  |  |  | 1 | SNAPPING OF CONDUCTOR
74 | BVN | CITY-1 | POWERHOUSE | THAKARSHIBHAI MAKAWANA | 2008-01-18 |  | 1 |  |  |  | Link switch of TC was disconnected before execution of work but power supply was not disconnected
75 | BVN | Palitana | PALITANA-R | Sajalben Bharatbhai Gohil | 02.02.08 |  |  |  | 1 |  | The victim was cutting the imali from the ambali tree with the help of an iron rod. The iron rod came in contact with HT live wire &get electrocuted.
76 | BVN | Palitana | PALITANA-R | Ghanshyambhai Jagdishbhai Gohil | 02.02.08 |  |  |  | 1 |  | The victim was cutting the imali from the ambali tree with the help of an iron rod. The iron rod came in contact with HT live wire &get electrocuted.
77 | BVN | Mahuva | mahuva-r | Bachubhai Jodhubhai , sh. Bhagvanbhai dayabhai | 07.02.08 |  |  |  | 1 |  | The wire broken due to truck accident
78 | BVN | Mahuva | mahuva-r | Bhola bhai Hakabhai Baraiya | 2008-07-02 |  |  | 1 |  |  | The victim touched with open starter and get electric shock . The accident is occurred at load side of the consumer
79 | BVN | Botad | paliyad | sh. Vinod bhai and batukbhai | 2008-02-21 |  |  |  | 1 |  | During the maintenance of Rangpur AG feeder the PSC pole broken and the two victim godhariya fall down with the pole 7 GET INJURED. This is a mechanical accident
80 | BVN | Botad | botad-r | sh. Kalusinh. | 22/02/08 |  |  |  | 1 |  | During the working on 11 kv feeder the victim got electrocution at 11 kv level and fall down.
81 | BVN | Botad | Botad-t | sh. Anopsinh ukabhai parmar | 23/02/08 | 1 |  |  |  |  | The victim climb the pole to attend complain no-533. He dis connect the power supply from the D.O Box of the T/C. The line was three phase 5-wire lt including the street light phase was dead. But when the victim came in contact with the street light phase
82 | BVN | Palitana | Trapaj | Dharaben Vinubhai | 2008-12-03 |  |  |  | 1 |  | Due to leakge from electric pump in office primises
83 | BVN | Bhavnagar rural | shihor-r | bhopabhai kalubhai koli | 2008-03-05 |  |  | 1 |  |  | due to collaps of truck to the pole and it was broken and falls on victim &get died.
1 | AMR | Amreli-1 | Liliya | Sh. Khushalbhai Shambubhai Gajera | 2007-04-17 | 0 |  | 1 |  |  | Winding the DO in his Ag. group without permission of company
2 | AMR | Una | Una-1 | Sh. Bhupendra Kantilal Bariya | 2007-04-20 |  |  |  | 1 |  | Contractor man felt from the pole and the mech. accident occurred
3 | AMR | Amreli-1 | Lathi | A buffalo of Sh. Merambhai Vaghabhai | 2007-04-21 |  |  |  |  | 1 | Buffelo had died due to contact with live condctor..
4 | AMR | Amreli-1 | Babra | A cow of Sh. Pathubhai Basiya | 2007-04-21 |  |  |  |  | 1 | Snapping of conductor
5 | AMR | Amreli-1 | Babra | Sh. Vinubhai Ramji | 2007-05-04 |  |  | 1 |  |  | While sharpening the Ag. motor cable in his own room the accident occurred
6 | AMR | S'Kundla | Rajula | FH-(1) Sh. Laljibhai Devayatbhai (2) Smt. Nayanaben Devayatbhai ; NFH-(1) Sh. Devayatbhai Tapubhai (2) Smt. Chakuben devayatbhai ; FA-2 bullock | 2007-05-06 |  |  | 2 | 2 | 2 | 11 KV conductor fell and touched his bullock cart
7 | AMR | S'Kundla | SKD (T) | Sh. Ramesh R. Damor, ALM | 2007-05-15 |  | 1 |  |  |  | Fell from the gurder pole and the mech. accident occurred |  | Not utilised due to not issued by Division
8 | AMR | Amreli-2 | Bagasara | Smt. Chanduben Babubhai | 2007-06-08 |  |  | 1 |  |  | Contact with short circuit motor in his house
9 | AMR | Amreli-2 | Bagasara | A buffalo of Sh. Bharat Jilubhai Vala | 2007-06-15 |  |  |  |  | 1 | Contact with PSC pole earthing
10 | AMR | Una | Una (T) | (1) Sh. Salimbhai Mohabatsah (2) Smt. Rehanaben Salimbhai | 2007-06-17 |  |  |  | 2 |  | Due to broken of 11KV feeder jumper fualt on dish TV cable power had passed on it
11 | AMR | Una | Una-1 | A bullock of Sh. Bijal Bhikha Bambhaniya | 2007-06-19 |  |  |  |  | 1 | Contact with LT live conductor
12 | AMR | Amreli-1 | Liliya | A buffalo of Sh. Babubhau Jadavbhai | 2007-06-23 |  |  |  |  | 1 | Snapping of LT conductor
13 | AMR | Amreli-1 | Lathi | Sh. Shambhubhai Nagjibhai Radadia | 2007-06-24 |  |  | 1 |  |  | Contact with live wire fallen from LT pin insulator
14 | AMR | Una | Una-1 | A buffalo of Sh. Kanubhai Bhimbhai Jasani | 2007-06-24 |  |  |  |  | 1 | Due to leakage from T/C earthing wire
15 | AMR | Una | Kodinar-2 | Buffalo of Sh. Govind Mala Chavda | 2007-06-24 |  |  |  |  | 1 | Contact with live earthing wire
16 | AMR | S'Kundla | SKD(R) | (1) Sh. Zakir Husen Usman Miya V.S. Helper (2) Sh. Gautam Lalji Dafda | 2007-06-25 |  | 2 |  |  |  | While working on the T/C, suddenly the induction was started from live LT condctors. |  | Sefty belt issued in gang but not used
17 | AMR | Amreli-1 | Lathi | Two bullock of sh. Pravinbhai Virjibhai Malavia | 1907-06-04 |  |  |  |  | 2 | Snapping of LT conductor
18 | AMR | Amreli-1 | Chalala | Ankhlo of Sh. Hanifbhai Kasambhai | 1907-06-29 |  |  |  |  | 1 | Leckage of power at street light brocken,open cond. Tutch the pole
19 | AMR | Una | Una-1 | A cow of Sh. Ramjibhai Khimjibahi Parmar | 1907-06-25 |  |  |  |  | 1 | Snapping of LT conductor
20 | AMR | Una | Kodinar-2 | A buffalo of Sh. Rama Sidi | 1907-06-17 |  |  |  |  | 1 | Snapping of LT conductor
21 | AMR | Amreli-1 | Damnagar | Sh. Praduman Chhotala Joshi | 3-7-07 |  |  |  | 1 |  | Fall from the pole and mech. Accident | Victim is Panchayat helper but he has not used any safety tools while working on line. | Instruction has already been given to line staff for using safety tools while working.
22 | AMR | Amreli-1 | Amreli R | Bullock of Sh. Bhupatbhai Valkubhai | 12-7-07 |  |  |  |  | 1 | Snapping of LT conductor
23 | AMR | Amreli-1 | Babra | Smt. Shardaben Mavjibhai | 23-7-07 |  |  | 1 |  |  | Contect with leakage current from butter milk making machine motor.
24 | AMR | Amreli-1 | Babra | A Four Sheep of Sh. Khima Amrabhai | 24-7-07 |  |  |  |  | 1 | Snapping of LT conductor
25 | AMR | Amreli-1 | Chital | A Cow of Sh. Kalubhai Harsurbhai | 25-7-07 |  |  |  |  | 1 | Leckage power of T/C earthing
26 | AMR | S'Kundla | Jafrabad | A Bullock of sh. Chitarbhai Kadvabhai | 28-7-07 |  |  |  |  | 1 | 11KV cond. Fall from Disc Insulator and Bullock tutch.
27 | AMR | S'Kundla | Rajula | A Buffalow of Sh. Ghosabhai Jeturbhai | 29-7-07 |  |  |  |  | 1 | LT conductor fall rfrom the pole and contect.
28 | AMR | Una | Kodinar-1 | A Buffalow of Sh. Karsanbhai Rambhai | 6-7-07 |  |  |  |  | 1 | Contect with live 11KV conductor
29 | AMR | Una | Kodinar-2 | A cow of Sh. Dhirubhai Jikabhai | 30/6/07 reporting on July - 07 |  |  |  |  | 1 | Leckage power of T/C earthing wire
30 | AMR | Una | Kodinar-1 | A two Buffalow of Sh. Alabhai Chinabhai | 1-7-07 |  |  |  |  | 1 | Snapping of conductor.
31 | AMR | Una | Una-2 | A Buffalow of Sh. Mohan Rana | 10-7-07 |  |  |  |  | 1 | Tuch of LT cable of T/C center.
32 | AMR | Amreli-2 | Kunkavav | Sh. Keshubhai Karsanbhai | 28/6/07 reporting on July - 07 |  |  |  | 1 |  | Accident took place when cond. of LT line fell in C clamp and came into contact of earthing wire.
33 | AMR | Amreli-2 | Chalala | A buffalow of sh Laljibhai Devabhai | 9/7/2007 |  |  |  |  | 1 | Contect with LT Conductor.
34 | AMR | Amreli-2 | Dhari | A Cow of Sh. Hirabhai Arfebbhai | 21/6/07 reporting on July-07 |  |  |  |  | 1 | Leckage of PSC pole earthing
35 | AMR | Amreli-2 | Dhari | A Cow of Sh. Anakbhai Gabhrubhai | 24/6/07 reporting on July - 07 |  |  |  |  | 1 | Leckage power of transformer earthing
36 | AMR | Amreli-2 | Dhari | A Bullock of Sh. Nanjibhai Savjibhai | 8-7-07 |  |  |  |  | 1 | Leckage of GUY wire
37 | AMR | Amreli-2 | Vadia | Sh. Yasvantbhai Bhupatbhai Solanki | 29-7-07 |  |  |  | 1 |  | Victim is Panchayat helper and Accident occurred when the crossing live line came into contact of the span of dead line on which victim was working |  | It is necessary to instruct line staff strictly to make all crossing live lines dead, where the work is to be carried out by disconnecting the flow of supply before starting the work.
38 | AMR | Una | Una-2 | Sh. Mala Ram Sanklhat | 28-7-07 |  |  |  | 1 |  | Victim was tutched live 11KV cond. Near his Balcony. |  | Notice has been served to the victim, either to dismantle the balcony or to produce the permission given by the connected Nagarpalika regarding construction of the balcony.
39 | AMR | Amreli-1 | Babra | A Buffalow of Sh.Valabhbhai Shamjibhai. | 29/7/2007. Reporting on Aug."07 |  |  |  |  | 1 | Leakage power of Tranformer earthing.
40 | AMR | Amreli-1 | Liliya | Sh. Popatbhai Maganbhai Dhanani | 2007-09-08 |  |  |  | 1 |  | Snapping of LT conductor at shakle point. |  |  | Aug-08
41 | AMR | S'Kundla | Khambha | Sh.A.R.Bhatt. (App. Line Man) | 2007-10-08 |  | 1 |  |  |  | When working on 11kv nanudi feeder, He experienced induction and fall from the pole. | Not used any safety tools while working on line. | Instruction has already been given to line staff for using safety tools while working. | Aug-08
42 | AMR | S'Kundla | SKD(R) | Sh. Rambhai Chhaganbhai Dhameliya. | 28/7/2007 Reporting on Aug.07 |  |  | 1 |  |  | Victim brother informe on dt.30.7.07, after two days of accedent occurred. We have not found any evidance at the site but victime had try to Lungar from Ex.Lt line. |  |  | Aug-08
43 | AMR | Una | Una-2 | A cow of Sh. Kiritbhai Anupbhai | 3-8-07 |  |  |  |  | 1 | Snapping of LT conductor |  |  | Aug-08
44 | AMR | Una | Una-1 | A buffalo of Babubhai Mulubhai | 6-8-07 |  |  |  |  | 1 | Snapping of LT conductor |  |  | Aug-08
45 | AMR | Una | Una-1 | A buffalo of Hirabhai Vaghbhai | 13-8-07 |  |  |  |  | 1 | Snapping of 11 KV conductor |  |  | Aug-08
46 | AMR | Una | Una-2 | A buffalo of Jayantibhai Rambhai | 16-8-07 |  |  |  |  | 1 | Snapping of LT conductor |  |  | Aug-08
47 | AMR | Amreli-2 | Dhari | A buffalo of Bhagvanbhai Thakarshibhai | 17-7-07 Reporting on Aug. 07 |  |  |  |  | 1 | Leakage current of LT pole earthing |  |  | Aug-08
48 | AMR | Amreli-2 | Kunkavav | Sh. Shankarbhai Lakahbhai Nayak | 2-8-07 |  |  | 1 |  |  | Leakage earthing wire of transformer, and touched with guy wire, victim was touched guy wire |  | Necessary maintenance of transformer is carried out | Aug-08
49 | AMR | Amreli-2 | Kunkavav | Sh. V.M. Dabhi (V.S. Helper) | 9-8-07 |  | 1 |  |  |  | Sh. V.M. Dabhi was attending a lighting fault on PSC pole, and he experienced induction and fell from pole | He has not used any safety tools while working on line | Instruction has already been given to line staff for using safety tools while working. | Aug-08
50 | AMR | Amreli-2 | Chalala | A buffalo of Sh. Ghanshyamhai Ukabhai | 11-8-07 |  |  |  |  | 1 | Leakage of transformer earthing wire |  |  | Aug-08
51 | AMR | Amreli-2 | Bagasara | A buffalo of Ghelabhai Ukabhai | 14-8-07 |  |  |  |  | 1 | Snapping of LT conductor |  |  | Aug-08
52 | AMR | Amreli-2 | Kunkavav | Sh. Hiteshbhai Devabhai Padhiyar | 18-8-07 |  |  | 1 |  |  | Victim was removing flexible wire from plug one wire were on his hand, and other wire in plug, he touched open wire |  |  | Aug-08
53 | AMR | Amreli-2 | Bagasara | A cow of Sh. Jasabhai Devayatbhai | 26-8-07 |  |  |  |  | 1 | Snapping of L.T. cond. |  |  | Aug-08
54 | AMR | Amreli-2 | Dhari | A buffalo of Punjabhai Caprajbhai | 10-8-07 |  |  |  |  | 1 | Leakage power of X'mer earthing |  |  | Aug-08
55 | AMR | S'Kundla | Rajula | FH - Sh. Rameshbhai Jivabhai NFH - (1) Sh. Kanubhai Ravjibhai | 19-8-07 |  |  | 1 | 1 |  | Due to heavy rain and wind presure tree branch fall on L.T. live cond. |  |  | Aug-08
56 | AMR | Una | Kodinar-1 | A buffalo of Sh. Bhimabhai Balubhai | 11-8-07 |  |  |  |  | 1 | Leakage power of Tranformer earthing. |  |  | Aug-08
57 | AMR | Una | Kodinar-2 | A buffalo of Mandanbhai Hamirbhai | 12-8-07 |  |  |  |  | 1 | Leakage power of PSC pole earthing |  |  | Aug-08
58 | AMR | Una | Una-1 | A buffalo of Ranabhai Sarmanbhai | 27-8-07 |  |  |  |  | 1 | Leakage power of Tranformer earthing. |  |  | Aug-08
59 | AMR | Una | Kodinar-1 | A buffalo of Masaribhai Bhagvanbhai | 28-8-07 |  |  |  |  | 1 | Snapping of L.T. cond. |  |  | Aug-08
60 | AMR | Una | Kodinar-1 | A bullock of Pratapbhai Kacharabhai | 29-8-07 |  |  |  |  | 1 | Snapping of L.T. cond. |  |  | Aug-08
61 | AMR | Una | Una-2 | Smt. Rudiben Kanabhai Sankhat | 11-8-07 |  |  |  | 1 |  | Snapping of L.T. cond. |  |  | Aug-08
62 | AMR | Una | Una-2 | A buffalo of Lajibhai Bhanabhai | 10-8-07 |  |  |  |  | 1 | Snapping of L.T. cond. |  |  | Aug-08
63 | AMR | Una | Una (T) | A bullock of ValiMahmad Chauhan | 10-8-07 |  |  |  |  | 1 | Snapping of L.T. cond. |  |  | Aug-08
64 | AMR | Una | Una-2 | A bullock of Hajibhai Lakhabhai | 22-8-07 |  |  |  |  | 1 | Snapping of L.T. cond. |  |  | Aug-08
65 | AMR | Amreli-1 | Babra | Nirenbhai Rameshbhai Parmar | 30-8-07 |  |  | 1 |  |  | The victim came in contact with live 1 Ph wire due to faulty two pin connected with 1 Ph motor in his private premises. |  |  | Aug-08
66 | AMR | Amreli-1 | Babra | Sh.Arvindbhai Chhatrasing Bariya (contractar Man) | 2007-09-09 |  |  | 1 |  |  | Victim was working on line and fell from the pole Mech Acct.
67 | AMR | Amreli-1 | Amreli-R | 2no's Bullock of Sh.Govindbhai Nanjibhai | 2007-09-10 |  |  |  |  | 1 | Snapping of LT conductor
68 | AMR | Amreli-2 | Chalala | A Bullock of Sh.Nareshbhai Kanabhai. | 2007-09-03 |  |  |  |  | 1 | Snapping of LT conductor
69 | AMR | Amreli-2 | Dhari | Sh.Ashokbhai Laxmanbhai Rathava (ALM) | 2007-09-09 |  | 1 |  |  |  | Viktim was working 11kv fdr.but LT of Other fdr.cross and victim experienced induction and fell from pole. | He has not used any safety tools while working on line | Instruction has already been given to line staff for using safety tools while working.
70 | AMR | Amreli-2 | Dhari | Smt.Bhanube Kantilal | 20-09-07 |  |  | 1 |  |  | Accident accured in his premises.
71 | AMR | Amreli-2 | Dhari | 2no's cow of Sh.Gokalbhai Danabhai | 24-09-07 |  |  |  |  | 1 | Snapping of LT conductor
72 | AMR | Amreli-2 | Dhari | Buffalo of Sh. Madhabhai Dhanjibhai | 27-09-07 |  |  |  |  | 1 | Snapping of LT conductor
73 | AMR | S'Kundla | Savarkundla® | Buffalo of Sh.Rameshbhai Virjibhai. | 2007-03-09 |  |  |  |  | 1 | Leakage current of LT pole earthing
74 | AMR | S'Kundla | Rajula | Buffalo of Sh.Mulubhai Smatbhai. | 25-09-07 |  |  |  |  | 1 | Leakage current of LT pole earthing
75 | AMR | Una | Una-2 | Bullock of sh.Ajibhai lakhabhai | 22-08-07 |  |  |  |  | 1 | Snaping of LT conductor
76 | AMR | Una | Una-1 | Buffalo of sh.Natha dana | 2007-01-09 |  |  |  |  | 1 | Leakage current of Transeformer earthing wire
77 | AMR | Una | Una-2 | Buffalo of sh.Nanabhai atabhai | 16-09-07 |  |  |  |  | 1 | Leakage current of Transeformer earthing wire
78 | AMR | Una | Una-1 | Buffalo of sh.Hamirbhai Jethabhai | 20-09-07 |  |  |  |  | 1 | Snaping of LT conductor
79 | AMR | Una | Una-1 | 3'no of Buffalo sh.Bhikhabhai baubhai | 21-09-07 |  |  |  |  | 1 | Snaping of LT conductor
80 | AMR | Una | Kodinar-2 | Buffalo of sh.kadubhai ukabhai | 22-09-07 |  |  |  |  | 1 | Snaping of LT conductor
81 | AMR | Una | Kodinar-2 | Buffalo of sh.Dadubhai sardulbhai | 27-08-07 |  |  |  |  | 1 | Leakage current of Transeformer earthing wire
82 | AMR | Una | Kodinar-2 | Buffalo of sh.Manubhai naranbhai | 29-08-07 |  |  |  |  | 1 | Snaping of LT conductor
83 | AMR | Una | Una-1 | A cow of sh.Nanabhai pachabhai | 27-09-07 |  |  |  |  | 1 | Leakage current of Transeformer earthing wire
84 | AMR | Una | Kodinar-2 | Buffalo of sh.Ghelabhai tapubhai | 18-09-07 |  |  |  |  | 1 | Leakage current of Transeformer earthing wire
85 | AMR | Una | Kodinar-2 | Buffalo of sh.Ranjitbhai naranbhai | 26-09-07 |  |  |  |  | 1 | Leakage current of Transeformer earthing wire
86 | AMR | Una | una_1 | FA to small ox of Shri Balubhai Kalubhai Gujariya | 29.09.2007 |  |  |  |  | 1 | not found any kind of fault in PGVCL line, accident occurred due to any reason.
87 | AMR | Una | Kodinar-1 | Farid Hussain Dhoki | 30.09.2007 |  |  | 1 |  |  | by taking illigeal power supply from pole non consumer and electrocuted.
88 | AMR | AMR-I | AMR-T | Champaben Harjibhai Solanki | 1.10.2007 |  |  |  | 1 |  | pvc twin core s/L accidently broken by private vehicle and said broken s/L wounded around the neck of victim
89 | AMR | Una | kodinar-2 | NF_Mechanical accident to Shri Samat Hira Madha | 2.10.2007 |  |  |  | 1 |  | due to breaking of psc pole.
90 | AMR | AMR-II | Bagasara | FA to cow of shri Lalabhai Gababhai Matiya | 3.10.2007 |  |  |  |  | 1 | snapping of 11 kv conductor from disc insulator
91 | AMR | Una | una_2 | FA to 2 no of Buffallo (1) shri Lakha Bhaya jadav & (2) shri Jivabhai Rambhai Parmar | 5.10.2007 |  |  |  |  | 1 | snapping of LT conductor
92 | AMR | Una | kodinar-I | FA to Buffalo of shri Oghadbhai Ranabhai Parmar | 9.10.2007 |  |  |  |  | 1 | due to snapping of conductor
93 | AMR | Amreli-2 | Bagasara | NFH_Mechanical accident to Deptt. Person Shri A.H.Chauhan (ALM) | 9.10.2007 |  | 1 |  |  |  | loosing balance during working on DP Structure due to slipping of conductor from disc insulator
94 | AMR | AMR-II | Dhari | FA to Chhagan Parsottam Sardhara | 9.10.2007 |  |  | 1 |  |  | Snapping of LT conductor
95 | AMR | Amreli-2 | Dhari | NFH to Deptt. Person Manishkumar M Pandya_VS Helper | 9.10.2007 |  | 1 |  |  |  | while attending the jumper fault experience jerk and felt from the transformer center.
96 | AMR | AMR-II | Dhari | FA to cow (Rowery) | 13.10.2007 |  |  |  |  | 1 | Snapping of LT conductor
97 | AMR | AMR-II | Dhari | FA to 5 nos of wild animal (3 lioness + 2 cub) | 12.10.2007 informed on dtd. 19.10.2007 |  |  |  |  | 1 | Ag-consumer have illigelly connected power supply from LT line passing through his field in the fencing lying around his ag. Land. The said animals came in contact and electrocuted.
98 | AMR | AMR-II | Chalala | NF_Mechanical Accident to o/s human shri Rajubhai Nanjibhai Rathod age_22 yrs at village Lakhapadar | 24.10.2007 |  |  |  | 1 |  | due to breaking of psc pole
99 | AMR | AMR-I | AMRELI RURAL | Non fatal accident to Shri Hanubha Takhtasinh Jadeja age 40 yrs at village Bai Dudhala | 3.11.07 |  |  |  | 1 |  | While providing DO fuse wire of TC Victim used Short Bamboo rod and climb at some height on TC pole, DO fuse wire touched to DO Angle, Victim got electric shock through Earth wire and met with Non fatal accident | partially utlilized | victim is a contractor person and issued a notice to the victim for utlization of safety tools
100 | AMR | UNA | UNA-II | fatal accident to buffallo of shri Balubhai Lakhabhai Dangodra at village Juna_Ugala | 4.11.07 |  |  |  |  | 1 | snapping of 11 KV conductor |  | maintainance work carried out
101 | AMR | UNA | kodinar-II | fatal accident to cow of shri Hirabhai Ranabhai Jotava at village vadnagar | 5.11.07 |  |  |  |  | 1 | due to heavy rain and wind pressure conductor snapped |  | maintainance work carried out
102 | AMR | UNA | kodinar-II | fatal accident to Nathiben Jeshabhai Gadhe and Non fatal Accident to Valiben Kalabhai Chandera | 11.11.07 |  |  | 1 | 1 |  | L T pole was broken by truck driver Motigar Arfebbhai Goswami while driving truck No. GJ -10W -7981 in rough manner. One woman fell down due to breaking of LT P.S.C. pole and met with fatal accident. Another got electric shock due to falling of live cond |  | FIR LODGE AGAINST THE TRUCK DRIVER BY THE CONCERN DE vide no 114/07
103 | AMR | UNA | kodinar-II | fatal accident to o/s late Arshibhai Kanabhai Chudasama at village Dolasa | 16.11.07 |  |  | 1 |  |  | while pulling out mobile charger from the three pin socket accidently came in contact of live phase and electrocuted | victim himself is responsible | victim himself was responsible, said accident occurred in his private premises.
104 | AMR | Una | kodinar-II | Fatal accident to O/S late Rajesh Govind Vaja at village Mityaz Navapara | 29.12.07 | 0 | 0 | 1 | 0 | 0 | snapping of 11KV conductor from the shackle point insulator hardware and snapped conductor from load side lying on the road and at a same time victim passing through the road and came in contact with the snapped conductor and electrocuted.
105 | AMR | S'Kundla | Jafrabad | Non fatal accident to Shri Sarvansinh age 40 yrs at village Gangad Taluka Jafrabad | 31.12.07 | 0 | 0 | 0 | 1 | 0 | container having height having 9.6' touched the 11 kv line and tyre of the container was totally burnt, when victim came in the contact of live part of the container, he got the electric shock.
106 | AMR | Una | kodinar-II | Fatal accident to buffallo of shri Bhupatbhai Kantibhai Soanki at villageNani Garmali tal:Chalala | 7.01.08 | 0 | 0 | 0 | 0 | 1 | leakage of current from the transformer earthing of village t/c |  | maintainance work carried out.
107 | AMR | Amreli_I | Chital | Fatal accident to O/S human late sumitraben VajupariGosai-age 32 yrs at village Manchiyala taluka amreli dist amreli | 06.3.08 | 0 | 0 | 1 | 0 | 0 | open extention code wire touched the iron roof of house and hence leakage current flow through the iron string utlised for hanging the wet clothes, victim touched the iron string and got electric shock. |  | victims herself was responsible and hence said accident occurred in her private primises.
108 | AMR | Amreli_I | Lilya | Fatal accident to he-buffallo and she buffallo of shri Kanubhai Dayabhai Bambha at village Mota kankot Tal;Lilya, Dist Amreli | 25.03.08 | 0 | 0 | 0 | 0 | 2 | private truckGJ11U 8691 damaged the psc pole and hence conductor snapped on the animals and animal came contact with live conductor and electrocuted |  | FIR lodge against the vehicle driver of v.no:GJ11 U 869. FIR lodge by the owner of the animal shri Kanubhai Dayabhai Bambha.
1 | SNR | SNR 1 | LIMBADI ( T) | Hasmukhbhai Bababhai | 2007-05-17 |  |  |  | 1 |  | Snapping of Conductor | NA | NA
2 | SNR | SNR 1 | S`nagar city 1 | Daxaben Pareshbhai Parmar | 2007-05-24 |  |  | 1 |  |  | Internal wiring | NA | NA
3 | SNR | SNR 1 | LIMBADI ( T) | Bijalbhai Ishwerbhai Rangpara | 2007-06-12 |  | 1 |  |  |  | Slipping from pole |  | NA
4 | SNR | SNR 1 | Jorawernagar | Dhirubhai Devjibhai Makwana | 2007-06-29 |  | 1 |  |  |  | Entered in induction zone of HT while working on LT Line
5 | SNR | SNR 2 | Muli | Nakubhai Hathibhai | 2007-06-01 |  |  |  | 1 |  | Snapping of Conductor | NA | NA
6 | SNR | SNR 2 | Muli | Mukeshbhai Bijalbhai | 2007-06-01 |  |  |  | 1 |  | Snapping of Conductor | NA | NA
7 | SNR | DHG | DGH R | Rajeshbhai Ratilal Darji | 2007-06-05 |  |  |  | 1 |  | Snapping of conductor | NA | NA
8 | SNR | SNR 1 | LSD R | BUFF of Bhikhubhai Shivubhai | 2007-06-01 |  |  |  |  | 1 | Broken of LT Pole | NA | NA
9 | SNR | SNR 1 | Wadhwan | Cow of Bijalbhai Sagrambhai | 2007-06-21 |  |  |  |  | 1 | Snapping of Conductor | NA | NA
10 | SNR | SNR 1 | LSD R | BUFF of Nazabhai Dhanabhai | 2007-06-21 |  |  |  |  | 1 | TC Earthing Leakage | NA | NA
11 | SNR | SNR 1 | S`nagar city 2 | Cow of Sagrambhai Malabhai | 2007-06-06 |  |  |  |  | 1 | Snapping of Conductor | NA | NA
12 | SNR | SNR 1 | LSD R | BUFF of Kasirambhai Nagarbhai | 2007-06-15 |  |  |  |  | 1 | Pole Earthing Leakage | NA | NA
13 | SNR | SNR 2 | Sayla | Panchabhai Nathabhai Bharwad | 2007-06-17 |  |  |  |  | 1 | TC Earthing Leakage | NA | NA
14 | SNR | SNR 2 | Muli | Buffalow of Madhuben Becharbhai | 2007-06-18 |  |  |  |  | 1 | TC Earthing Leakage | NA | NA
15 | SNR | SNR 2 | Muli | Bufallow of Ratansang Malubhai | 2007-06-21 |  |  |  |  | 1 | HT Pole earthing GI wire struct in horn of BUFF. Which touch to jumper on pole | NA | NA
16 | SNR | SNR 2 | Chotila | BUFF of Rupabhai Khimabhai | 2007-06-19 |  |  |  |  | 1 | Pole Earthing Leakage | NA | NA
17 | SNR | DHG | Patdi | Buffalow of Balubha Jalamsang | 2007-06-15 |  |  |  |  | 1 | Snapping of conductor | NA | NA
18 | SNR | SNR 2 | Sayla | Panchabhai Nathabhai Bharwad | 2007-06-17 |  |  | 1 |  |  | TC Earthing Leakage | NA | NA
19 | SNR | DHG | Rajsitapur | Kanjibhai Rajabhai Rabari | 2007-05-31 |  |  | 1 |  |  | Internal wiring | NA | NA
20 | SNR | DHG | DGH R | Altafbhai Bachubhai Sipai | 2007-06-05 |  |  |  | 1 |  | Snapping of conductor | NA | NA
21 | SNR | DHG | DGH R | Kalubhai Amarshibhai | 2007-06-05 |  |  |  | 1 |  | Snapping of conductor | NA | NA
22 | SNR | DHG | Halwad | Satabhai Butabhai Bharwad |  |  |  |  | 1 |  | Mech Accedent Pole broken | NA | NA
23 | SNR | SNR 1 | S`nagar city 1 | Cow of Bhimabhai Satabhai Bharwad | 2007-07-09 |  |  |  |  | 1 | Leakage from st ltg fixture | NA | NA
24 | SNR | SNR 2 | Than | BUFF of Bhabhalubhai Vastabhai Khachar | 2007-07-05 |  |  |  |  | 1 | TC Earthing Leakage | NA | NA
25 | SNR | DHG | Rajsitapur | Maheshbhai Ranchhobhai Koli | 2007-07-01 |  |  | 1 |  |  | Direct contact with 22 KV line | NA
26 | SNR | DHG | Halwad | BUFF of Musa Daud Ghanchi | 2007-07-05 |  |  |  |  | 1 | Snapping of conductor | NA | NA
27 | SNR | DHG | Halwad | BUFF Of Dilipbhai Shivabhai Patel | 2007-07-02 |  |  |  |  | 1 | Snapping of conductor | NA | NA
28 | SNR | DHG | Halwad | BUFF Of Bipinbhai Chhaganbhai | 2007-07-14 |  |  |  |  | 1 | TC Earthing Leakage | NA | NA
29 | SNR | DHG | Patdi | BUFF of GovindbhaiSandhabhai | 2007-06-30 |  |  |  |  | 1 | Snapping of conductor | NA | NA
30 | SNR | SNR 2 | Muli | Kanchanben Dhirubhai Rathod | 2007-06-01 |  |  | 1 |  |  | Internal wiring | NA | NA
31 | SNR | DHG | Patdi | Babubhai Bhagwandas Mali | 2007-06-25 |  |  | 1 |  |  | Internal wiring | NA | NA
32 | SNR | SNR 1 | LSD R | Kishorbhai Bhavanbhai Chawda | 2007-07-13 |  |  | 1 |  |  | Internal wiring | NA | NA
33 | SNR | SNR 1 | LSD R | BULL OF SHARIFABEN RUSTAMBHAI | 2007-07-15 |  |  |  |  | 1 | Snapping of conductar | NA | NA
34 | SNR | SNR 1 | LSD R | Shafiq Yakubbhai Bhadula | 2007-07-31 |  |  | 1 |  |  | Snapping of conductar | NA | NA
35 | SNR | SNR 1 | LSD R | Kanjibhai Keshubhai Makwana | 2007-08-04 |  |  | 1 |  |  | Internal wiring | NA | NA
36 | SNR | SNR 1 | Jorawernagar | Atulbhai Devendrabhai Trivedi ALM | 2007-08-03 |  | 1 |  |  |  | Mechanical Accedent | Not
37 | SNR | SNR 2 | S`nagar Rural | Buff. Of Laxmanbhai Kalubhai | 2007-08-01 |  |  |  |  | 1 | TC Earthing Leakage
38 | SNR | DHG | DHG Rural | Bhikhubhai Hindubhai Saraiya | 2007-08-08 |  |  | 1 |  |  | Internal wiring | NA | NA
39 | SNR | DHG | Halwad | Hiteshbhai Jamanbhai Jasani | 2007-08-14 |  |  | 1 |  |  | Matter is under investigation | NA | NA
40 | SNR | SNR 2 | Chotila | She Horse Of Sh Bhabhlubhai Pithubhai | 2007-08-03 |  |  |  |  | 1 | Leakage of earthing | NA | NA
41 | SNR | SNR 1 | Wadhwan | Kapil Khimjibhai Bhatt | 2007-08-28 |  |  | 1 |  |  | Came in contact of live LT Phase, while climbed on truck. | NA | NA
42 | SNR | SNR 1 | S`nagar city 2 | Nilamben | 2007-07-10 |  |  |  | 1 |  | Leakage from st ltg fixture | NA | NA
43 | SNR | SNR 1 | S`nagar city 1 | Cow of Sh Devabhai Kunvarabhai | 2007-07-02 |  |  |  |  | 1 | Snapping of Conductor | NA | NA
44 | SNR | SNR 1 | LSD R | BUFF of Dashrathbhai Gangubhai | 2007-08-27 |  |  |  |  | 1 | Snapping of conductar | NA | NA
45 | SNR | DHG | PATADI | Buff of Somabhai Gandabhai | 2007-07-29 |  |  |  |  | 1 | Snapping of conductor | NA | NA
46 | SNR | SNR 1 | LSD R | BUFF of Sh Kasam Umar | 2007-09-10 |  |  |  |  | 1 | Leakage of earthing | NA | NA
47 | SNR | SNR 2 | Sara | Buff of Sh Chhhana Chatur | 2007-09-25 |  |  |  |  | 1 | Bufalow came in contact of 11 KV through Stay, while rubbing head with stay | NA | NA
48 | SNR | SNR 2 | Sayla | Lalabhai Kacharabhai Patel | 2007-09-12 |  |  | 1 |  |  | Came in contact of live 11 KV Line on Roof of hotel | NA | NA
49 | SNR | SNR 2 | Sayla | Ox of Sh Hamirbhai Dolabhai | 2007-09-29 |  |  |  |  | 1 | Snapping of Conductor | NA | NA
50 | SNR | SNR 2 | S`nagar Rural | Cow of Sh Manjibhai Chhaganbhai Panara | 2007-09-28 |  |  |  |  | 1 | Snapping of Conductor | NA | NA
51 | SNR | DHG | Halwad | Buff of Sh Rameshbhai Bhurabhai Bharwad | 2007-09-24 |  |  |  |  | 1 | Snapping of Conductor | NA | NA
52 | SNR | DHG | PATADI | Cow of Sh Hindubhai Vastabhai | 2007-08-29 |  |  |  |  | 1 | Snapping of Conductor | NA | NA
53 | SNR | SNR 1 | LSD R | Hiteshkumar Dalpatbhai at vill Khambhalav | 2007-09-19 |  |  |  | 1 |  | Came in contact of HT Line | n a
54 | SNR | SNR 1 | S`nagar city 1 | Meenaben Bhupatbhai Vaghela | 2007-09-22 |  |  | 1 |  |  | Internal wiring
55 | SNR | SNR 1 | LSD R | BUFF of Sh Rameshbhai Dayaram Dalwadi Karmad | 2007-09-23 |  |  |  |  | 1 | Leakage of earthing
56 | SNR | SNR 1 | S`nagar city 2 | Dipakbhai Premjibhai Parmar Employee P&T | 2007-10-03 |  |  | 1 |  |  | Came in contact of LT while tying the P&T line on LT Pole
57 | SNR | SNR 1 | LSD R | Hiraben Dalpatbhai Rathod At vill Ankevaliya | 2007-10-03 |  |  |  | 1 |  | Snapping of LT Conductor
58 | SNR | SNR 1 | LSD R | BUFF of Sh Bhagwan Arfeb Jograna At vill Ranagadh | 2007-10-11 |  |  |  |  | 1 | Snapping of LT Conductor
59 | SNR | DHG | DHG Rural | Sh Girishbhai Natvarbhai Raval LM | 2007-10-05 | 1 |  |  |  |  | Mech. Accd. Due to PSC Pole Broken
60 | SNR | SNR 2 | S`nagar Rural | Cow of Sh Manji Chhagan At vill Dudhrej | 2007-09-28 |  |  |  |  | 1 | Snapping of HT Conductor
61 | SNR | SNR 1 | S`nagar city 1 | Buff of Sh Laljibhai Merabhai Bharwad | 2007-11-08 |  |  |  |  | 1 | Leakage of StreetLight Ph
62 | SNR | SNR 2 | Chotila | Buff of Sh Ranchhodbhai Dayabhai Rajpara vill Mokasar | 2007-11-08 |  |  |  |  | 1 | Leakage of earthing
63 | SNR | DHG | Rajsitapur | R G Vora ALM, Rajubhai Masarusinh, Madanbhai Masrusinh at vill Dudapur | 2007-11-19 |  | 1 |  |  |  | Cont.`s labor climbed on live line for rejumpering, while ALM & other one working on dead section got momentory jerk of 11 KV Power.
64 | SNR | SNR 1 | LSD R | Sh Ghanshyambhai Bhikhabhai Chauhan At vill Chokadi | 2008-07-03 |  |  | 1 |  |  | Came in direct contact of 11 KV line while filling the building Slabe. | NA | NA
65 | SNR | SNR 1 | LIMBADI ( T) | Sh Mukeshbhai Mohanbhai Nakiya App. LM at vill Limbdi | 27-03-08 |  | 1 |  |  |  | Climbed up on wrong feeder pole. |  | Explanation from ALM Sh M D Chauhan is asked.
66 | SNR | DHG | Charadwa | Sh Mansukhbhai Bhavabhai At vill Chupani | 31-03-08 |  |  | 1 |  |  | Came in direct contact of 11 KV line when he climbed on Tree. | NA | NA
Total | [5 empty] | 10 | 80 | 179 | 101 | 409
[6 empty] | 10 | 81 | 181 | 101 | 409

## 11
SoP 011 - A : System Average Interrruption Frequency Index (SAIFI), System Average Interrruption Duration Index (SAIDI), Momentary Average Interruption Frequency Index (MAIFI)
Qtr. | Month | Category of feeder | SAIFI | SAIDI | MAIFI
4 | JAN-23 | total
ag dom
ind
urban
jgy
| FEB-23 | total
agom
ind
urban
jgy
| MAR-23 | total
agom
ind
urban
jgy
Quarter Total | JAN -23 to MAR-23 | total
agom
ind
urban
jgy
Qtr. | Month | Category of feeder | SAIFI | SAIDI | MAIFI
3 | OCT-22 | total
ag dom
ind
urban
jgy
| NOV-22 | total
agom
ind
urban
jgy
| DEC-22 | total
agom
ind
urban
jgy
Quarter Total | OCT -22 to DEC-22 | total
agom
ind
urban
jgy
2 | JUL-22 | total | 11.754 | 0.86801 | 10.6759
|  | ag dom | 22.1813 | 1900-01-01 11:49 | 18.7144
|  | ind | 3.3687 | 0.17599 | 1.6696
|  | urban | 5.7749 | 0.23037 | 5.0394
|  | jgy | 12.5627 | 0.61437 | 12.6455
| AUG-22 | total | 9.2831 | 0.60147 | 9.1588
|  | agom | 18.9758 | 1899-12-31 18:09 | 16.8936
|  | ind | 2.3213 | 0.10564 | 1.1683
|  | urban | 4.4007 | 0.16173 | 3.9312
|  | jgy | 9.204 | 0.40642 | 10.8016
| SEP-22 | total | 9.7154 | 0.61058 | 9.176
|  | agom | 20.4242 | 1899-12-31 18:16 | 16.1385
|  | ind | 2.8091 | 0.15701 | 1.3341
|  | urban | 4.9282 | 0.19284 | 4.4651
|  | jgy | 8.8781 | 0.39099 | 10.7051
Quarter Total | JUL -22 to SEP-22 | Total | 10.2894 | 0.6962 | 9.7156
|  | AG Dom | 20.5267 | 1900-01-01 00:05 | 17.2482
|  | Others | 2.5648 | 0.13128 | 1.2511
|  | Urban | 5.0338 | 0.19494 | 4.478
|  | JGY | 10.2141 | 0.47054 | 11.3836
1 | APR-22 | total | 5.9213 | 0.37077 | 7.0357
|  | ag dom | 11.8964 | 0.94636 | 12.8314
|  | ind | 1.8887 | 0.10128 | 1.1746
|  | urban | 2.9524 | 0.13748 | 3.519
|  | jgy | 5.7941 | 0.29004 | 7.7647
| MAY-22 | total | 7.3423 | 0.63538 | 7.8138
|  | agom | 14.6399 | 1899-12-31 13:33 | 14.6693
|  | ind | 2.0852 | 0.11563 | 1.2374
|  | urban | 3.7844 | 0.26619 | 3.3584
|  | jgy | 7.1291 | 0.50129 | 9.0154
| JUN-22 | total | 10.4589 | 0.793 | 9.8761
|  | agom | 20.9525 | 1900-01-01 06:05 | 17.6256
|  | ind | 3.2192 | 0.19195 | 1.3435
|  | urban | 5.3469 | 0.24988 | 4.5925
|  | jgy | 10.1229 | 0.526 | 11.577
Quarter Total | APR -22 to JUN-22 | Total | 7.908 | 0.59975 | 8.2421
|  | AG Dom | 15.8309 | 1899-12-31 14:07 | 15.0427
|  | Others | 2.3982 | 0.13633 | 1.2519
|  | Urban | 4.0281 | 0.21786 | 3.8234
|  | JGY | 7.6823 | 0.43913 | 9.4526

## 012
Performa SoP 012 - System Losses at EHT / 11 KV and Below
1 HALF UPTO APR-22 TO SEP -22
Losses in 11 KV System and Connected Equipment
i | Energy Delivered into EHT / 11 KV and LT Distribution System from EHT/11 KV SSs (MUs) | A (SENT) | 20026.2127
ii | Energy Sold (Billed). EHT direct sales (MUs) | B (EHT SOLD) | 2535.5124
iii | Energy Sold (Billed) in the 11 KV LT system (MUs) | C (TOTAL EXCL. EHT) | 14387.0173
iv | Total Sales (MUs) | (B+C) | 16922.5297
v | Losses (MUs) | {(A) - (B+C)} | 3103.683
vi | % Losses | {(A) - (B+C)} X 100 / (A) | 15.4981
2 HALF UPTO OCT-22 TO MAR-23
Performa SoP 012 - System Losses at EHT / 11 KV and Below
Losses in 11 KV System and Connected Equipment
i | Energy Delivered into EHT / 11 KV and LT Distribution System from EHT/11 KV SSs (MUs) | A (SENT)
ii | Energy Sold (Billed). EHT direct sales (MUs) | B (EHT SOLD)
iii | Energy Sold (Billed) in the 11 KV LT system (MUs) | C (TOTAL EXCL. EHT)
iv | Total Sales (MUs) | (B+C) | 0
v | Losses (MUs) | {(A) - (B+C)} | 0
vi | % Losses | {(A) - (B+C)} X 100 / (A) | #DIV/0!

## 13
Performa SoP 013: Meter faults
Name of Area/Circle | Consumer Category | No. of faulty meters at the start of the quarter / year | No. of faulty meters added during the quarter / year | Total no. of defective / faulty Meter | No. of faulty Meters repaired and replaced | No of faulty meters pending at the end of the quarter
cr | 33 | [1] | [2] | (3)=(2)+(1) | [4] | (5)=(3)-(4)
RJC | HT | 0 | 0 | 0 | 0 | 0
| Single Phase | 1834 | 1263 | 3097 | 1485 | 1612
| Three Phase | 192 | 529 | 721 | 377 | 344
RJR | HT | 0 | 0 | 0 | 0 | 0
| Single Phase | 1466 | 1893 | 3359 | 1228 | 2131
| Three Phase | 2440 | 1507 | 3947 | 855 | 3092
MRB | HT | 0 | 0 | 0 | 0 | 0
| Single Phase | 1010 | 970 | 1980 | 895 | 1085
| Three Phase | 1355 | 696 | 2051 | 977 | 1074
PBR | HT | 0 | 0 | 0 | 0 | 0
| Single Phase | 2955 | 1244 | 4199 | 707 | 3492
| Three Phase | 1899 | 839 | 2738 | 1247 | 1491
JMN | HT | 0 | 0 | 0 | 0 | 0
| Single Phase | 4773 | 2432 | 7205 | 931 | 6274
| Three Phase | 4695 | 669 | 5364 | 296 | 5068
BHJ | HT | 0 | 0 | 0 | 0 | 0
| Single Phase | 1642 | 1565 | 3207 | 729 | 2478
| Three Phase | 805 | 404 | 1209 | 574 | 635
ANJ | HT | 0 | 0 | 0 | 0 | 0
| Single Phase | 439 | 1299 | 1738 | 730 | 1008
| Three Phase | 182 | 186 | 368 | 106 | 262
JND | HT | 0 | 0 | 0 | 0 | 0
| Single Phase | 2403 | 1972 | 4375 | 1290 | 3085
| Three Phase | 2427 | 593 | 3020 | 855 | 2165
BVN | HT | 0 | 0 | 0 | 0 | 0
| Single Phase | 4326 | 2710 | 7036 | 1037 | 5999
| Three Phase | 4748 | 649 | 5397 | 482 | 4915
BTD | HT | 0 | 0 | 0 | 0 | 0
| Single Phase | 680 | 1615 | 2295 | 1904 | 391
| Three Phase | 654 | 933 | 1587 | 1135 | 452
AMR | HT | 0 | 0 | 0 | 0 | 0
| Single Phase | 5445 | 2828 | 8273 | 1644 | 6629
| Three Phase | 6904 | 114 | 7018 | 611 | 6407
SNR | HT | 0 | 0 | 0 | 0 | 0
| Single Phase | 2215 | 910 | 3125 | 359 | 2766
| Three Phase | 1711 | 353 | 2064 | 122 | 1942
PGVCL | HT | 0 | 0 | 0 | 0 | 0
| Single Phase | 29188 | 20701 | 49889 | 12939 | 36950
| Three Phase | 28012 | 7472 | 35484 | 7637 | 27847

## 014
Performa SoP 014: Statement Showing the ATC losses, collection
Efficiency and Billing Efficiency | [7 empty] | YEAR | 2022-23
Name of Circle | Quarter | Months | Units input (Mus) | Units Billed (Mus) | Billing Efficiency | Revenue Billed (Rs. Lacs) | Revenue Collected (Rs. Lacs) | Collection Efficiency % | Business Efficiency | ATC Loss%
|  |  | A | B | C = (B/A)*100 | D | E | F = (E/D)*100 | G = (C*F)/100 | H = 100 - G
PGVCL | I | APR | 3754.9735 | 2957.1844 | 78.7538 | 180536.5996 | 160562.191 | 88.9361 | 70.0406 | 29.9594
|  | MAY | 3750.6394 | 2987.8204 | 79.6616 | 187055.0506 | 175922.5187 | 94.0485 | 74.9206 | 25.0794
|  | JUN | 3614.9378 | 2954.7667 | 81.7377 | 199010.5303 | 192842.859 | 96.9008 | 79.2045 | 20.7955
|  |  | 11120.5507 | 8899.7715 | 80.03 | 566602.1805 | 529327.5687 | 93.4214 | 74.7651 | 25.2349
| II | JUL | 2785.5783 | 2756.0579 | 98.9402 | 202103.925 | 188037.7356 | 93.0401 | 92.0541 | 7.9459
|  | AUG | 2714.3492 | 2656.1586 | 97.8562 | 195783.6937 | 180442.104 | 92.164 | 90.1882 | 9.8118
|  | SEP | 3405.7345 | 2610.5417 | 76.6514 | 186965.0264 | 184674.5664 | 98.7749 | 75.7123 | 24.2877
|  |  | 8905.662 | 8022.7582 | 90.086 | 584852.6451 | 553154.4061 | 94.5801 | 85.2035 | 14.7965
| III | OCT |  |  | #DIV/0! |  |  | #DIV/0! | #DIV/0! | #DIV/0!
|  | NOV |  |  | #DIV/0! |  |  | #DIV/0! | #DIV/0! | #DIV/0!
|  | DEC |  |  | #DIV/0! |  |  | #DIV/0! | #DIV/0! | #DIV/0!
|  |  | 0 | 0 | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0!
| IV | JAN |  |  | #DIV/0! |  |  | #DIV/0! | #DIV/0! | #DIV/0!
|  | FEB |  |  | #DIV/0! |  |  | #DIV/0! | #DIV/0! | #DIV/0!
|  | MAR |  |  | #DIV/0! |  |  | #DIV/0! | #DIV/0! | #DIV/0!
|  |  | 0 | 0 | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0!
| TOTAL UPTO THE QUARTER |  | 20026.2127 | 16922.5297 | 84.5019 | 1151454.8256 | 1082481.9748 | 94.0099 | 79.4402 | 20.5598

## 015
Performa SoP 015: Release of New Connection status
Name of Area/Circle | Consumer category |  | Total no. of consumers connected at the beginning of half-year/year | Pending at the Beginning of the of the Half year/year | New Applications received during the half-year / year | No. of connections released during the half-year / year | No. of applications pending at the end of half-year / year | Total no. of consumers connected at the end of half-year/year
1st Half | RGP |  | 3818117 | 10128 | 51777 | 53355 | 8619 | 3875684 |  | 1907938 | 1967746
| GLP |  | 31813 | 91 | 342 | 359 | 62 | 32055
| N-RGP & LTMD |  | 723646 | 3472 | 18604 | 17389 | 2841 | 738289 |  | 613049 | 97550 | 3120 | 24570
| Public Water Works |  | 18275 | 58 | 280 | 233 | 107 | 18467 |  | 385 | 2829 | 13608 | 1645
| Agriculture (Total) | unmetered | 255237 | 0 |  | -113 |  | 255124 | 113
|  | metered | 827799 | 31967 | 16491 | 12196 | 15781 | 836411 |  | 826589 | 4454 | 39 | 5329
| public lighting |  | 8549 | 4 | 3 | 9 | 1 | 8682 |  | 7802 | 880
| Industrial HT |  | 6927 | 292 | 294 | 267 | 273 | 7205
Railway
| Total |  | 5690363 | 46012 | 87791 | 83695 | 27684 | 5771917
2nd Half | RGP
GLP
N-RGP & LTMD
Public Water Works
| Agriculture (Total) | unmetered
metered
public lighting
Industrial HT
Railway
Total
Annual | RGP |  | 3818117 | 10128 | 51777 | 53355 | 8619 | 3875684
| GLP |  | 31813 | 91 | 342 | 359 | 62 | 32055
| N-RGP & LTMD |  | 723646 | 3472 | 18604 | 17389 | 2841 | 738289
| Public Water Works |  | 18275 | 58 | 280 | 233 | 107 | 18467
| Agriculture (Total) | unmetered | 255237 | 0 | 0 | -113 | 0 | 255124
|  | metered | 827799 | 31967 | 16491 | 12196 | 15781 | 836411
| public lighting |  | 8549 | 4 | 3 | 9 | 1 | 8682
| Industrial HT |  | 6927 | 292 | 294 | 267 | 273 | 7205
| Railway |  | 0 | 0 | 0 | 0 | 0 | 0
| Total |  | 5690363 | 46012 | 87791 | 83695 | 27684 | 5771917

## 016
Performa SoP 016: Release of New Connection status
COMPENSATION DETAILS
Circle | Sr. No | Event | Compensation | No of cases where compensation was given (in numbers) | Amt of compensation paid (in Rs.)
RJC | 1 | Duty to provide supply | NIL | 0 | 0
|  | a) New Connection |  | 0 | 0
|  | b) Additional Load |  | 0 | 0
|  | c) Temporary supply |  | 0 | 0
|  | d) Shifting service connection |  | 0 | 0
|  | e)Transfer of service connection |  | 0 | 0
|  | f) Change in tariff category of consumer |  | 0 | 0
| 2 | Complaints in billing | NIL | 0 | 0
| 3 | Replacement of meters | NIL | 0 | 0
| 4 | Interruption of supply | NIL | 0 | 0
| 5 | Voltage fluctuations and complaints | NIL | 0 | 0
| 6 | Responding to consumer's complaints | NIL | 0 | 0
| 7 | Grievance Handling | NIL | 0 | 0
| TOTAL |  |  | 0 | 0
|  |  |  | 0 | 0
RJR | 1 | Duty to provide supply | NIL | NIL | NIL
|  | a) New Connection |  | NIL | NIL
|  | b) Additional Load |  | NIL | NIL
|  | c) Temporary supply |  | NIL | NIL
|  | d) Shifting service connection |  | NIL | NIL
|  | e)Transfer of service connection |  | NIL | NIL
|  | f) Change in tariff category of consumer |  | NIL | NIL
| 2 | Complaints in billing | NIL | NIL | NIL
| 3 | Replacement of meters | NIL | NIL | NIL
| 4 | Interruption of supply | NIL | NIL | NIL
| 5 | Voltage fluctuations and complaints | NIL | NIL | NIL
| 6 | Responding to consumer's complaints | NIL | NIL | NIL
| 7 | Grievance Handling | NIL | NIL | NIL
TOTAL
MRB | 1 | Duty to provide supply | NIL | NIL | NIL
|  | a) New Connection |  | NIL | NIL
|  | b) Additional Load |  | NIL | NIL
|  | c) Temporary supply |  | NIL | NIL
|  | d) Shifting service connection |  | NIL | NIL
|  | e)Transfer of service connection |  | NIL | NIL
|  | f) Change in tariff category of consumer |  | NIL | NIL
| 2 | Complaints in billing | NIL | NIL | NIL
| 3 | Replacement of meters | NIL | NIL | NIL
| 4 | Interruption of supply | NIL | NIL | NIL
| 5 | Voltage fluctuations and complaints | NIL | NIL | NIL
| 6 | Responding to consumer's complaints | NIL | NIL | NIL
| 7 | Grievance Handling | NIL | NIL | NIL
TOTAL
PBR | 1 | Duty to provide supply | Nill | 0 | 0
|  | a) New Connection |  | 0 | 0
|  | b) Additional Load |  | 0 | 0
|  | c) Temporary supply |  | 0 | 0
|  | d) Shifting service connection |  | 0 | 0
|  | e)Transfer of service connection |  | 0 | 0
|  | f) Change in tariff category of consumer |  | 0 | 0
| 2 | Complaints in billing | 0 | 0 | 0
| 3 | Replacement of meters | 0 | 0 | 0
| 4 | Interruption of supply | 0 | 0 | 0
| 5 | Voltage fluctuations and complaints | 0 | 0 | 0
| 6 | Responding to consumer's complaints | 0 | 0 | 0
| 7 | Grievance Handling | 0 | 0 | 0
TOTAL
JMN | 1 | Duty to provide supply | NIL
a) New Connection
b) Additional Load
c) Temporary supply
d) Shifting service connection
e)Transfer of service connection
f) Change in tariff category of consumer
| 2 | Complaints in billing
| 3 | Replacement of meters
| 4 | Interruption of supply
| 5 | Voltage fluctuations and complaints
| 6 | Responding to consumer's complaints
| 7 | Grievance Handling
TOTAL
BHJ | 1 | Duty to provide supply | NIL
a) New Connection
b) Additional Load
c) Temporary supply
d) Shifting service connection
e)Transfer of service connection
f) Change in tariff category of consumer
| 2 | Complaints in billing
| 3 | Replacement of meters
| 4 | Interruption of supply
| 5 | Voltage fluctuations and complaints
| 6 | Responding to consumer's complaints
| 7 | Grievance Handling
TOTAL
ANJ | 1 | Duty to provide supply | NIL | NIL | NIL
|  | a) New Connection |  | NIL | NIL
|  | b) Additional Load |  | NIL | NIL
|  | c) Temporary supply |  | NIL | NIL
|  | d) Shifting service connection |  | NIL | NIL
|  | e)Transfer of service connection |  | NIL | NIL
|  | f) Change in tariff category of consumer |  | NIL | NIL
| 2 | Complaints in billing | NIL | NIL | NIL
| 3 | Replacement of meters | NIL | NIL | NIL
| 4 | Interruption of supply | NIL | NIL | NIL
| 5 | Voltage fluctuations and complaints | NIL | NIL | NIL
| 6 | Responding to consumer's complaints | NIL | NIL | NIL
| 7 | Grievance Handling | NIL | NIL | NIL
TOTAL
JND | 1 | Duty to provide supply | Nill | 0 | 0
|  | a) New Connection |  | 0 | 0
|  | b) Additional Load |  | 0 | 0
|  | c) Temporary supply |  | 0 | 0
|  | d) Shifting service connection |  | 0 | 0
|  | e)Transfer of service connection |  | 0 | 0
|  | f) Change in tariff category of consumer |  | 0 | 0
| 2 | Complaints in billing | 0 | 0 | 0
| 3 | Replacement of meters | 0 | 0 | 0
| 4 | Interruption of supply | 0 | 0 | 0
| 5 | Voltage fluctuations and complaints | 0 | 0 | 0
| 6 | Responding to consumer's complaints | 0 | 0 | 0
| 7 | Grievance Handling | 0 | 0 | 0
TOTAL
BVN | 1 | Duty to provide supply | NIL
a) New Connection
b) Additional Load
c) Temporary supply
d) Shifting service connection
e)Transfer of service connection
f) Change in tariff category of consumer
| 2 | Complaints in billing | NIL
| 3 | Replacement of meters | NIL
| 4 | Interruption of supply | NIL
| 5 | Voltage fluctuations and complaints | NIL
| 6 | Responding to consumer's complaints | NIL
| 7 | Grievance Handling | NIL
TOTAL
BTD | 1 | Duty to provide supply | NILL
a) New Connection
b) Additional Load
c) Temporary supply
d) Shifting service connection
e)Transfer of service connection
f) Change in tariff category of consumer
| 2 | Complaints in billing | NILL
| 3 | Replacement of meters | NILL
| 4 | Interruption of supply | NILL
| 5 | Voltage fluctuations and complaints | NILL
| 6 | Responding to consumer's complaints | NILL
| 7 | Grievance Handling | NILL
TOTAL
AMR | 1 | Duty to provide supply | NIL | NIL | NIL
|  | a) New Connection |  | NIL | NIL
|  | b) Additional Load |  | NIL | NIL
|  | c) Temporary supply |  | NIL | NIL
|  | d) Shifting service connection |  | NIL | NIL
|  | e)Transfer of service connection |  | NIL | NIL
|  | f) Change in tariff category of consumer |  | NIL | NIL
| 2 | Complaints in billing | NIL | NIL | NIL
| 3 | Replacement of meters | NIL | NIL | NIL
| 4 | Interruption of supply | NIL | NIL | NIL
| 5 | Voltage fluctuations and complaints | NIL | NIL | NIL
| 6 | Responding to consumer's complaints | NIL | NIL | NIL
| 7 | Grievance Handling | NIL | NIL | NIL
TOTAL
SNR | 1 | Duty to provide supply | NIL | 0 | 0
|  | a) New Connection |  | 0 | 0
|  | b) Additional Load |  | 0 | 0
|  | c) Temporary supply |  | 0 | 0
|  | d) Shifting service connection |  | 0 | 0
|  | e)Transfer of service connection |  | 0 | 0
|  | f) Change in tariff category of consumer |  | 0 | 0
| 2 | Complaints in billing | NIL | 0 | 0
| 3 | Replacement of meters | NIL | 0 | 0
| 4 | Interruption of supply | NIL | 0 | 0
| 5 | Voltage fluctuations and complaints | NIL | 0 | 0
| 6 | Responding to consumer's complaints | NIL | 0 | 0
| 7 | Grievance Handling | NIL | 0 | 0
TOTAL

## sop011-(AG)
SoP 011 - A : System Average Interrruption Frequency Index (SAIFI) for AG. Dominant Category
Sr. No | Month | Ni - Number of Customers for each sustained interruptions (in numbers) | NT - Total No of customers served (in Numbers) | CI=∑ Ni | SAIFI = ∑ Ni/Nt (Monthly SAIFI)
1 | 2 | 3 | 4 | 5 | 6=5/4
1 | 2022-04-01 | 1237578 | 1275987 | 15179674 | 11.8964
2 | 2022-05-01 | 1241518 | 1274625 | 18660341 | 14.6399
3 | 2022-06-01 | 1265009 | 1276621 | 26748439 | 20.9525
| 1st Qtr | 3744105 | 1276621 | 60588454 | 47.46
4 | 2022-07-01 | 1263493 | 1275657 | 28295783 | 22.1813
5 | 2022-08-01 | 1262805 | 1276719 | 24226803 | 18.9758
6 | 2022-09-01 | 1259388 | 1277448 | 26090888 | 20.4242
| 2nd Qtr | 3785686 | 1277448 | 78613474 | 61.5395
7 | 2022-10-01 | 0 | 0 | 0 | #DIV/0!
8 | 2022-11-01 | 0 | 0 | 0 | #DIV/0!
9 | 2022-12-01 | 0 | 0 | 0 | #DIV/0!
| 3rd Qtr | 0 | 0 | 0 | #DIV/0!
10 | 2023-01-01 | 0 | 0 | 0 | #DIV/0!
11 | 2023-02-01 | 0 | 0 | 0 | #DIV/0!
12 | 2023-03-01 | 0 | 0 | 0 | #DIV/0!
| 4th Qtr | 0 | 0 | 0 | #DIV/0!
| Yearly Data | 7529791 | 1277448 | 139201928 | 108.9688
SoP 011 - B : System Average Interrruption Duration Index (SAIDI) for AG. Dominant Category
Sr. No | Month | Ri = Restoration Time for each sustained interruption event (in hours) | Ni - Number of interrupted Customers for each sustained interruption event (in numbers) | Ri* Ni - Total customer interrution Duration | NT - Total No of customers served (in Numbers) | Customer Intt. Duration CMI = ΣRi*Ni | SAIDI = ΣRi*Ni/Nt (Monthly SAIDI)
1 | 2 | 3 | 4 | 5 = 3 * 4 | 6 | 7 | 8=7/6
1 | 2022-04-01 | 0.086315 | 1237578 | 2192-06-17 22:52 | 1275987 | 1207544.1271 | 0.94636
2 | 2022-05-01 | 0.11981 | 1241518 | 2307-04-06 17:12 | 1274625 | 1994285.7358 | 1899-12-31 13:33
3 | 2022-06-01 | 0.1226 | 1265009 | 2324-08-09 21:28 | 1276621 | 2877268.2146 | 1900-01-01 06:05
| 1st Qtr | 0.32873 | 3744105 | 1230783.0973 | 1276621 | 6079098.0775 | 1900-01-03 18:17
4 | 2022-07-01 | 0.13433 | 1263493 | 2364-09-08 07:12 | 1275657 | 3179776.8467 | 1900-01-01 11:49
5 | 2022-08-01 | 0.10986 | 1262805 | 2279-11-04 17:01 | 1276719 | 2242352.8612 | 1899-12-31 18:09
6 | 2022-09-01 | 0.098735 | 1259388 | 2240-06-10 17:34 | 1277448 | 2249909.3596 | 1899-12-31 18:16
| 2nd Qtr | 0.34293 | 3785686 | 1298222.2467 | 1277448 | 7672039.0675 | 1900-01-05 00:08
7 | 2022-10-01 | 0 | 0 | #DIV/0! | 0 | 0 | #DIV/0!
8 | 2022-11-01 | 0 | 0 | #DIV/0! | 0 | 0 | #DIV/0!
9 | 2022-12-01 | 0 | 0 | #DIV/0! | 0 | 0 | #DIV/0!
| 3rd Qtr | 0 | 0 | 0 | 0 | 0 | #DIV/0!
10 | 2023-01-01 | 0 | 0 | #DIV/0! | 0 | 0 | #DIV/0!
11 | 2023-02-01 | 0 | 0 | #DIV/0! | 0 | 0 | #DIV/0!
12 | 2023-03-01 | 0 | 0 | #DIV/0! | 0 | 0 | #DIV/0!
| 4th Qtr | 0 | 0 | 0 | 0 | 0 | #DIV/0!
| Yearly Data | 0.67165 | 7529791 | 5057420.0877 | 1277448 | 13751137.145 | 1900-01-09 18:21
SoP 011 - C : Momentary Average Interruption Frequency Index (MAIFI) for AG. Dominant Category
Sr. No | Month | IMi = Number of Momentary interruptions for the month (in numbers) | Nmi = Total no of customers for each momentary interruptions (in numbers) | Imi =Nmi Number of customer Momentary interruptions (in numbers) | Nt - Total no of customers served (in numbers) | Customer Intt. ΣImi*Nmi | MAIFI=ΣImi*Nmi/Nt
1 | 2 | 3 | 4 | 5 = 3 * 4 | 6 | 7 | 8=7/6
1 | 2022-04-01 | 46198 | 1205397 | 55686930606 | 1275987 | 16372706 | 12.8314
2 | 2022-05-01 | 53404 | 1194826 | 63808487704 | 1274625 | 18697877 | 14.6693
3 | 2022-06-01 | 65334 | 1216490 | 79478157660 | 1276621 | 22501218 | 17.6256
| 1st Qtr | 164936 | 3616713 | 596526175368 | 1276621 | 57571801 | 45.097
4 | 2022-07-01 | 69786 | 1218488 | 85033403568 | 1275657 | 23873137 | 18.7144
5 | 2022-08-01 | 62353 | 1197593 | 74673516329 | 1276719 | 21568369 | 16.8936
6 | 2022-09-01 | 59390 | 1205975 | 71622855250 | 1277448 | 20616042 | 16.1385
| 2nd Qtr | 191529 | 3622056 | 693728763624 | 1277448 | 66057548 | 51.7106
7 | 2022-10-01 | 0 | 0 | 0 | 0 | 0 | #DIV/0!
8 | 2022-11-01 | 0 | 0 | 0 | 0 | 0 | #DIV/0!
9 | 2022-12-01 | 0 | 0 | 0 | 0 | 0 | #DIV/0!
| 3rd Qtr | 0 | 0 | 0 | 0 | 0 | #DIV/0!
10 | 2023-01-01 | 0 | 0 | 0 | 0 | 0 | #DIV/0!
11 | 2023-02-01 | 0 | 0 | 0 | 0 | 0 | #DIV/0!
12 | 2023-03-01 | 0 | 0 | 0 | 0 | 0 | #DIV/0!
| 4th Qtr | 0 | 0 | 0 | 0 | 0 | #DIV/0!
| Yearly Data | 356465 | 7238769 | 2580367791585 | 1277448 | 123629349 | 96.7784

## SOP011-(JGY)
SoP 011 - A : System Average Interrruption Frequency Index (SAIFI) for JGY category
Sr. No | Month | Ni - Number of Customers for each sustained interruptions (in numbers) | NT - Total No of customers served (in Numbers) | CI=∑ Ni | SAIFI = ∑ Ni/Nt (Monthly SAIFI)
1 | 2 | 3 | 4 | 5 | 6=5/4
1 | 2022-04-01 | 1797370 | 1979675 | 11470362 | 5.7941
2 | 2022-05-01 | 1821790 | 1980681 | 14120526 | 7.1291
3 | 2022-06-01 | 1927622 | 1980544 | 20048918 | 10.1229
| 1st Qtr | 5546782 | 1980544 | 45639806 | 23.0441
4 | 2022-07-01 | 1925822 | 1982572 | 24906420 | 12.5627
5 | 2022-08-01 | 1877341 | 1984132 | 18261939 | 9.204
6 | 2022-09-01 | 1862758 | 1985114 | 17623986 | 8.8781
| 2nd Qtr | 5665921 | 1985114 | 60792345 | 30.6241
7 | 2022-10-01 | 0 | 0 | 0 | #DIV/0!
8 | 2022-11-01 | 0 | 0 | 0 | #DIV/0!
9 | 2022-12-01 | 0 | 0 | 0 | #DIV/0!
| 3rd Qtr | 0 | 0 | 0 | #DIV/0!
1 | 2023-01-01 | 0 | 0 | 0 | #DIV/0!
2 | 2023-02-01 | 0 | 0 | 0 | #DIV/0!
3 | 2023-03-01 | 0 | 0 | 0 | #DIV/0!
| 4th Qtr | 0 | 0 | 0 | #DIV/0!
| Yearly Data | 11212703 | 1985114 | 106432151 | 53.6151
SoP 011 - B : System Average Interrruption Duration Index (SAIDI) for JGY category
Sr. No | Month | Ri = Restoration Time for each sustained interruption event (in hours) | Ni - Number of interrupted Customers for each sustained interruption event (in numbers) | Ri* Ni - Total customer interrution Duration | NT - Total No of customers served (in Numbers) | Customer Intt. Duration CMI = ΣRi*Ni | SAIDI = ΣRi*Ni/Nt (Monthly SAIDI)
1 | 2 | 3 | 4 | 5 = 3 * 4 | 6 | 7 | 8=7/6
1 | 2022-04-01 | 0.049586 | 1797370 | 2144-01-03 12:05 | 1979675 | 574178.7567 | 0.29004
2 | 2022-05-01 | 0.067057 | 1821790 | 2234-06-20 21:50 | 1980681 | 992886.3054 | 0.50129
3 | 2022-06-01 | 0.052524 | 1927622 | 2177-03-13 22:56 | 1980544 | 1041757.5583 | 0.526
| 1st Qtr | 0.16917 | 5546782 | 938331.706 | 1980544 | 2608822.6204 | 1899-12-31 07:37
4 | 2022-07-01 | 0.049042 | 1925822 | 2158-07-31 07:09 | 1982572 | 1218030.9992 | 0.61437
5 | 2022-08-01 | 0.044439 | 1877341 | 2128-05-29 09:16 | 1984132 | 806390.3154 | 0.40642
6 | 2022-09-01 | 0.045446 | 1862758 | 2131-10-09 10:50 | 1985114 | 776160.5392 | 0.39099
| 2nd Qtr | 0.13893 | 5665921 | 787146.1145 | 1985114 | 2800581.8537 | 1899-12-31 09:52
7 | 2022-10-01 | 0 | 0 | #DIV/0! | 0 | 0 | #DIV/0!
8 | 2022-11-01 | 0 | 0 | #DIV/0! | 0 | 0 | #DIV/0!
9 | 2022-12-01 | 0 | 0 | #DIV/0! | 0 | 0 | #DIV/0!
| 3rd Qtr | 0 | 0 | 0 | 0 | 0 | #DIV/0!
1 | 2023-01-01 | 0 | 0 | #DIV/0! | 0 | 0 | #DIV/0!
2 | 2023-02-01 | 0 | 0 | #DIV/0! | 0 | 0 | #DIV/0!
3 | 2023-03-01 | 0 | 0 | #DIV/0! | 0 | 0 | #DIV/0!
| 4th Qtr | 0 | 0 | 0 | 0 | 0 | #DIV/0!
| Yearly Data | 0.30809 | 11212703 | 3454558.4571 | 1985114 | 5409404.4742 | 1900-01-01 17:24
SoP 011 - C : Momentary Average Interruption Frequency Index (MAIFI) for JGY category
Sr. No | Month | IMi = Number of Momentary interruptions for the month (in numbers) | Nmi = Total no of customers for each momentary interruptions (in numbers) | Imi =Nmi Number of customer Momentary interruptions (in numbers) | Nt - Total no of customers served (in numbers) | Customer Intt. ΣImi*Nmi | MAIFI=ΣImi*Nmi/Nt
1 | 2 | 3 | 4 | 5 = 3 * 4 | 6 | 7 | 8=7/6
1 | 2022-04-01 | 10535 | 1806720 | 19033795200 | 1979675 | 15371622 | 7.7647
2 | 2022-05-01 | 12366 | 1829004 | 22617463464 | 1980681 | 17856542 | 9.0154
3 | 2022-06-01 | 16211 | 1880023 | 30477052853 | 1980544 | 22928718 | 11.577
| 1st Qtr | 39112 | 5515747 | 215731896664 | 1980544 | 56156882 | 28.3543
4 | 2022-07-01 | 17741 | 1891159 | 33551051819 | 1982572 | 25070651 | 12.6455
5 | 2022-08-01 | 15404 | 1847850 | 28464281400 | 1984132 | 21431720 | 10.8016
6 | 2022-09-01 | 14824 | 1865740 | 27657729760 | 1985114 | 21250780 | 10.7051
| 2nd Qtr | 47969 | 5604749 | 268854204781 | 1985114 | 67753151 | 34.1306
7 | 2022-10-01 | 0 | 0 | 0 | 0 | 0 | #DIV/0!
8 | 2022-11-01 | 0 | 0 | 0 | 0 | 0 | #DIV/0!
9 | 2022-12-01 | 0 | 0 | 0 | 0 | 0 | #DIV/0!
| 3rd Qtr | 0 | 0 | 0 | 0 | 0 | #DIV/0!
1 | 2023-01-01 | 0 | 0 | 0 | 0 | 0 | #DIV/0!
2 | 2023-02-01 | 0 | 0 | 0 | 0 | 0 | #DIV/0!
3 | 2023-03-01 | 0 | 0 | 0 | 0 | 0 | #DIV/0!
| 4th Qtr | 0 | 0 | 0 | 0 | 0 | #DIV/0!
| Yearly Data | 87081 | 11120496 | 968383912176 | 1985114 | 123910033 | 62.4196

## SOP011-(URBAN)
SoP 011 - A : System Average Interrruption Frequency Index (SAIFI) for URBAN category
Sr. No | Month | Ni - Number of Customers for each sustained interruptions (in numbers) | NT - Total No of customers served (in Numbers) | CI=∑ Ni | SAIFI = ∑ Ni/Nt (Monthly SAIFI)
1 | 2 | 3 | 4 | 5 | 6=5/4
1 | 2022-04-01 | 1783809 | 2349763 | 6937356 | 2.9524
2 | 2022-05-01 | 1981923 | 2350395 | 8894776 | 3.7844
3 | 2022-06-01 | 2010574 | 2351111 | 12571253 | 5.3469
| 1st Qtr | 5776306 | 2351111 | 28403385 | 12.0808
4 | 2022-07-01 | 1979244 | 2354732 | 13598344 | 5.7749
5 | 2022-08-01 | 1809141 | 2361386 | 10391681 | 4.4007
6 | 2022-09-01 | 1952170 | 2368227 | 11671167 | 4.9282
| 2nd Qtr | 5740555 | 2368227 | 35661192 | 15.0582
7 | 2022-10-01 | 0 | 0 | 0 | #DIV/0!
8 | 2022-11-01 | 0 | 0 | 0 | #DIV/0!
9 | 2022-12-01 | 0 | 0 | 0 | #DIV/0!
| 3rd Qtr | 0 | 0 | 0 | #DIV/0!
1 | 2023-01-01 | 0 | 0 | 0 | #DIV/0!
2 | 2023-02-01 | 0 | 0 | 0 | #DIV/0!
3 | 2023-03-01 | 0 | 0 | 0 | #DIV/0!
| 4th Qtr | 0 | 0 | 0 | #DIV/0!
| Yearly Data | 11516861 | 2368227 | 64064577 | 27.0517
SoP 011 - B : System Average Interrruption Duration Index (SAIDI) for URBAN category
Sr. No | Month | Ri = Restoration Time for each sustained interruption event (in hours) | Ni - Number of interrupted Customers for each sustained interruption event (in numbers) | Ri* Ni - Total customer interrution Duration | NT - Total No of customers served (in Numbers) | Customer Intt. Duration CMI = ΣRi*Ni | SAIDI = ΣRi*Ni/Nt (Monthly SAIDI)
1 | 2 | 3 | 4 | 5 = 3 * 4 | 6 | 7 | 8=7/6
1 | 2022-04-01 | 0.04976 | 1783809 | 2143-01-07 03:50 | 2349763 | 323034.0737 | 0.13748
2 | 2022-05-01 | 0.079168 | 1981923 | 2329-08-03 15:08 | 2350395 | 625662.4783 | 0.26619
3 | 2022-06-01 | 0.051567 | 2010574 | 2183-11-10 16:26 | 2351111 | 587501.7908 | 0.24988
| 1st Qtr | 0.1805 | 5776306 | 1042597.1624 | 2351111 | 1536198.3429 | 0.65339
4 | 2022-07-01 | 0.041358 | 1979244 | 2124-02-12 05:11 | 2354732 | 542458.9358 | 0.23037
5 | 2022-08-01 | 0.038138 | 1809141 | 2088-11-25 10:01 | 2361386 | 381896.3292 | 0.16173
6 | 2022-09-01 | 0.038944 | 1952170 | 2108-02-23 02:19 | 2368227 | 456692.785 | 0.19284
| 2nd Qtr | 0.11844 | 5740555 | 679913.8373 | 2368227 | 1381048.05 | 0.58316
7 | 2022-10-01 | 0 | 0 | #DIV/0! | 0 | 0 | #DIV/0!
8 | 2022-11-01 | 0 | 0 | #DIV/0! | 0 | 0 | #DIV/0!
9 | 2022-12-01 | 0 | 0 | #DIV/0! | 0 | 0 | #DIV/0!
| 3rd Qtr | 0 | 0 | 0 | 0 | 0 | #DIV/0!
1 | 2023-01-01 | 0 | 0 | #DIV/0! | 0 | 0 | #DIV/0!
2 | 2023-02-01 | 0 | 0 | #DIV/0! | 0 | 0 | #DIV/0!
3 | 2023-03-01 | 0 | 0 | #DIV/0! | 0 | 0 | #DIV/0!
| 4th Qtr | 0 | 0 | 0 | 0 | 0 | #DIV/0!
| Yearly Data | 0.29894 | 11516861 | 3442803.4692 | 2368227 | 2917246.3929 | 1899-12-31 05:34
SoP 011 - C : Momentary Average Interruption Frequency Index (MAIFI) for URBAN category
Sr. No | Month | IMi = Number of Momentary interruptions for the month (in numbers) | Nmi = Total no of customers for each momentary interruptions (in numbers) | Imi =Nmi Number of customer Momentary interruptions (in numbers) | Nt - Total no of customers served (in numbers) | Customer Intt. ΣImi*Nmi | MAIFI=ΣImi*Nmi/Nt
1 | 2 | 3 | 4 | 5 = 3 * 4 | 6 | 7 | 8=7/6
1 | 2022-04-01 | 2553 | 1850394 | 4724055882 | 2349763 | 8268857 | 3.519
2 | 2022-05-01 | 2636 | 1843634 | 4859819224 | 2350395 | 7893484 | 3.3584
3 | 2022-06-01 | 3456 | 1927093 | 6660033408 | 2351111 | 10797556 | 4.5925
| 1st Qtr | 8645 | 5621121 | 48594591045 | 2351111 | 26959897 | 11.4669
4 | 2022-07-01 | 3858 | 1929669 | 7444663002 | 2354732 | 11866509 | 5.0394
5 | 2022-08-01 | 3169 | 1841963 | 5837180747 | 2361386 | 9282963 | 3.9312
6 | 2022-09-01 | 3426 | 1967550 | 6740826300 | 2368227 | 10574260 | 4.4651
| 2nd Qtr | 10453 | 5739182 | 59991669446 | 2368227 | 31723732 | 13.3956
7 | 2022-10-01 | 0 | 0 | 0 | 0 | 0 | #DIV/0!
8 | 2022-11-01 | 0 | 0 | 0 | 0 | 0 | #DIV/0!
9 | 2022-12-01 | 0 | 0 | 0 | 0 | 0 | #DIV/0!
| 3rd Qtr | 0 | 0 | 0 | 0 | 0 | #DIV/0!
1 | 2023-01-01 | 0 | 0 | 0 | 0 | 0 | #DIV/0!
2 | 2023-02-01 | 0 | 0 | 0 | 0 | 0 | #DIV/0!
3 | 2023-03-01 | 0 | 0 | 0 | 0 | 0 | #DIV/0!
| 4th Qtr | 0 | 0 | 0 | 0 | 0 | #DIV/0!
| Yearly Data | 19098 | 11360303 | 216959066694 | 2368227 | 58683629 | 24.7796

## SOP011-(Other all)
SoP 011 - A : System Average Interrruption Frequency Index (SAIFI) for OTHER ALL category
Sr. No | Month | Ni - Number of Customers for each sustained interruptions (in numbers) | NT - Total No of customers served (in Numbers) | CI=∑ Ni | SAIFI = ∑ Ni/Nt (Monthly SAIFI)
1 | 2 | 3 | 4 | 5 | 6=5/4
1 | 2022-04-01 | 45957 | 98137 | 185350 | 1.8887
2 | 2022-05-01 | 45053 | 98272 | 204913 | 2.0852
3 | 2022-06-01 | 49962 | 98388 | 316730 | 3.2192
| 1st Qtr | 140972 | 98388 | 706993 | 7.1858
4 | 2022-07-01 | 47902 | 98485 | 331769 | 3.3687
5 | 2022-08-01 | 44867 | 98910 | 229596 | 2.3213
6 | 2022-09-01 | 48085 | 98568 | 276889 | 2.8091
| 2nd Qtr | 140854 | 98568 | 838254 | 8.5043
7 | 2022-10-01 | 0 | 0 | 0 | #DIV/0!
8 | 2022-11-01 | 0 | 0 | 0 | #DIV/0!
9 | 2022-12-01 | 0 | 0 | 0 | #DIV/0!
| 3rd Qtr | 0 | 0 | 0 | #DIV/0!
1 | 2023-01-01 | 0 | 0 | 0 | #DIV/0!
2 | 2023-02-01 | 0 | 0 | 0 | #DIV/0!
3 | 2023-03-01 | 0 | 0 | 0 | #DIV/0!
| 4th Qtr | 0 | 0 | 0 | #DIV/0!
| Yearly Data | 281826 | 98568 | 1545247 | 15.677
SoP 011 - B : System Average Interrruption Duration Index (SAIDI) for OTHER ALL category
Sr. No | Month | Ri = Restoration Time for each sustained interruption event (in hours) | Ni - Number of interrupted Customers for each sustained interruption event (in numbers) | Ri* Ni - Total customer interrution Duration | NT - Total No of customers served (in Numbers) | Customer Intt. Duration CMI = ΣRi*Ni | SAIDI = ΣRi*Ni/Nt (Monthly SAIDI)
1 | 2 | 3 | 4 | 5 = 3 * 4 | 6 | 7 | 8=7/6
1 | 2022-04-01 | 0.065105 | 45957 | 1908-03-10 00:25 | 98137 | 9939.6333 | 0.10128
2 | 2022-05-01 | 0.068117 | 45053 | 1908-05-25 21:03 | 98272 | 11363.3033 | 0.11563
3 | 2022-06-01 | 0.071512 | 49962 | 1909-10-11 21:02 | 98388 | 18885.3429 | 0.19195
| 1st Qtr | 0.20473 | 140972 | 1979-01-06 17:04 | 98388 | 40188.2796 | 0.40847
4 | 2022-07-01 | 0.041358 | 47902 | 1908-03-15 05:19 | 98485 | 17332.0312 | 0.17599
5 | 2022-08-01 | 0.038138 | 44867 | 1906-07-12 20:00 | 98910 | 10449.0296 | 0.10564
6 | 2022-09-01 | 0.038944 | 48085 | 1908-04-10 10:49 | 98568 | 15475.8308 | 0.15701
| 2nd Qtr | 0.11844 | 140854 | 1945-09-02 19:25 | 98568 | 43256.8917 | 0.43885
7 | 2022-10-01 | 0 | 0 | #DIV/0! | 0 | 0 | #DIV/0!
8 | 2022-11-01 | 0 | 0 | #DIV/0! | 0 | 0 | #DIV/0!
9 | 2022-12-01 | 0 | 0 | #DIV/0! | 0 | 0 | #DIV/0!
| 3rd Qtr | 0 | 0 | 0 | 0 | 0 | #DIV/0!
1 | 2023-01-01 | 0 | 0 | #DIV/0! | 0 | 0 | #DIV/0!
2 | 2023-02-01 | 0 | 0 | #DIV/0! | 0 | 0 | #DIV/0!
3 | 2023-03-01 | 0 | 0 | #DIV/0! | 0 | 0 | #DIV/0!
| 4th Qtr | 0 | 0 | 0 | 0 | 0 | #DIV/0!
| Yearly Data | 0.32317 | 281826 | 2149-05-11 20:35 | 98568 | 83445.1712 | 0.84657
SoP 011 - C : Momentary Average Interruption Frequency Index (MAIFI) for OTHER ALL category
Sr. No | Month | IMi = Number of Momentary interruptions for the month (in numbers) | Nmi = Total no of customers for each momentary interruptions (in numbers) | Imi =Nmi Number of customer Momentary interruptions (in numbers) | Nt - Total no of customers served (in numbers) | Customer Intt. ΣImi*Nmi | MAIFI=ΣImi*Nmi/Nt
1 | 2 | 3 | 4 | 5 = 3 * 4 | 6 | 7 | 8=7/6
1 | 2022-04-01 | 1154 | 33213 | 38327802 | 98137 | 115274 | 1.1746
2 | 2022-05-01 | 1305 | 34652 | 45220860 | 98272 | 121604 | 1.2374
3 | 2022-06-01 | 1761 | 34002 | 59877522 | 98388 | 132189 | 1.3435
| 1st Qtr | 4220 | 101867 | 429878740 | 98388 | 369067 | 3.7511
4 | 2022-07-01 | 2001 | 38568 | 77174568 | 98485 | 164435 | 1.6696
5 | 2022-08-01 | 1517 | 33208 | 50376536 | 98910 | 115556 | 1.1683
6 | 2022-09-01 | 1758 | 34797 | 61173126 | 98568 | 131504 | 1.3341
| 2nd Qtr | 5276 | 106573 | 562279148 | 98568 | 411495 | 4.1747
7 | 2022-10-01 | 0 | 0 | 0 | 0 | 0 | #DIV/0!
8 | 2022-11-01 | 0 | 0 | 0 | 0 | 0 | #DIV/0!
9 | 2022-12-01 | 0 | 0 | 0 | 0 | 0 | #DIV/0!
| 3rd Qtr | 0 | 0 | 0 | 0 | 0 | #DIV/0!
1 | 2023-01-01 | 0 | 0 | 0 | 0 | 0 | #DIV/0!
2 | 2023-02-01 | 0 | 0 | 0 | 0 | 0 | #DIV/0!
3 | 2023-03-01 | 0 | 0 | 0 | 0 | 0 | #DIV/0!
| 4th Qtr | 0 | 0 | 0 | 0 | 0 | #DIV/0!
| Yearly Data | 9496 | 208440 | 1979346240 | 98568 | 780562 | 7.919

## SOP011-(OVERALL)
SoP 011 - A : System Average Interrruption Frequency Index (SAIFI) for PGVCL as a whole
Sr. No | Month | Ni - Number of Customers for each sustained interruptions (in numbers) | NT - Total No of customers served (in Numbers) | CI=∑ Ni | SAIFI = ∑ Ni/Nt (Monthly SAIFI)
1 | 2 | 3 | 4 | 5 | 6=5/4
1 | 2022-04-01 | 4864714 | 5703562 | 33772742 | 5.9213
2 | 2022-05-01 | 5090284 | 5703973 | 41880556 | 7.3423
3 | 2022-06-01 | 5253167 | 5706664 | 59685340 | 10.4589
| 1st Qtr | 15208165 | 5706664 | 135338638 | 23.7159
4 | 2022-07-01 | 5216461 | 5711446 | 67132316 | 11.754
5 | 2022-08-01 | 4994154 | 5721147 | 53110019 | 9.2831
6 | 2022-09-01 | 5122401 | 5729357 | 55662930 | 9.7154
| 2nd Qtr | 15333016 | 5729357 | 175905265 | 30.7024
7 | 2022-10-01 | 0 | 0 | 0 | #DIV/0!
8 | 2022-11-01 | 0 | 0 | 0 | #DIV/0!
9 | 2022-12-01 | 0 | 0 | 0 | #DIV/0!
| 3rd Qtr | 0 | 0 | 0 | #DIV/0!
1 | 2023-01-01 | 0 | 0 | 0 | #DIV/0!
2 | 2023-02-01 | 0 | 0 | 0 | #DIV/0!
3 | 2023-03-01 | 0 | 0 | 0 | #DIV/0!
| 4th Qtr | 0 | 0 | 0 | #DIV/0! |  |  | 54.3244
| Yearly Data | 30541181 | 5729357 | 311243903 | 54.3244
SoP 011 - B : System Average Interrruption Duration Index (SAIDI) for PGVCL as a whole
Sr. No | Month | Ri = Restoration Time for each sustained interruption event (in hours) | Ni - Number of interrupted Customers for each sustained interruption event (in numbers) | Ri* Ni - Total customer interrution Duration | NT - Total No of customers served (in Numbers) | Customer Intt. Duration CMI = ΣRi*Ni | SAIDI = ΣRi*Ni/Nt (Monthly SAIDI)
1 | 2 | 3 | 4 | 5 = 3 * 4 | 6 | 7 | 8=7/6
1 | 2022-04-01 | 0.07814 | 4864714 | 380127.5689 | 5703562 | 2114696.5908 | 0.37077
2 | 2022-05-01 | 0.10812 | 5090284 | 550370.6175 | 5703973 | 3624197.8229 | 0.63538
3 | 2022-06-01 | 0.10692 | 5253167 | 561685.9939 | 5706664 | 4525412.9067 | 0.793
| 1st Qtr | 0.29318 | 15208165 | 4458803.6492 | 5706664 | 10264307.3204 | 1899-12-31 19:10
4 | 2022-07-01 | 0.11311 | 5216461 | 590051.1538 | 5711446 | 4957598.8129 | 0.86801
5 | 2022-08-01 | 0.094581 | 4994154 | 472350.1159 | 5721147 | 3441088.5354 | 0.60147
6 | 2022-09-01 | 0.087166 | 5122401 | 446499.6046 | 5729357 | 3498238.5146 | 0.61058
| 2nd Qtr | 0.29486 | 15333016 | 4521092.9685 | 5729357 | 11896925.8629 | 1900-01-01 01:50
7 | 2022-10-01 | 0 | 0 | #DIV/0! | 0 | 0 | #DIV/0!
8 | 2022-11-01 | 0 | 0 | #DIV/0! | 0 | 0 | #DIV/0!
9 | 2022-12-01 | 0 | 0 | #DIV/0! | 0 | 0 | #DIV/0!
| 3rd Qtr | 0 | 0 | 0 | 0 | 0 | #DIV/0!
1 | 2023-01-01 | 0 | 0 | #DIV/0! | 0 | 0 | #DIV/0!
2 | 2023-02-01 | 0 | 0 | #DIV/0! | 0 | 0 | #DIV/0!
3 | 2023-03-01 | 0 | 0 | #DIV/0! | 0 | 0 | #DIV/0!
| 4th Qtr | 0 | 0 | 0 | 0 | 0 | #DIV/0! | 1900-01-02 20:50
| Yearly Data | 0.58804 | 30541181 | 17959584.0929 | 5729357 | 22161233.1833 | 1900-01-02 20:50
SoP 011 - C : Momentary Average Interruption Frequency Index (MAIFI) for PGVCL as a whole
Sr. No | Month | IMi = Number of Momentary interruptions for the month (in numbers) | Nmi = Total no of customers for each momentary interruptions (in numbers) | Imi =Nmi Number of customer Momentary interruptions (in numbers) | Nt - Total no of customers served (in numbers) | Customer Intt. ΣImi*Nmi | MAIFI=ΣImi*Nmi/Nt
1 | 2 | 3 | 4 | 5 = 3 * 4 | 6 | 7 | 8=7/6
1 | 2022-04-01 | 60440 | 4895724 | 295897558560 | 5703562 | 40128459 | 7.0357
2 | 2022-05-01 | 69711 | 4902116 | 341731408476 | 5703973 | 44569507 | 7.8138
3 | 2022-06-01 | 86762 | 5057608 | 438808185296 | 5706664 | 56359681 | 9.8761
| 1st Qtr | 216913 | 14855448 | 3222339792024 | 5706664 | 141057647 | 24.7181
4 | 2022-07-01 | 93386 | 5077884 | 474203275224 | 5711446 | 60974732 | 10.6759
5 | 2022-08-01 | 82443 | 4920614 | 405670180002 | 5721147 | 52398608 | 9.1588
6 | 2022-09-01 | 79398 | 5074062 | 402870374676 | 5729357 | 52572586 | 9.176
| 2nd Qtr | 255227 | 15072560 | 3846924271120 | 5729357 | 165945926 | 28.9641
7 | 2022-10-01 | 0 | 0 | 0 | 0 | 0 | #DIV/0!
8 | 2022-11-01 | 0 | 0 | 0 | 0 | 0 | #DIV/0!
9 | 2022-12-01 | 0 | 0 | 0 | 0 | 0 | #DIV/0!
| 3rd Qtr | 0 | 0 | 0 | 0 | 0 | #DIV/0!
1 | 2023-01-01 | 0 | 0 | 0 | 0 | 0 | #DIV/0!
2 | 2023-02-01 | 0 | 0 | 0 | 0 | 0 | #DIV/0!
3 | 2023-03-01 | 0 | 0 | 0 | 0 | 0 | #DIV/0!
| 4th Qtr | 0 | 0 | 0 | 0 | 0 | #DIV/0! | 53.5843
| Yearly Data | 472140 | 29928008 | 14130209697120 | 5729357 | 307003573 | 53.5843