## MG COVER PAGE
Name of Distribution Licensee: M G V C L
Annual
Year: 2023-24

## MG SoP 01
Name of Distribution Licensee: M G V C L
Annual 2023-24
Year:2023-24
Performa - SoP 001: Fatal and Non-Fatal electrical accident report
Annual 2023-24
Sr. No | Name of Area/Circle | Cumulative since the first quarter of the current FY 2023-24 |  |  | Cumulative since the first quarter of the Last FY 2022-23
|  | TOTAL |  |  | TOTAL
|  | FH | FA | NFH | FH | FA | NFH
1 | Baroda (City) | 8 (3-Pvt) | 2 | 1 | 1 | 0 | 3
2 | Baroda (O&M) | 11 | 23 (1-Pvt) | 9 | 12 (1-Pvt) | 19 | 11
3 | Anand | 12 (3-Pvt) | 13 | 4 | 3 | 5 | 2
4 | Godhra | 21 (6-Pvt) | 44 (1-Pvt) | 10 | 17 (9-Pvt) | 25 (2-Pvt) | 9
5 | Nadiad | 11 (1-Pvt) | 20 | 7 | 11 (2-Pvt) | 23 | 11
| TOTAL | 63 (13-Pvt) | 102 (2-Pvt) | 31 | 44 (12-Pvt) | 72 (2-Pvt) | 36
|  |  |  | 196 |  |  | 152

## SoP 002
Performa – SoP 003: Action taken report for safety measures complied for the electrical accidents occurred
ACTION TAKEN REPORT FOR SAFETY MEASURES COMPLIED FOR THE ELECTRICAL ACCIDENTS OCCURED IN THE FY 2023-24
1 | 2 |  |  | 3 | 4 | [5 empty] | 5 | 6 | 7 | 8 | 9 | 10
Sr. No | Location of Accident and details of the victim | Address | sdn | Date of occurrence | Type of Accident | Installation |  | Accident Type |  |  | Cause of Accident | Findings of CEI / EI / AEI | Remedies suggested by CEI /EI / AEI in various cases | Whether the remedy suggested is complied | Action taken to avoid recurrence of such Accident | Circle office
1 | Thakrda Vijaykumar Dahyabhai, Mujmohda, Sahjanand kutir laghu udhyog gate, Vill/Tal/Dist-Vadodara |  |  | 2023-04-18 | FHO | [5 empty] | LATE. SH. THAKARDA VIJAYKUAMR DAHYABHAI WAS SITTING ON EXISTING RSJ POLE FOR MAINTENANCE WORK OF 11 KV HT LINE AT LOCATION SAHJANAND KUTIR LAGHU UDHYOG GATE,THE LINE CLEAR OF 11 KV SAHJANAND KUTIR WAS TAKEN UNDER PLANN SHUT DOWN,VICTIM WAS FAINTED AND REMAIN AT TOP OF RSJ POLE WHICH WAS BROUGHT DOWN BY LADDER VAN AND TAKEN TO HOSPITAL WHERE HE WAS DECLARED DEAD. THE DEAD BODY HAS BEEN SENT FOR POSTMORTEM.PRIMA FACIE THE CAUSE OF THE DEATH IS MIGHT BE DUE TO RETURN POWER SUPPLY FROM THE GENERATO | Awaited | NA | NA | Show Cause issued to Line Inspector of Atladara Sdn Wide No. - VWD/HR/23/44, Dt-24.04.23 | Baroda City
2 | cow of Shri Yogesh Narsinh Makwana, Vill- juni ladvel, Tal-Lunawada, Dist-Mahisagar |  |  | 2023-04-22 | FA | [5 empty] | Due to wind at the juni ladvel vill the tree branch of the Gorasaamli tilted on the 11kv jumper of 11kv Thanasavli ag feeder DO tapping. And due to this the 11kv jumper may have touched with the Do angle of the DP structure And during this fault the animal may have came in contact with GI wire and Hence may get electeic shock.Also it came to notice that Yogesh Narsinh mamwana has tied his animal nearby to the said HT pole. | Awaited | NA | NA | JUMPER REPAIRED AND NECESSARY LINE MAINTENANCE WORK DONE | Godhra
3 | BULLOCK of AMALIYAR BACHUBHAI RAMSINGBHAI, GALALIYAWAD SARSATALAI TC, Vill-Galiyawad, Tal/Dist-Dahod |  |  | 2023-04-30 | FA | [5 empty] | DURING PRIMARY INVESTIGATION ON SPOT IT IS LEARNT THAT THE BULLOCK WAS WONDERING NEAR TRANSFORMER CENTER.TRANSFORMER CENTER AND LAND WAS WET DUE TO DAILY USED WATER COMING FROM NEAR BY HOME,THE BULLOCK MAY CAME IN CONTECT WITH TRANSFORMER PSC POLE AND ELECTROCUTED. | Awaited | NA | NA | MAINTENANCE OF TRANSFORMER DONE, NEW EARTHING DONE,PVC PIPE IS ADDED IN EARTHING | Godhra
4 | Buffalo of Thakor Ganpathsinh Bhursinh, Bhathhi faliya, Juni Vadi, Tal-Shahera, Dist PMS |  |  | 2023-05-03 | FA | FA |  |  |  |  | Due to heavy wind, B Phase to LT 3-ph 4 wire came in contact with angle which was touching stay wire. Since LT GUY was not there, leakage current was there. As buffalo experienced itching, it went near Stay wire got electrocuted and died on the sport. | Awaited | NA | NA | Pole Maimtance done , Stay set Providede By Guy Insnsulator. | Godhra
5 | Shree Kishor Mansing damor(Owener 01 nos. Female buffalo), VACHALU FALIYU, Vill-Chundadi, Tal-Singvad, Dist-Dahod |  |  | 2023-05-04 | FA | FA |  |  |  |  | Due to fault on LT side conductor snapped, Broken and fall on the ground. During the time of accident, The Buffalo was grazing below the LT line. As the Live conductor fall on the buffalo, came in contact and Electrocuted. | Awaited | NA | NA | Line made PDC due Arrears. | Godhra
6 | SHE BUFFALO OF PASAYA VAJESINH SAMABHAI, MAL FALIA, Vill-Rachva, Tal-Dhanpur, Dist-Dahod |  |  | 2023-05-10 | FA | FA |  |  |  |  | 11KV CONDUCTOR SNAPPED AND FELL ON GROUND WHERE BUFFALO WAS GRAZING , GOT ELECTROCUTED AND DIED | Awaited | NA | NA | NEW PIN INSULATOR IS INSTALLED AND CONDUCTOR BINDING IS DONE, MAINTENANCE WORK DONE | Godhra
7 | Shri Tansingbhai Shakariyabhai Ravat, KOTAR FALIYA, Vill-Abhlod, Tal-Garbada, Dist-Dahod |  |  | 2023-05-12 | FHO | FHO |  |  |  |  | As per primary investigation it has found that 11kv Abhlod Ag feeder passing inside boundary area of private land . Digging of soil was going on in that private land . As per site visit soil was dump below the line.the clearance between 11kv line and ground is reduced due to soil dumping below the line. As per eye witness , the victim climb on dumped soil below the line while talking on his mobile and by mistake touch to live conductor gets electric shock and died on spot | Awaited | NA | NA | CLEARANCE FROM GROUND IS MAINTAINED | Godhra
8 | SHE-Buffalow of Shree Snajaybhai Najubhai Rathwa, BHUMASVADA ROAD, Vill-Baidiya, Tal-Kawant, Dist-Chhotaudepur |  |  | 2023-05-22 | FA | FA |  |  |  |  | AS PER PRIMARY INVESTIGATION INFORMATION RECIEVED FROM VILLEGERS 11 KV CONDUCTOR HAD BROCKEN ADN FALLEN ON GROUND AND SHE-BUFFELO CAME IN CONTECT WITH LIVE CONDUCTOR AND GOT ELECTROCUTED. | AWAITED | NA | NA | CONDUCTOR RE-JOINT & POWER SUPPLY RESTORED. NO OTHER ACTION WAS TAKEN IN THIS MATTER. | Baroda O&M
9 | Damoe Parubhai Panjibhai, Bhadroli (Bujarg), Tal-Kalol, Dist-PMS |  |  | 2023-05-23 | FHO | FHO |  |  |  |  | Victim was unauthorized trying to provide DO fuse with help of plier and he was electrocuted | Awaited | NA | NA | Guided for not any operation himself on complain in MGVCL | Godhra
10 | SHE BUFFALO of Vajesinh Samabhai Pasaya, NILKANTHPURA, Vill-Virol, Tal-Mahemdabad, Dist-Kheda |  |  | 2023-05-29 | FA | FA |  |  |  |  | DUE TO HEAVY WIND AND RAIN DURING NIGHT,LT LINE GOT DAMAGED AND DETACHED WIRE CAME IN CONTACT WITH BUFFALO UNDER IT AND GOT ELECROCUTED. | AWAITED | NA | NA | DAMAGED LT LINE WAS REPLACED AND OWNER OF FARM INSTRUCTED TO NOT TIE HIS PET ANIMALS NEAR/UNDER ELECTRICAL LINE/STRUCTURE/POLE. | Nadiad
11 | SHRI RAIJIBHAI SHANABHAI TALPADA, mahadev faliyu, Vill-Punaj, Tal-Matar, Dist-Kheda |  |  | 2023-05-29 | NFHO | NFHO |  |  |  |  | VICTIM CLIMB ON HIS ROOF AND REARRANGE HIS ROOF ON HIS HOUSE SUDDENLY HE CAME IN CONTACT WITH LIVE WIRE OF 11 KV PUNAJ JGY | AWAITED | NA | NA | Immediately shifted for treatment. | Nadiad
12 | RAKESH D. KANOJIYA, Vill-BANAIYA, Tal-Dabhoi, Dist-Vadodara |  |  | 2023-05-30 | NFHD | NFHD |  |  |  |  | while cutting of tree branch on standing psc pole with operating rod victim accidentely came in contact with live conductor.victim got electric shock and fell down from psc pole, | Awaited | NA | NA | instruction of all line staff for use of safety articals at that time of work. | Baroda O&M
13 | BUFFALO OF DHIRUBHAI CHATRASINH PARMAR, Ramnagar Sim, Vill-Divel, Tal-Borsad, Dist-Anand |  |  | 2023-05-30 | FA | FA |  |  |  |  | SHE BUFFALO CAME ON CONTACT WITH LIVE LT BROKEN CONDUCTOR AND DIED ON SAID PLACE | Awaited | NA | NA | Open LT conductor replaced with 2W AB cable | Anand
14 | COW OWNED BY KARSANBHAI DANABHAI BHARWAD, NR NSJ Vill-MACHHIPURA, Tal-Sankheda, Dist-Chhotaudepur |  |  | 2023-05-31 | FA | FA |  |  |  |  | Insulation of LT ABC got damaged and slipped which came in contact of GI wire through U clamp and Runnig wire of Un Charged HT ABC laid bt not charged from Village Tc to NSJ DP and got leak at NSJ DP where the cow came in contact of GI for earthing and got electrocuted. | AWAITED | NA | NA | Provided Of Tap in LT ABC | Baroda O&M
15 | Vishvarajsinh Dilipsinh Chauhan, Bhaibapura, Vill-Pratappura, Tal-Umreth, Dist-Anand |  |  | 2023-05-31 | FHO | FHO |  |  |  |  | Due to Heavy Cyclonic wind nearby tree branch fell on service line of Ranjitsinh U Chauhan, victim was passing from there & at that time victim came in contact to the metal wire used for fixing metal sheets on roof.Due to tree branch fell on service line insulation of service line came in contact with metal sheet of roof and victim might be electroculated on dtd.31.05.23 | Awaited (Visit on 13.06.23) | NA | NA | Tree branch removed. Service line replaced. | Anand
16 | Buffalo of Vill-Kanetiya |  |  | 2023-05-31 | FA | [5 empty] | Buffalo passing near from T/C Centre and conatact with LT Distribution Box and got electrcutrd | Awaited | NA | NA | Distribution box in New kit kat fuse provided, GI EARHING done by insulation pipe. | Godhra
17 | Abbasmiya Ismailmiya Malek, Vill-Bandhani |  |  | 2023-06-02 | NFHO | [5 empty] | On date 19-06-2023 a letter received from mahelav police station regarding non fatal accident case On Dated 02.06.2023 at approx. time 11:00 hr at Village- Bandhani ,Ta: Petlad on 11 KV Piplav JGY Feeder Loc No mhl/plv jgy/015/9/14 victim shri Abbasmiya Ismailmiya Malek and his colleague were working on new construction construction contract of Udesinh Bakorbhai Solanki's shop near bandhani chowkdi , sunav road and 11 KV Piplav JGY and suddenly victim Abbasmiya Ismailmiya Malek stands on butter | Awaited | NA | NA | Notice issued for unauthorised construction | Anand
18 | goats of Vill-Koli na Puvada |  |  | 2023-06-04 | FA | [5 empty] | At that accident place many goats eating a grass near the LT line broken pole. This pole was broken with open 04 wire LT line due to wind storm with heavy rain. And also at dt:-04.06.2023, Sunday in morning approx... 09:30 am wind storm with heavy rain came in this area. So due to wind storm 11KV NAGVAV JGY FDR LT & 11KV GUNA AG FDR LT came in contact with each other and current flow from JGY LT TO AG LT. So at that time goats eating grass near the AG LT line and 03 nos. of goats came in contact | Awaited | NA | NA | REMOVED THE AG And JGY LT LINE CROSSING | Godhra
19 | PIYUSHABHAI GOPALBHAI CHUNARA, Vill-Vadodara |  |  | 2023-06-04 | FHO | [5 empty] | DUE TO HEAVY WIND AND CYCLONE THREE PHASE SURVICE WIRE FIRE NEAR JOINTS WITH ABC AND MIGHT BE COME IN TOUCH TEMPORARIALY WITH GIRDER POLE DUE TO WHICH LEAKAGE CURRENT MAY HAVE PASS THROUGH GIRDER POLE AND VICTIM MAY COME IN CONTACT WITH THE GIRDER POLE AND GET ELECTROCUTED EVENTHOUGH AT SITE NO ANY SYMPTOM OF ELCTROCUTION ON RSJ POLE IS FOUND. | Awaited | NA | NA | All burnt Service line are replaced by New one. New Jumpers are provided. | Baroda City
20 | SHE CALF OF COW of unknown, Vill-Dabhoi |  |  | 2023-06-06 | FA | [5 empty] | LEAKAGE CURRENT MIGHT BE DUE TO BROKEN STAY WIRE TOUCHED THE LIVE PART OF YAMUNANAGAR DODP | Awaited | NA | NA | stay wire romoved | Baroda O&M
21 | Shri Rajubhai Baldevbhai Parmar, Vill-Santrampur |  |  | 2023-06-10 | FHO | [5 empty] | Late Shri Rajubhai baldevbhai Parmar, resident of Rampiri Chali, Jamalpur, Ahmedabad, on 10.06.2023, at around 17.00 Hrs, a labourer of New France Bakery (Bakery opened on Rent by Naushad Yusuf Ansari, Ahmedabad) at the ground floor beneath Aarzoo Auto Parts, climbed the terrace of the building owned by Salim Ishaq Bhura, to finalize the location of New France Bakery Bill Board, alongwith his neice, but unknowingly he came in contact with the H.T. Line. Afterwards, he became unconscious & uncomf | Awaited | NA | NA | NOTICE ISSUED TO PARTY FOR UN AUTHORISED CONSTRUCTION | Godhra
22 | 2NOS COW & 1NO CALF, Vill-NIZRAN DILGAM |  |  | 2023-06-11 | FA | [5 empty] | CONDUCTOR SNAP DUE TO TREE BRANCH FALLEN ON POLE NO. JGD/KDV/HPR/253 | Awaited | NA | NA | Tree cutting work done and restringing Of conductor done. | Godhra
23 | jagdishbhai govindbhai sejva, Vill-Rajnagar |  |  | 2023-06-11 | FHO | [5 empty] | Suspected | Awaited | NA | NA | Re-stringing of conductor | Baroda O&M
24 | Sh. Vinubhai Ninama, Vill-Ratanpur |  |  | 2023-06-11 | NFHO | [5 empty] | As per site visit and eyewitness statement, at open space of the Bharatnagar society, Between HT pole location of KTB/KTB/JGY/101 & KTB/KTB/JGY/101/01 under the HT line of 11 kV Khatamba feeder, Sh. Vinubhai Ninama, driver of Eicher Dumper, was doing ‘land levelling -Mati Puran’ work in the open space of the Bharatnagar society, in front of house of Sh. Shelabhai Rama Bhai Bharwad at the request/ instruction of him (i.e. Sh. Shelabhai Rama Bhai Bharwad), resident of Bharatnagar Society. During | AWAITED | No | No | both side v cross arm extention | Baroda O&M
25 | Manekben Bharatbhai Padhiyar, Vill-Kalamsar |  |  | 2023-06-15 | FHO | [5 empty] | Due to Heavy wind flow in " BIPARJOY" cyclone , Service wire and its support GI wire broken at the same time victim may came in contact with service wire and GI wire and electrocuted. | Awaited | NA | NA | Removed broken GI wire and rectified by providing new service line | Anand
26 | 2 BUFFALO AND 1 CALF of Vill-Nadiad |  |  | 2023-06-16 | FA | [5 empty] | DUE TO HEAVY WIND LT OPEN POLE BROKEN AND CONDUCTOR SNAPPED DOWN AND 2 BUFFALO AND 1 CALF CAUGHT IN TOUCH WITH LIVE CONDUCTOR AND ELECTROCULATED | AWAITED | NA | NA | LT line passing through trees is re-routed and open conductor changed to AB Cable. | Nadiad
27 | COW OF LALITBHAI NARANBHAI PATEL, Vill-Shahpura |  |  | 2023-06-16 | FA-Pvt | [5 empty] | As per statement and information recieved from eye witness & owner, due to heavy wind and rainfall, conductor of streetlight snapped and buffalo which was tied underneath the LT Line, came in contact with live wire and got electrical shock & died on the spot | AWAITED | No | No | strert light wire joint and gaurdine done | Baroda O&M
28 | Maheshbhai Natubhai Sindha, Vill-Banejada |  |  | 2023-06-16 | FHO-Pvt | [5 empty] | Reparing of Shed galavanised Sheet Touch with open Wire and Victim Electrocuted | Awaited | NA | NA | Collecter new TR of internal wiring | Anand
29 | BUFFALO OF RANCHODBHAI SAVDASBHAI BHARWAD, Vill-SEVALIYA |  |  | 2023-06-17 | FA | [5 empty] | BIG TREE BRANCH OF SEVAN TREE BROKEN AND FALL DOWN ON LT LINE ONE CONDUCTOR BROKEN AND FALL BUFFALO PASSING NEAR TO BE LINE DIED ON SPOT | AWAITED | NA | NA | FALLEN TREE BRANCH CUT DOWN AND DAMAGED LT WIRE REPAIRED. | Nadiad
30 | DAMOR VASANTBHAI JAHUBHAI, Vill-NANSALAI |  |  | 2023-06-17 | FA | [5 empty] | AS PER STATEMENT OF EYE WITNESS COW OF SHREE VASANTBHAI JAHUBHAI PASSING THROUGH TRANSFORMER CENTRE,LAND WAS WET DUE TO RAIN COW MAY CAME IN CONTACT WITH EARTHING WIRE AND ELECTROCUTED AND DIED ON THE SPOT | Awaited | NA | NA | MAINTENANCE OF TRANSFORMER DONE, NEW EARTHING DONE,PVC PIPE IS ADDED IN EARTHING | Godhra
31 | Cow- 2 Nos of Vill-Paladi |  |  | 2023-06-17 | FA | [5 empty] | It is found that due to heavy winds, One LT conductor is snapped down and cows were passing through Jagdishbhai's farm where incident happened, cows were come in contact with conductor and got electrocuted. | Awaited | NA | NA | Conductor rejoint done and restringing of conductor done | Godhra
32 | Shri Jayeshbhai Raijibhai Parmar, Vill-Kasor |  |  | 2023-06-17 | FHO-Pvt | [5 empty] | On Dated 17.06.2023 at approx. time 11:30 hr at Village- kasor ,Ta: Sojitra on 11 KV Ganganagar JGY Feeder LT Line Loc No GGN JGY/004/LT/013 near consumer no 04702023322 of parmar raijibhai maganbhai. Victim Late. Shri Parmar Jayeshbhai Raijibhai was helping his father in tree cutting and unauthorized street light wire was hanged on iron road and two open wire which was used month ago in halogen light for his marriage and no any precaution was taken by victim him self. un authorized open stre | Awaited | NA | NA | Removed illegal temporary wire from street ltg pole | Anand
33 | SHANKARBHAI SHANABHAI PADHIYAR, Vill-Chamara |  |  | 2023-06-17 | FHO-Pvt | [5 empty] | During Primary investigation accident met at victim private Premises of his Negligence with house open wiring hand touched with any Live open wiring and got electrode and met accident | Awaited | NA | NA | Notice for proper wiring and new test report issued.Connection disconnected. | Anand
34 | OWNER: MANGABHAI GOKALBHAI CHAUHAN, Vill-Amarpura |  |  | 2023-06-18 | FA | [5 empty] | 1 PH 2 WIRE JGY LT OF 11 KV SOJALI JGY FDR PASSING THROUGH THE PREMISES OF MANGABHAI GOKALBHAI CHAUHAN FARM, AT LOC. MANGABHAI GOKALBHAI CHAUHAN FARM VILL: AMARAPURA FOR LT 1 PH CONNECTION. THIS LT LINE IS VERY OLD 1 PH 2 WIRE AAAC 34 MMSQ. DUE TO HEAVY WIND AND RAINFALL CONDUCTOR FALL DOWN TO EARTH. AND OWNER TAKE OFF FUSE FROM DISTRIBUTION BOX BUT AFTER SOMETIME UNKNOWN PERSON CONNECT FUSE IN THE BOX AND BUFFALO CAME IN CONTACT WITH LIVE CONDUCTOR AND DIED ON SPOT. | AWAITED | NA | NA | CONDUCTOR JOINT REMOVE | Nadiad
35 | KANUBHAI KHIMABHAI BHARWAD, Vill-Varsada |  |  | 2023-06-18 | FHO | [5 empty] | DUE TO BIPORJOY CYCLONE HEAVY WIND FLOW AND RAIN OCCURED IN THIS ARAE .SO AT ABOVE LOC.11 KV COATED CONDUCTOR IS BROKEN WHICH COMES IN CONTACT WITH THE VICTIM AND ELECTROCUTE AND FATAL ACCIDENT OCCURED .THERE IS NO ANY INTERRUPTION RECORDED IN THIS TIME AT 66 KV KHANPUR SS END. | Awaited | NA | NA | Joint provided to broken conductor and restringing done | Anand
36 | Kiranbhai Naginbhai Prajapati, Vill-Bhuvel |  |  | 2023-06-22 | FHO | [5 empty] | As per eye witness statement victim was repairing of street light without shut off the power ans without intimation of this office or village helper.During reparing work he might be touch live wire of street light and got electrocuted. | Awaited | NA | NA | No action required | Anand
37 | DAXITKUMAR SHAILESHBHAI GOHEL, Vill-Shahpur |  |  | 2023-06-24 | NFHO | [5 empty] | VICITM WAS LANDING ON SLOPE OF LAND NEAR TO THE GROUND AND ALSO LAND OWNER DIG THE SOIL AND PUTTED ON ONE SIDE AND DUE TO THIS LITTLE LINE TO GROUND CLARANCE AND VICITM ACCIDENTALLY VICITM COMES IN CONTACT WITH LIVE CONDUCTOR AND GOT ELECTRIC SHOCK | AWAITED | NA | NA | Immediately Shifted To Carewell Hospital Kathlal For Treatment , His Condition Is Critical And Right Now He Is In ICU. | Nadiad
38 | COW OF RAJUBHAI GHELABHAI BHARVAD, Vill-Pilag |  |  | 2023-06-24 | FA | [5 empty] | COW OF RAJUBHAI GHELABHAI BHARVAD PASSING BETWEEN TRANSFORMER CENTER AND SUDDANLY FALL DOWN ON LAND AND DIED BUT THERE IS NO ANY LEKAGE CURRENT FOUND | AWAITED | NA | NA | Outgoing cable from transformer is changed from ABC to PVC cable. | Nadiad
39 | TWO NO COWS of Vill-Godhra |  |  | 2023-06-24 | FA-Pvt | [5 empty] | THERE WERE INTERNAL WIRING PROBLEM IN STREET LIGHT CONTROLLING BOX AND DUE TO THAT PROBLRM LEACKAGE CURRENT WAS FLOWING FROM BOX TO EARTH WIRE OF PSC POLE & THESE TWO COWS CAME IN CONTACT WITH THIS POLE & GOT ELECTROCUTED & DIED. | Awaited | NA | NA | Informed to Nagarpalika Chief Officer | Godhra
40 | COW of Vill- DHOKALIYA |  |  | 2023-06-25 | FA | [5 empty] | AS PER SITE VISIT IT IS FOUND THAT THEIR IS NO LEAKAGE CURRENT AT THE TIME OF SITE VISIT BUT IT IMAY BE POSSIBILITY OF LEAKAGE CURRENT PASS THROUGH TRANSFOEMER EARTHING WIRE AND THAT TIME COW WAS CONTACT WITH EARTHING WIRE AND GOT ELECTROCUTED & DIED. | AWAITED | NA | NA | DUE TO WADI CONNECTION CONSUMER SIDE WIRING SHOT THE RETURN CURRENT CAME FROM NEUTRAL TO TRANSFORMER EARTHING WIRE. SO DISCONNECT SUPPLY OF WADI CONNECTION AND AFTER RECTIFICATION OF WIRING THE FRESH TEST REPORT TAKEN AND POWER SUPPLY RESTORED TO WADI CONNECTION. EARTHING PIPE INSTALLED IN TRANSFORMER EARTHING WIRES. | Baroda O&M
41 | RAMESHBHAI SHELABHAI BHARVAD, Vill-MANJIPURA |  |  | 2023-06-26 | FA | [5 empty] | The cow of Shri Rameshbhai Shelabhai Bharvad passing through 11 mtr RSJ girder Loc no- DRN/JGY/076 , LT jumper touch the 11 mtr RSJ girder and current pssing through this girder and cow was electrocuted and died | AWAITED | NA | NA | Re-jumpering done and tape provided. | Nadiad
42 | BUFFALO of Vill-Tarapur |  |  | 2023-06-26 | FA | [5 empty] | ON THAT DAY AT THE TIME OF ACCIDENT RAIN IS RAINING ,AT THAT TIME ONE CONDUCTOR SNAPPED OF LT BARE CONDUCTOR LINE DUE TO LEAKAGE CURRENT ONE BUFFALO GOT ELECTROCUTED NEAR LT POLE OF THE LINE. | Awaited | NA | NA | 4W LT bare conductor rejointed and stringing done and conductor tied with shackle insulator properly | Anand
43 | MOHANSINH LALSINH RAWAT, Vill-Alwa |  |  | 2023-06-27 | NFHO | [5 empty] | It is come to the notice that during new line erection work of AGDZ paid pending application as given to contractor M.M.RAJPUT by subdivision,Shri saidabanu mansuri at village-Alwa , victim(contract persons) shri Mohansinh Lalsinh Rawat one of gang member of M.M.RAJPUT electrical line work contractor was electrocuted as victim was climbing on the existing PSC POLE of 11 KV Alwa AG feeder live line with 4 ft 6 inch MS Tapping angle fitting.At that time the fitting of tapping angle to PSC POLE | AWAITED | NA | NA | ICTIM WAS IMMEDIATLY SENT TO HOSPITAL FOR TREATMENT | Nadiad
44 | SOLANKI GORDHANBHAI SANABHAI, Vill-Talsat |  |  | 2023-06-27 | FHO | [5 empty] | As per information received from owner of house, shree Chhaganbhai Mayajibhai, his home is under construction and Victim was arranging Iron angle (Approx 20 Ft Long) at construction site, angle came in to contact with live conductor of 11 KV Pawan Urban feeder passing near by this house and victim got electrocuted and died | Awaited | NA | NA | neglince from victim no any action requred by discom | Baroda O&M
45 | BUFFELO OWNER : BHARWAD RANCHHODBHAI NAGABHAI, Vill-Sokhda |  |  | 2023-06-29 | FA | [5 empty] | Buffelo was grazing near by the existing HT line of NEJA Ag feeder and one conductor snapped and fall on the victim and got electrocuted | Awaited | NA | NA | 50 meter conductor replaced with 55 mm2 and restringing done | Anand
46 | 1 Buffelo Owner Babarbhai Dahyabhai Rathod, Vill-Maghrol |  |  | 2023-06-29 | FA | [5 empty] | At above address, Buffalo was returning to home .Due to heavy wind and rain, jumper of lt line dropper touches to the earth GI wire, so that leakage earth current, Buffalo may be dead. | Awaited | NA | NA | LT line jumper repaired and GI wire rectified with earth | Anand
47 | cow of Vill-Serkhi |  |  | 2023-06-29 | FA | [5 empty] | on Dated 29.6.23 while Shri Rabari Dilipbhai Govindbhai grazing his cow and cow electrocuted at PSC pole Guy wire. Tree was fall on line at lOC- GTR/SVS/VM/TC-2/CR-2/006, hence this pole got tilted and support GI wire of service broke which was got touch to service wire dropper and got live, this live support GI wire got touch with guy wire, that time caw was passing near the above said pole and got touch with live guy wire and got electrocuted. | AWAITED | NA | NA | GI wire and service line rectified | Baroda O&M
48 | BULLOCK, Vill-Makani |  |  | 2023-06-29 | FA | [5 empty] | DUE TO DAMAGE OF INSULATION OF LT ABC | Awaited | NA | NA | PROVIDENIG TAP TO LT ABC | Baroda O&M
49 | COW of Vill-Zaverpura |  |  | 2023-06-29 | FA | [5 empty] | AS PER SITE VISIT IT IS FOUND THAT THEIR IS LT LINE SUPPORT WIRE WAS TOUCHED TO STAY PAIR OF LT POLE .SO THAT LEAKAGE CURRENT PASS THROUGH EARTHING WIRE AND THAT TIME COW WAS CONTACT WITH EARTHING WIRE AND GOT ELECTROCUTED & DIED | AWAITED | NA | NA | THIS IS THE LAST POLE OF LT LINE. DUE TO SUPPORT WIRE OF LT AB CABLE BREAKE, THE PHASE OF LT AB CABLE IS TOUCH TO THE EARTHING WIRE OF POLE. SO SEPARATE THE PHASE OF LTAB CABLE & EARTHING PIPE IS INSTALLED IN EARTHING WIRE OF POLE. | Baroda O&M
50 | buffelo of Vill-Chaliyer |  |  | 2023-06-29 | FA | [5 empty] | buffelo passing near location of lt line and toching of that pole | AWAITED | NA | NA | Replaced shackle insulator with U clamp also stringing and maintenance of LT line. | Baroda O&M
51 | BULLOCK of Vill-Madodhar |  |  | 2023-06-29 | FA | [5 empty] | An bullock was passing near transformer loc-wgh/jgy/88/10 and got shocked by touching pole and got electrocuted due to rain water passing through transformer area at that time of incident and bullock may come in contact with leakage current | AWAITED | NA | NA | Pipe provided on earthing wire and maintenance of TC. | Baroda O&M
52 | COW of Vill-Godhra |  |  | 2023-06-29 | FA | [5 empty] | FALLEN TV CABLE WIRE FROM RSJ POLE WAS STRETCHED BY COW & NEUTRAL DROP ON POLE TOUCHED WITH THIS POLE & LEACKAGE CURRENT STARTED FLOWING FROM POLE TO EARTH & THIS COW CAME IN CONTACT WITH THIS POLE & GOT ELECTROCUTED & DIED. | Awaited | NA | NA | Pole Maimtance done & Notce Issued to TV Cable Net work Owner. | Godhra
53 | GOAT of vill-NAVCHETAN |  |  | 2023-06-29 | FA | [5 empty] | ON 29.06.2023 DUE TO HEVAY RAIN AND WIND TREE FALLEN ON LT LINE AT SHAKTIPURA VISTAR OF NAVCHETAN VILLAGE. DUE TO THAT LT LINE GOT DAMAGED AND TOUCHED WITH EARTHING WIRE OF POLE. GOAT OF SHREE BHANUBHAI DEVABHAI BHARVAD PASSING NEARBY THAT LIVE WIRE ACCIDENTLY CAME IN CONTACT WITH THAT EARTH WIRE AND GOT ELECTROCUTED. | AWAITED | NA | NA | FALLEN TREE BRANCH CUT DOWN AND DAMAGED LT WIRE REPAIRED. | Nadiad
54 | SHE COW of vill-NAVCHETAN |  |  | 2023-06-29 | FA | [5 empty] | ON 29.06.2023 DUE TO HEVAY RAIN AND WIND TREE FALLEN ON LT LINE AT SHAKTIPURA VISTAR OF NAVCHETAN VILLAGE. DUE TO THAT LT LINE GOT DAMAGED AND TOUCHED WITH EARTHING WIRE OF POLE. COW OF SHREE LAXMANBHAI DEVABHAI BHARVAD PASSING NEARBY THAT LIVE WIRE ACCIDENTLY CAME IN CONTACT WITH THAT EARTH WIRE AND GOT ELECTROCUTED. | AWAITED | NA | NA | FALLEN TREE BRANCH CUT DOWN AND DAMAGED LT WIRE REPAIRED. | Nadiad
55 | BUFFALOW of Vill-Singvad |  |  | 2023-06-30 | FA | [5 empty] | ON DATE 30.06.2023 NEAR GOVERNMENT HOSPITAL SINGVAD AT COLLAGE 63 KVA DP STRUCTURE A BUFFALOW WAS FOUND DEAD DUE TO UNKNOWN REASONS AT PRESENT OR MAY HAVE DIED DUE TO ELECTRICK SCHOCK | Awaited | NA | NA | TC STRUCTURE MAINTENANCE CARRIED OUT, NEW EARTHING DONE,PVC PIPE IS ADDED IN EARTHING | Godhra
56 | VANITABEN THAKORBHAI KATARA, Vill-CHITRODIYA |  |  | 2023-06-30 | FHO | [5 empty] | AS PER PRIMARY INVESTIGATION INFORMATION RECEIVED FROM EYE WITNESS,VICTIM WAS DOING GRASS CUTTING IN FARM ALSO LAND WAS WET DUR TO RAIN SUDDENLY VICTIM WAS CAME IN CONTACT WITH EARTHING WIRE OF THE LT POLE AND ELECTROCUTED AND DIED ON THE SPOT | Awaited | NA | NA | RECTIFIED SERVICE WIRE WHICHES WAS TOUCHED TO THE EARTHING WIRE, AFTER THAT NO POWER IN EARTHING WIRE. | Godhra
57 | DHIRUSINGBHAI RAYSINGBHAI BARIA, Vill-CHAMARIA |  |  | 2023-06-30 | NFHO | [5 empty] | As per primary investigation information recieved from MGVCL ZALOD staff who are working on site , rectifying broken 11kv line conductor they isolated all the location of live power and doing work on site while stringing the 11kv wire victim who is standing near the location and he had tried to away conductor from house with his hand and elecrocuted and injured on both hand. | Awaited | NA | NA | BROKEN CONDUCTOR OF 11KV NENKI JGY FEEDER RECTIFIED | Godhra
58 | Pitamsinh Babusinh,Sureli Bechri Road,Vill-Sureli,Ta-Umreth,Dist-Anand |  |  | 2023-06-22 | FHO | [5 empty] | BIG CONTAINER WAS PASSING THROUGH SURELI BECHRI ROAD AND ACCIDENTLY CAME IN TOUCH WITH 11 KV DHULETA JGY FEEDER AND DRIVER GOT ELCTROCULATED | Awaited | NA | NA | V EXTENSION PROVIDED HIGHT MAINTAINED | Anand
59 | 2 bullock of Jasu Pratap Baria,vakasiya mal falia,Vill-Vakasiya,Tal-Dhanpur,Dist-Dahod |  |  | 2023-07-01 | FA | [5 empty] | DUE TO CONTACT OF UNCHARGED 11KV LINE WITH LT LINE OF JGY , AND 11KV UNCHARGED LINE CONDUCTOR KEPT ON GROUND , BULLLICK CAME IN CONTACT WITH LIVE WIRE AND DIED | Awaited | NA | NA | THE LOCATION IS RECTIIFED AND STRINGING AND BINDING OF UNCHARGED WIRE IS CARRIED OUT. | Godhra
60 | Buffalo,Dakaniya,Vill-Othvad,Tal-Balasinor, Dist-Mahisagar |  |  | 2023-07-02 | FA | [5 empty] | HERD OF BUFFALO WAS PASSING BY VILLAGE TC AS PER ROUTINE. ONE BUFFALO SUDDENLY FALL ON GROUND AND DIED ON SPOT. AS PER TALK WITH OWNER, BUFFALO TOUCHED THE METAL DB AND DIED, DURING SITE VISIT NO LEAKAGE CURRENT WAS FOUND AT ANY POINT ON TC STRUCTURE. | YES | To follow Regulation Act 2010 Sr No. 12 and 13 | Yes | AT THE TIME OF DEATIL INVESTIGATION NO CAUSE FOUND OF LEAKE CURRENT | Nadiad
61 | Bullock,Tandi faliyu, Vill-Agarwada, Tal-MORVAHADAF, Dist-Panchmahal |  |  | 2023-07-03 | FA | [5 empty] | Due to aging effect there is a possibility that insulation of LT AB cable got damaged so contacted with GI wire of LT pole earthing and leakage current flow to wet ground. | Awaited | NA | NA | LT ABC replaced & Necessary Line Maintance done. | Godhra
62 | FEMALE HORSE OF RAVJIBHAI PATANWADIYA,NEAR SAWMILL,Vill-ANKHI,Tal/Dist-Vadodara |  |  | 2023-07-03 | FA | [5 empty] | INSULATION OF AB CABLE WAS DAMAGED, AND CONDUCTER SCRUB WITH RSJ POLE. | Awaited | NA | NA | Pipe provided on earthing wire and maintenance of TC. | Baroda O&M
63 | DINESHBHAI PARVATBHAI BARIA,DAYRA FALIYU,B/H. IOC PETROL PUMP EXTENDED PREMISES,Vill-WAGJHIPUR, Tal-Shahera, Dist-PANCHMAHAL |  |  | 2023-07-04 | FHO | [5 empty] | VICTIM WAS LOADING TRACTOR TROLLY WITH CIVIL CONSTRUCTION CENTING MATERIAL,SAND,LONG IRON ROADS ETC. TRACTOR WAS PARKED UNDER 11 KV SARADIYA JGY FEEDER OVERHEAD HT LINE AND DURING THE WORK ONE IRON ROAD APPROX. 10 FEET LONG, VICTIM HOLDING IN HIS HAND ACCIDENTILY COME IN CONTACT WITH LIVE HT LINE AND GOT ELECTROCUTED DUE TO HIS NEGLIGENCE AND INATTENTION | YES | NA | NA | Necessary Line Maintance done. | Godhra
64 | Cow owner Name Bharwad Bhanabhai Bhikhabhai,Haripura Lat, Vill-Motipura, Tal-Khambhat, Dist-Anand |  |  | 2023-07-04 | FA | [5 empty] | Fatal Animal accident occurred on dated 05.07.23 time approx. 15:00 hours, During visit at site on Dtd 05.07.23,it is found that the accident took place on the 11KV Malu AG feeder at DO DP Structure having location No.075/15/9 While grazing on farm ,A Cow was scratching with stay wire cause it might have been pulled slightly , due to this upper part of stay wire touched to DO fuse jumper and current may have passed on stay and cow got electrocuted and died on the spot. | Awaited | NA | NA | new stay wire porvided & new jumper provided | Anand
65 | Buffalo,Nr Darjipura Prathmik School,Vill-Darjipura,Ta/Dist-Vadodara |  |  | 2023-07-06 | FA | [5 empty] | Fatal animal electrical accident, the buffalo was passing near the LT Line pole, where she must have contact with earthing wire of pole, the leakage current must have caused the accident death of that buffalo. | Awaited | NA | NA | New Service Provided and Open LT line converted to LT ABC | Baroda City
66 | COW,OPP. KEDI TEMPLE,Vill-KEDI,Ta-Balasinor,Dist-Mahisagar |  |  | 2023-07-06 | FA | [5 empty] | COW CAME IN CONTACT WITH RSJ POLE RUNNING 4W LT ABC. INSULATION OF LT ABC GOT DAMAGED DUE TO FRICTION DURING CYCLONIC WINDS. SO CURRENT LEAKED FROM DAMAGED INSULATION TO U CLAMP TO GROUND. | YES | To follow Regulation Act 2010 Sr No. 12 and 13 | Yes | DAMAGE PORTION OF LT ABC CABLE REPLACE | Nadiad
67 | Cow of Shri Bharvad Rahulbhai Laxmanbhai,In the farm of Shri Dolatsinh Nathusinh Thakor,Vill-Vyasda,Ta-Kalol,Dist-Panchmahal |  |  | 2023-07-07 | FA | [5 empty] | At location no.3 of LT line of the AG transformer of Village. Vyasda Y phase conductor release from shackle insulator and touched to U-Clamp and thus leakage current started to flow from neutral wire of transformer center. Victim came in contact with neutarl wire got electrocuted and met with fatal electrical accident. | Awaited | NA | NA | Y Phase conductor relocate at shackel insulatore and maintanance done. | Godhra
68 | LAXMANBHAI LALLUBHAI BHIL,NAVINAGARI,OPP GWSSB PLANT,Vill-Sadhali,Ta-Sinor,Dist-Vadodara |  |  | 2023-07-07 | FHO | [5 empty] | The victim was trying to fix long round pipe on top of tempo trailer.While doing so pipe came in contact with 11 kv live line conductor and got electrocuted. | Awaited | NA | NA | due to negligance of victim | Baroda O&M
69 | BAFALLO,NR BALETIYA SEEM BUBEN KOTAL DELHI MUMBAI EXPRESSWAY,Vill-BALETIYA,Ta-Kalol,Dist-Panchmahal |  |  | 2023-07-08 | FA | [5 empty] | As Per Eyewitness Statement Bafallo Trying To Eat Grass Around LT Pole And Touched To Pole And Get Electric Shock And Dead At The Momment | YES/1032/04.09.2023 | follow the CEA regulation-2010 - regulation no. 12 | NA | LT Wire Coated And Restringing With Lt Shackel Insulator | Godhra
70 | UNKNOWN,SHREEJI PARTY PLOT,Vill/Tal/Dist-Vadodara |  |  | 2023-07-09 | FHO-Pvt | [5 empty] | THERE IS 80KW LT CONNECTION IS GIVEN TO SHREEJI PARTY PLOT.40/200A METER IS INSTALLED NEARER TO 100KVA SHREEJI PARTY PLOT TC.150SQMM LT CABLE PASSING THROUGH METER IS CONNECTED TO 70 SQMM LOAD SIDE LT CABLE. DISTRIBUTION OF POWER INSIDE PREMISES OF SHREEJI PARTY PLOT IS DONE THROUGH 50SQMM LT CABLES. ONE END OF THE LOAD SIDE LIVE 16SQMM LT UG CALBE CONNECTED TO THE LT BUSBAR. SECOND END OF 16SQMM LT UG CABLE IS CONNECTED TO THE MCB INSTALLED INSIDE THE SMC BOX AFFIXED ON IRON TOWER.SAID 16SQMM | Awaited | NA | NA | Circuit-wise ELCB provided on load side wiring of consumer. | Baroda City
71 | Kaliben Dineshbhai,Vill/Tal/Dist-Dahod |  |  | 2023-07-09 | FHO-Pvt | [6 empty] | Awaited | NA | NA | NO ANY LEAKAGE CURRENT WAS FOUND.AS THE ACCIDENT HAPPENED DUE TO FAULTY WIRING ON CONSUMER'S SIDE, THE CONNECTION WAS DISCONNECTED. | Godhra
72 | COW,HADIYA VISTAR,Vill-BUDHEJ, Tal-Tarapur, Dist-Anand |  |  | 2023-07-10 | FA | [5 empty] | AT ABOVE LOCATION APPROXIMATE 20 COWS ARE PASSSING FOR GRAZING WITH OWNER ACCIDENTALY AMONG ALL COWS ONE COWS CAME INTO CONTACT WITH LT LINE POLE APPROX. 1 METER AWAY. DUE TO HEAVY WIND AND RAIN INSULATION DAMAGED OF LT ABC SINGLE PHASE TWO WIRE ALSO SLIPPED AND TOUCHED TO C CLAMP OF LT LINE AND ALSO TOUCHES TO THE GI WIRE,SO THAT LEAKAGE EARTH CURRENT COW MAY BE DEAD.(PM REPORT AWAITED) | Awaited | NA | NA | restringing of abc & rectification of gi wire | Anand
73 | Solanki Ashokbhai Motibhai,Vill-moxi padhro,Ta-Savli,Dist-Vadodara |  |  | 2023-07-13 | FA | [5 empty] | 13-07-2023 at 17:15 hrs visited site and prepared panchnama. Information received at office by S.N.Baranda (EA) that incident happened due to leakage current passing through earth wire via D clamp of LT ABC (1 phase-2 wire) cable in LT pole and buffalo was passed near pole and got electrocuted. | Awaited | NA | NA | Replacement of insulator with stringing of LT Line to avoid accident. | Baroda O&M
74 | BUFFALO OF OWNER SHRI BARIA GULABSINH BHOPATSINH,NISHAL FALIYA,Vill-SURBAR,Ta-Halol,Dist-Panchmahal |  |  | 2023-07-16 | FA | [5 empty] | WHILE ITICHING AT DISTRIBUTION BOX TC WHILE POWER ON POSITION ACCIDENTLY CAME CONTACT TO LIVE PART | Awaited | NA | NA | Distribution box in New kit kat fuse provided, GI EARHING done by insulation pipe. | Godhra
75 | Murtujakhan Sikandarkhan Pathan,Saiyad Farm, Vill-Vansar,Ta-Matar,Dist-Kheda |  |  | 2023-07-16 | FHO-Pvt | [5 empty] | Victim came in contact which iron fensing of said garden. which was carring the current due leakage in fancy lights installed on fensing. | Awaited | NA | NA | The Connection Was Disconnected And Consumer Was Served Notice To Provide New Test Report Along With Proper ELCB/RCCB Installation. | Nadiad
76 | AJITKUMAR RAYJIBHAI PARMAR,Vill-JITPURA(SARNEJ),Ta- Waghodia,Dist- vadodara |  |  | 2023-07-17 | FA | [5 empty] | AS PER PRIMARY INVESTIGATION REPORT,IT IS FOUND THAT WHEN BUFFALO WAS PASSING FROM CANAL ROAD TO FARM ,ITS TAIL TOUCHED THE EARTHING WIRE OF TC WHERE LEAKAGE CURRENT PASSED SO BUFFALO GOT ELECTROCUTED | Awaited | NA | NA | Maintanance done- Transformer erthing reactivated | Godhra
77 | CHUNARA ASHOKBHAI MANGALBHAI,Vill-moxi padhro,Ta-Savli,Dist-Vadodara |  |  | 2023-07-17 | FA | [5 empty] | The 11 KV line situated at clay mountain hilly area and tapping of 11 kv line span sag is lying between mountain height and at ground level of area. So, the incident occured beacuse of less ground clearance of 11 kv HT line due to uneven ground level and heavy sag of conductor between two poles. At that time buffalo was eating grass at hilly mountain area under line and got electrocuted | Awaited | NA | NA | New pole erected for maintaining ground clearance | Baroda O&M
78 | Pagi Vajabhai Girdharbhai'S buffalo,Pruthvisinh Deepsinh Solanki‘s Farm OPP bapu faliyu,Vill-CHAPARI MUVADA,Ta-Lunawada,Dist-Mahisagar |  |  | 2023-07-18 | FA | [5 empty] | On That Location 11 KV Degamda Agdom Feeder And it’s 3P4W ABC Cable Cross Each Other And That Location 8meter Psc Pole Carrie At Top Guarding & Below Lt Line Of 11 KV Degamda Agdom Feeder 3P4W ABC Cable. That Both Line Passed through Pruthvisinh Deepsinh Solanki‘S Farm .Due To Corrosion Of Guarding Wire Was Broken At That Location So LT of 3P4W ABC Touch With Guarding Wire. Due To Insulation Of ABC Cable Damaged And Punctured Then This Power Passed Through Guarding Wire. Unfortunately This Ti | Awaited | NA | NA | NEW LT ABC PROVIDED | Godhra
79 | Bharvad Ramabhai Devabhai,Vill-Poicha,Ta-Savli,Dist-Vadodara |  |  | 2023-07-18 | FA | [5 empty] | On dtd: 18-07-2023 at 17:30hrs visited site and prepared panchnama. Information received from local resident Shri Ashokbhai R Bhoi. The incident happened on LT ABC(1ph2w) cable which came out of from LT insulator and got stuck on D clamp of pole,leakage current was passing from the GI earth wire in to ground. At that time claves were passing near by pole and it touched the earth wire and got electrocuted. | Awaited | NA | NA | Replacement of insulator with stringing of LT Line to avoid accident. | Baroda O&M
80 | COW,Chapariya,Vill-Nadisar,Ta-Godhra,Dist-Panchmahal |  |  | 2023-07-19 | FA | [5 empty] | owner of cow Name-Bharwad babubhai popatbhai, - Due to LT pole broken of Nadisar AG Feeder (before 3days), LT open wire line snapped and jumper of LT line was cut. At that location crossing of LT and HT line is there. The cow was touch to snap LT line at that time at crossing birds were flew from line and HT line touch to LT line. Due to induction power came and got electrocuted and cow died at the spot. | Awaited | NA | NA | LT ABC provided in crossing & Necessary Line Maintance done. | Godhra
81 | DITABHAI LUNJABHAI GARASIYA,TIMARAN FALIYA,Vill-SAGADAPADA,Tal-FATEPURA, Dist-Dahod |  |  | 2023-07-21 | FHO | [5 empty] | AS PER PRIMARY INFORMATION VICTIM WAS WORKING IN HIS FARM AT TIMARAN FALIYA VILL SAGADAPADA TA FATEPURA,AS PER EYE WITENESS STATEMENT VICTIM ACCIDENTALY COME IN CONTACT WITH STAY WIRE OF PSC POLE OBJECT NEARBY AND GET THE ELECTRICAL SHOCK AND VICTIM DIED WHILE APPROCHING TO THE HOSPITAL. | Awaited | NA | NA | THE LOCATION IS RECTIIFED AND STRINGING AND BINDING OF UNCHARGED WIRE IS CARRIED OUT. | Godhra
82 | COW,NR. ADA TALAVDI,Vill-CHHANI,Ta-Vadodara,Dist-Vadodara |  |  | 2023-07-22 | FA | [5 empty] | WHILE PASSING VERY NEAR TO TRANS CENTRE, DUE TO LAND FILLED WITH WATER THERE MIGHT BE MINOR LEAKAGE IN NEUTRAL OF TC GOT ELECTROCUTED AND GOT DEATH BECAUSE OF STEP POTENTIAL | Awaited | NA | NA | Rectification of transformer center is done and new earthing provided. | Baroda O&M
83 | BUFFALO,PATELIYA FALIYU,Vill-NANA DOKVA,Ta-Lunavada,Dist-Mahisagar |  |  | 2023-07-23 | FA | [5 empty] | A Fatal Animal Accident Occurred to Buffalo on Dtd:23.07.2023, At approximetaly 12:15hrs. Telephonic message received on sub division complain centre number that a Buffalo of Shri. Pateliya Bhemabhai Motibhai got electrical shock and died. on the spot feeder made off from sub station and after site visited by line staff and cut off power supply after feeder made on from sub station and on the same day on dtd 23.07.2023 at 14:00 in afternoon site visit by officer and employees and found Buffalo w | Awaited | NA | NA | Tree cutting work done and Repair of Cable | Godhra
84 | BULLOCK OF SHRI MOHANIA NAGRUBHAI SAVJIBHAI,SAJOI KALAM FALIA,Vill-SAJOI, Tal-Dhanpur, Dist-Dahod |  |  | 2023-07-23 | FA | [5 empty] | THE BULLOCK WAS PASSING NEAR TC STRUCTURE OF SAJOI KALAM FALIA WW TC WHEN IT MIGHT HAVE COME IN CONTACT WITH GI WIRE CARRYING LEAKAGE CURRENT AND GOT ELECTROCUTED | Awaited | NA | NA | THE LOCATION IS RECTIFIED AND NEW EARTHING DONE,PVC PIPE IS ADDED IN EARTHING | Godhra
85 | COW,BARIYA FALIYU,Vill-ABRAM PATEL NA MUVADA,Ta-Godhra,Dist-Panchmahal |  |  | 2023-07-23 | FA | [5 empty] | Due to heavy wind and Rain ,leakage of current might be got flow in Transformer neutral wire and passed through Earthing,The Cow while garzing the grass was came in contact to earthing wire and might be got electrocuted and spot died at site. | Awaited | NA | NA | TC Earthing Insulated Pipe protction done & Necessary Line Maintance done. | Godhra
86 | PARMAR SAVITABEN FATESINH,behind prathmik school,Vill-Panchmahudi,Ta-Halol,Dist-Panchmahal |  |  | 2023-07-24 | FA | [5 empty] | AS PER PRIMARY INVESTIGATION REPORT IT IS FOUND THAT WHEN BUFFALO WAS GRAZING IT REACH TO THE TRANSFORMER CENTER .IT TOUCH THE GI WIRE OF TC WHEREE LEAKAGE CURRENT FLOWS SO BUFFALO GOT ELECTROCUTED | Awaited | NA | NA | Maintanance done- Transformer erthing reactivated | Godhra
87 | KISHMAT VIKRAMBHAI VAGHARI,SAVA TALAVADI,Vill-ODE,Ta-Anand,Dist-Anand |  |  | 2023-07-25 | FHO | [5 empty] | on the LT pole (Geo Loc - 1) where accident took place, ABC 1ph2w is passing through it. In such rainy and heavy wind atmosphere, due to fall of Neem tree branches and rubbing its insulation it may possible that the binding may get loosen and LT ABC 1ph2w line directly came in the contact of U Clamp of the same pole. In results, leakage current may passed continuously through GI wire. Meanwhile, the boy passing through the narrow pathway, tried to took the help of a pole to get back down to the | Awaited | NA | NA | MAINTAINACE OF LINE 2W ABC 200 MTR REPLACE REMAING LT POLE EARTHING PIPE PROVIDED POLE EARTHING NEW DONE TREE CUTTING DONE | Anand
88 | NA,Naswadi Aakona road, infront of kabir city,Vill/Tal-Naswadi, Dist-Chhotaudepur |  |  | 2023-07-25 | FA | [5 empty] | As per site visit and statement of eye witness. It is found that group of buffalo was grassing around the transformer center of Kalediya ag Feeder and suddenly two buffalo fight with each other and run towards transformer center. At that time one leg of he buffalo is stuck with guy wore and guy wire is broken. Broken guy wire is touched and contacted with 11KV bushingjumper of transformer and he buffalo got electrocuted and died at same time. | Awaited | NA | NA | New stay provided and conductor restringing. | Baroda O&M
89 | Buffelow of Jitendrabhai Ramabhai Dabhi,Padarda Sim vistar,Vill-Bilodra, Tal-Nadiad, Dist-KHEDA |  |  | 2023-07-27 | FA | [5 empty] | Buffelow of Jitendrabhai R Dabhi Reach at near line Pole where ABC wire Insulation damage due to friction with tree this wire touch with uclamp and uclamp connected with earth wire so, buffelow get contact with earth wire and get electrocuted and died. | Distribution company should maintain electric installtion by regular interval | NA | YES | AB Cable replaced | Nadiad
90 | MALE BUFFALO,BEHIND GAURI CINEMA,Vill/Ta-Godhra,Dist-Panchmahal |  |  | 2023-07-27 | FA | [5 empty] | The Male Buffalo was grazing the grass Behind gauri cinema area & suddenly the broken LT conductor which is already laid on ground got stucked to leg of male buffalo so he madly run.Hence, due to broken conductor hanging from LT pole got stretched and due to this the live 2 WLT AB Cable of Omkar feeder also broken and falls on ground and the male buffalo might experienced the electric shock and found dead | Awaited | NA | NA | LT Line Conductor Replaced & necessary maintance carried out. | Godhra
91 | JAYDIPSINH MANUSINH RAJ,HARSIDHI AGRI TECH RAMNAGAR BRIDGE,Vill-Vadod,Ta-Anand,Dist-Anand |  |  | 2023-07-30 | NFHO | [5 empty] | ON DATE 30.7.23 AT 16 HR LABUR OF HARSIDHI AGRI TECH LOCATED AT:RUPAREL,VILL:VADOD TA&DI:ANAND DOING UNLODING OF NURSARY PLANT FROM TRUCK HE CLIMB ON REALING OF TRUCH WHEN HRE MOVE UP SIDE ON TRUCK REALING COMES IN CONTACT OF LIVE 11 KV RAMNAGAR AGRI FDR OF 66 KV MOGAR SS OF VASAD SDN HE GOT ELECTROCUTED ,HE UNDER TREATMENT AT HOSPITAL | due to party's mistake line was already at 15.3ft height | NA | NA | no action needed | Anand
92 | Buffalo of Chandubhai Somabhai Chauhan, Vill-Vinzol, Tal-Godhra, Dist-PMS |  |  | 2023-07-29 | FA | [5 empty] | A tree fallen on Open LT linedue to which conductor snapped and fall on Buffalo and it got electrocuted | Awaited | NA | NA | Tree cutting & necessary Maintance Done. | Godhra
93 | BUFFALO OWNER BALVANTBHAI DALPATBHAI BARIA, GUVARIYA FALIYU, Vill-Aniyad, Tal-Shahera, Dist-PMS |  |  | 2023-08-02 | FA | [5 empty] | The Buffalo Was Tied Beside 16 KVA DP Structure Of 11 KV Nathujina Muvada Feeder Along With Other Animals Of Balvantbhai Dalpatbhai.Complain Received At Fault Center Regarding Above Incident. While Visiting Site No Any Current Mark Was Seen On Buffalo. After Visual Inspection Power Restored, By Checking With Tester No Any Leakage Current Was Found On Earthing Or Guy Wire Of Said TCDP.It Reveals That There Were No Leakage Current Found At Victimized Site.So, There Were No Chance Of Death Of Buffalo Due To Leakage Current | Awaited | NA | NA | EARTHING PIPE PROVIDED & Necessary Line Maintance done. | Godhra
94 | BUFFALO of Bhikhabhai Bhailal Vasava, KURALI BUSTAND PASE, Vill-Kurali, Tal-Karjan, Dist-Vadodara |  |  | 2023-08-02 | FA | [5 empty] | FROM THE OBSERVATION AT SITE,BUFFALO TOUCH WITH NEAR BY LT POLES EARTHING WIRE AND GET ELECTROCUTED AND DIED ON THE SPOT.THERE IS 4W AMC LT LINE ON THAT POLEBUT DUE TO WIND AND TREE BRANCH FRICTION WITH AB CABLE,INSULATION OF AB CABLE DAMAGED AND PHASE WIRE TOUCHING WITH U CLAMP NAD THROUGH U CLAMP EARTHING WIRE WAS BECOME LIVE. | Awaited | NA | NA | New earthing provided, and Tree branch CUTTING | Baroda O&M
95 | Mrs. VAGHELA FULIBEN BALDEVBHAI, TANKIVALU FALIYU, Vill-Kuna, Tal-Mahemdabad, Dist-Kheda |  |  | 2023-08-03 | FHO | [5 empty] | 3PH 4WIRE LT LINE OF 11KV JINJAR JGY FDR PASSING FROM TANKIVALU FALYU AT VILL KUNA IN EVENING TIME MONKEY JUMP FROM LT ABC CABLE TO METAL SHED. DUE TO THIS LT LINE FALL ON GI WIRE AND POWERFLOW FROM LT AB CABLE TO METAL SHED.MILK ZAR HANGING ON METAL SHED BY METAL HOOK. Mrs. VAGHELA FULIBEN BALDEVBHAI CAME IN CONTACT WITH METAL JAR AND GOT ELECTROCUTED AND DIED ON SAME PLACE. | Awaited | NA | NA | LT LINE MAINTENANCE DONE WITH IDEAL SERVICE JOIN AND GI WIRE TIED WITH CLEAR DISTANCE MAINTAIN FROM LIVE PART EVEN IF THE MONKEY JUMPS. | Nadiad
96 | BUFFALO OF SHRI LAXMANBHAI BHEMABHAI TALAR, talar fadiyu, Vill-Dholi, Tal-Virpur, Dist-Mahisagar |  |  | 2023-08-05 | FA | [5 empty] | tree branches fallen on open conductor line at that time conductor broken and fall down on the buffalo, got electrocuted and mat with fatal electrical accident | Awaited | NA | NA | LT Conducter Jointed and Necessary maintenance carried out | Godhra
97 | Bullock of Shree Narasiyabhai Rembhai Bhil, GIHARIYA FALIYA, Vill-Kutbi, Tal-Kawant, Dist-Chhotaudepur |  |  | 2023-08-05 | FA | [5 empty] | AS PER PRIMARY INVESTIGATION INFORMATION RECIEVED FROM SARAPANCH SHREE KOTBI 11 KV CONDUCTOR HAD BROCKEN AT DODP AND FALLEN ON GROUND AND BULLOCK CAME IN CONTECT WITH LIVE CONDUCTOR AND GOT ELECTROCUTED. | Awaited | NA | NA | Do-fuse rejumpering work done | Baroda O&M
98 | She Buffalow, Koliboriyad, Towards rajpura gam, Vill-KiliBoriyad, Tal-Naswadi, Dist-Chhotaudepur |  |  | 2023-08-11 | FA | [5 empty] | During Passing through LT line of 1Ph. 2wire, Because of Sparking in conductor of LT line and break one wire and fallen on passing she buffalo at that time. She buffalo died at same time due to conductor snapped. | Awaited | NA | NA | Conductor rejointed | Baroda O&M
99 | Buffallow of Shri Parthavbhai Dhulabhai Gohel, opp Panchayat office New Koshiyal, Tal-Matar, Dist-Kheda |  |  | 2023-08-12 | FA | [5 empty] | Buffallow of Parthavbhai Dhulabhai Patel Grassing and Suddenly Fall Down on The earth Near TC due to Leackage Current In the earthing wire and died due to Electric shock | Awaited | NA | NA | Transformer Maintenace Carried Out And New Earthing Provided | Nadiad
100 | BUFFELO, NEAR BHUDHABHAI KHODHABHAI PARMAR KUVA, Vill-Kinkhlod, Tal-Borsad, Dist-Anand |  |  | 2023-08-14 | FA | [5 empty] | NEAR DP STRUCTURE BUFFALO GONE TO DRINK WATER EARTHING WIRE TOUCH WITH BODY LEFT SIDE AND VICTIN GOT ELECTROCUTED. | 11 kv line conductor touched with earthing wire due to loose span |  |  | new earthing done and line stringing done as per regulation | Anand
101 | DODIYAR PARVAT MASHRU, Vill-bamroli, Tal-Shahera, Dist-PMS |  |  | 2023-08-19 | FHO-Pvt | [5 empty] | AS PER STATEMENT OF EYE WITNESS,VICTIM WAS BATHING IN HIS HOUSE WHEN HE HEARD SOUND OF PEOPLE SHOUTING PIGS HAVE CAME IN NEARBY FARM .HE RAN TO SHOO AWAY THE PIGS AND WHILE DOING SO HE COME CONTACT WITH FENCING OF BARIA RAMESHBHAI SHANABHAI WHO HAD GIVEN ILLEGAL POWER SUPPLY TO THE FENCING.DUE TO THIS CONTACT OF FENCING VICTIM GOT ELECTROCUTED AND DIED ON SPOT | Awaited | NA | NA | Police compaint done to avoid such activity. | Godhra
102 | BUFFALO of Gopalbhai Nathubhai Bharwad, opp vishvakarma engg. company,kailashpati chokdi,vitthal udyognagar, Tal/Distt-Anand |  |  | 2023-08-21 | FA | [5 empty] | THERE IS 1 TRANSFORMER CENTER(CMP/TC/003) FEED POWER TO 3 NOS OF CONSUMERS, 1 CONN. NAME SHRI VISHVAKARMA ENGG COM. 01201505887 CHECKED AND FOUND ONE FAULTY 3 PH MOTOR AND DUE TO THAT WHEN MOTOR STARTS THERE IS NEUTRAL RETURN BACK AT TC CENTER EARTHING FUNEL. DUE TO THIS POSSIBLE REASON BUFFALO GOT ELECTROCUTED AND DIED AT SITE. | Awaited | Awaited | NA | Notice issued to vishvakarma to replace faulty motor. New TR submitted on 25.8.23. Insulation pipe provided on earthing. | Anand
103 | Cow, Rohil Pandad, Tal-Khambhat, Dist-Anand |  |  | 2023-08-21 | FA | [5 empty] | As per Primary Investigation report, it is found that when cow was grazing it reached to the transformer center and came to contact with GI Earthing wire of TC where leakage current may be flow at that time so cow got electrocuted. | Awaited | NA | NA | reactivation of earthing of transformer | Anand
104 | BARIYA TAKHATSINH CHAKABHAI, Vill-GOTHADA, Tal-Godhra, Dist-PMS |  |  | 2023-08-23 | FHO-Pvt | [5 empty] | VICTIM TRY TO INSTALL BULB IN HOLDER ON BOARD AND ACCIDENTALLY CAME INTO CONTACT TO OPEN COVER MCB GOT ELECTROCUTED | Awaited | NA | NA | Advice to installed ELCB | Godhra
105 | BHARATSIGH DHIRUBHAI RATHVA, C J BARIYA FARM, Vill-Rajnagar, Tal-Bodeli, Dist-Chhotaudepur |  |  | 2023-08-24 | FHD | [5 empty] | Attending ag complaint of C J Bariya he checked voltage at consumer end with DO road provided with test lamp through flexible wire but due to non avelibility of voltage at consumer end,while going towards TC with open do rod on his shoulder one end of flexible wirewas on top of DO and another inhis hand came in contect with HT Overhead line of 11 kv vadeli ag feeder and got eletrocuted | Awaited | NA | NA | one pole ercetion on long span and conductors stringing | Baroda O&M
106 | BUFFALO OF VIJAY R. PAWA, PATANVADIYA FALIYA,VADHVANA, Tal-Dabhoi, Dist-Vadodara |  |  | 2023-08-25 | FA | [5 empty] | Due to Monkey jumped on ext. LT line near House of shri vijaybhai ramchandrabhai Pawa LT line was broken and snapped on buffalo of shri vijaybhai ramchandrabhai Pawa .this broken neutral Conductor came in Contact with buffalo & buffalo got Electric shock & became Electrocuted. | Awaited | NA | NA | SINGLE CORE AB CABLE PROVIDED | Baroda O&M
107 | RATHAVA VINUBHAI KARSHANBHAI, KHEDA VILLAGE ROAD FALIYU, Vill-Kheda, Tal-Jetpur Pavi, Dist-C'udepur |  |  | 2023-09-01 | NFHD | [5 empty] | The victim was doing replacement of HT jumpers on 11 KV vasantgadh AG feeder.LCP was taken by victim Vinubhai Karchanbbai Rathava from 66 KV Vadoth ss of 11 KV vasantgadh AG feeder & parallel passing 11 KV Jamba JGY feeder. During jumper replacement, one jumper was replaced & another jumper replacement work, suddenly current was coming and got electrocuted. The victim Rathava Vinubhai karchanbhai was fallen down and injured (burn)in both hand. He is admitted to Bodeli hospital for further treatm | Awaited | NA | NA | Crossing remove by stringing of HT conductor at 03 no`s location | Baroda O&M
108 | Shri Devabhai V Dindor, Vill-Sarsa, Tal/Dist-Anand |  |  | 2023-09-06 | NFHD | [5 empty] | Victim was got complain of Chandubhai R Patel was not getting one phase so victim gone for attending above complain then he removed TC DO fuse and lt side bushing lugs checked during that suddenly insects bite on left hand of victim and hand touched with upperside of do fuse and victim got electrocuted | Awaited | NA | NA | DISCUSS THE POINT IN SEAFTY MEETING | Anand
109 | COW-Karanbhai Ramanbhai Bharvad, BHATHIJI NAGAR NEAR CHANDRAMOLESHWAR, Vadodara |  |  | 2023-09-06 | FA | [5 empty] | Cow passed neat LT Round pole and steel pole had leakage current due to LT jumper touched with pole so cow came in contact with steel pole resulting in fatal acciedent | Awaited | NA | NA | immediately supply cut off and rectified the jumper | Baroda City
110 | COW- Vill-Nava Rozva, Tal-Galteshwar, Dist-Kheda |  |  | 2023-09-07 | FA | [5 empty] | On Dated 7/9/23, Telephonic Message Received Approx At 19:30 Hrs On Fault Center Regarding Electrocute Of Cow Near Village TC Of Nava Rozva. At That Time Rainfall Is Continued. During Site Visit There Was No Any Leakage Current Found At Stay Wire, Earthing Wires, Distribution Box And Poles. Earthing GI Wire Is Covered With PVC Rigid Pipe. Cow May Electrocuted Due To Induction Field Created Due To Rain And Wet Land. | Awaited | NA | NA | AT THE TIME OF INVESTIGATION NO CAUSE FOUND BUT TRANCSFORMAR EARTHING RECATIVATED | Nadiad
111 | Cow - SATABHAI RAMJIBHAI BHARWAD, RAM TALAVDI, Vill-Chikhlod, Tal-Kapadwanj, Dist-Kheda |  |  | 2023-09-08 | FA | [5 empty] | ON DATED 08.09.2023 AROUND 11:00 AM AT CHIKHLOD VILLAGE AREA 11KV RAMDEVPIR AGDOM FEEDER's TRANSFORMER (25 KVA KANTIBHAI DAHYABHAI PATEL VALU TC ) LT LINE CONDUCTOR WAS SNAPPED ACCIDENTALLY DUE TO TREE BRANCHES FALLING ON LIVE LT LINE (TREE BRANCHES FALLEN DUE TO HEAVY WIND AND RAIN) AT THAT TIME COW OF SHRI GORABHAI RAMJIBHAI BHARWAD WAS GRAZING AND PASSING BETWEEN THIS CONDUCTOR SNAPPED LOCATION AND ACCIDENTALLY SHE GOT CONTACT WITH LIVE CONDUCTOR OF LT LINE AND GOT ELECTROCUTED AND DIED ON SP | Awaited | NA | NA | Transformer Maintenace Carried Out And New Earthing Provided | Nadiad
112 | Buffalo-Yogeshbhai Manubhai Parmar, Joshi Vistar, Mahudiyapura, Vill-Bar Bamroli, Tal-Petlad, Dist-Anand |  |  | 2023-09-08 | FA | [5 empty] | Due to snapping of LT line conductor, Buffalo of Yogeshbhai came in contact with live wire and died. | Awaited | NA | NA | lt LINE RESTRINGING WORK CARRIED OUT .Maintenance carried out | Nadiad
113 | MOHAMMAD RAFIK ABDUL RAUF SHAIKH (GOAT), NR POLICE STATION, Vill/Tal-Shahera, Dist-PMS |  |  | 2023-09-09 | FA | [5 empty] | NEAR THE PSC LT POLE WHERE THE GOAT WAS LYING DEAD HAD CCTV CAMERA WIRES TIED WITH CENTERING WIRE ALONG WITH 3PH4WLT ABC AND 2 FOOT ANGLE. NO LEAKAGE CURRENT WAS OBSERVED DURING THE VISIT.ALSO HEAVY RAINFALL WAS THERE IN SHAHERA TOWN AT THE TIME OF ACCIDENT THERE MIGHT BE POSSIBILTY OF LEAKAGE CURRENT AND GOAT MIGHT HAVE COME IN CONTACT WITH GI WIRE DURING THIS TIME AND MIGHT GOT ELECTROCUTED .PM REPORT AWAITED. | Awaited | NA | NA | Pole Service bunch Maintance Done. | Godhra
114 | T B BARIA, Vill-chipat (navi nagari), Tal-Waghodia, Dist-Vadodara |  |  | 2023-09-09 | NFHD | [5 empty] | The information received at offie complain center by consumer regarding electric shock to shri T>B>Baria at vill-chipat (navi nagari) while attending the complaint of consumer shri Sardarbhai saburbhai parmar (Consumer no-02959/02154/1) on primary investigation it was found that while climbing tha PSC pole for attending complain shri T.B.Baria got in touch with live wire used for private street light purpose hanging on pole and fallen down from pole. | Awaited | NA | NA | Illegal wiring is removed and maintenance of line. | Baroda O&M
115 | THAKOR KISHORSINH CHHATRASINH (COW ), Vill-khant na muvada, Tal-Shahera, Dist-PMS |  |  | 2023-09-10 | FA | [5 empty] | THE COW WAS RETURNING AFTER GRAZING IN THE FIELD AND SUDDENLY HT CONDUCTOR OF 11 KV SAKARIYA AG FEEDER SNAPPED AND FELL ON THE COW BELOW. DUE TO THIS COW GET ELECTROCUTED AND DIED ON THE SPOT | Awaited | NA | NA | 11KV HT Line Maintanace Done. | Godhra
116 | GANPATBHAI SOMABHAI CHAUHAN, OPP AMSARAN PETROL PUMP, Vill-Amarson, Tal-Mahemdabad, Dist-Kheda |  |  | 2023-09-13 | FHO | [5 empty] | A HIGHTECH TURBO SAND LOADED TRUCK WAS PARKED BELOW THE 11 KV GHODALI AG FEEDER BY TRUCK DRIVER OPP. AMSARAN PETROL PUMP. AS CONSTRUCTION WORK IS RUNNING OF GANPATBHAI'S HOUSE AT HIS FARM. VICTIM SHRI. G S CHAUHAN WAS CLIMBS ON TRUCK TO CHECK THE SAND. ALSO THE TRUCK PARKED PLACE AREA TOO DARK & UNKOWNLY WITHOUT SEE UPER SIDE LIVE HT ELECTRIC LINE. HE WAS CAME IN TOUCH WITH UPPER SIDE 11 KV GHODALI AG FEEDER THEREFORE ELECTROCUTED & DIED AT SAME PLACE AMSARAN OPP. PETROL PUMP. | Awaited | NA | NA | AS INFORMATION RECIEVED AND IMMEDIATELY LINE CLEAR TAKEN ON SAME TIME OF 11 KV GHODALI AG FDR AND AFTER JOINTING BROKEN CONDUCTOR POWER RESTORED OF 11 KV GHODALI AG FDR | Nadiad
117 | Rajeshbhai Ambubhai Rathwa, Farm of Rathwa Rajeshbhai Ambubhai, Koliboriyad, Naswadi |  |  | 2023-09-14 | FHO | [5 empty] | Guy Wire of pole near Rajeshbhai Ambubhai rathwa is not its proper place. May be its remove by them for that the line clearance of Span is lower but its not as much as accident occurred. The line span is around 10 ft. due to Guy wire is removed by the victim or any other person line span is get low with the ground clearance may be. | Awaited | NA | NA | New stay provided and conductor restringing. | Baroda O&M
118 | Bullock-Rameshbhai Kanabhai Parghi, Nagji Muvada, Vill-Bhamri, Tal-Santrampur, Dist-Mahisagar |  |  | 2023-09-15 | FA | [5 empty] | A Fatal Accident of Bullock was reported by Shri Rameshbhai Kanabhai Pargi through in-person application on 16.09.2023 at 09.30 AM. As per Site Panchnama, at the time of incident due to heavy wind and rain, the Pin Insulator on the nearby Pole of 11 KV Ukhreli-JGY Feeder got fired and due to this the conductor fell on the V-Cross Arm (with the fired remains of Pin Insulator was found nearby Pole). In addition to this, the sign of Pole Firing was also found in the direction of the house. Due to | Awaited | NA | NA | 11kv Pin Insulater Replace and Necessary maintenance work carried out | Godhra
119 | Mukesh, Kacharapeti tc, Bavamanpura, Vadodara |  |  | 2023-09-15 | NFHO | [5 empty] | Drunk man climbed on live TC Sructure | Awaited | NA | NA | Danger Board applied on TCDP & FIR Lodged against the Victim | Baroda City
120 | Ku. Ramilaben Navalsinh Bariya, NEAR GNYAN JYOT KUMAR CHHATRALAY, Vill-Gundi, Tal-Ghoghamba, Dist-PMS |  |  | 2023-09-16 | FHO | [5 empty] | a fatal Human and Animal accident occurred to. Ku.Ramilaben Navalsinh Bariya and her two no’s of Goat. in the farm of Heerabhai Punabhai Rathwa at Gundi Village.Ta.Ghoghamba, Dist.Panchamahal, due to Heavy wind pressure and rain Tree fallen on LT Line & due to that conductor of LT Line was snapped and fallen on the land & they came in contact with live LT Line and met with an eletal accidentctrical fa | Awaited | NA | NA | Tree cutting work done and restringing Of conductor done. | Godhra
121 | 2 NOS GOAT, NEAR GNYAN JYOT KUMAR CHHATRALAY, Vill-Gundi, Tal-Ghoghamba, Dist-PMS |  |  | 2023-09-16 | FA | [5 empty] | a fatal Human and Animal accident occurred to. Ku.Ramilaben Navalsinh Bariya and her two no’s of Goat. in the farm of Heerabhai Punabhai Rathwa at Gundi Village.Ta.Ghoghamba, Dist.Panchamahal, due to Heavy wind pressure and rain Tree fallen on LT Line & due to that conductor of LT Line was snapped and fallen on the land & they came in contact with live LT Line and met with an eletal accidentctrical fa | Awaited | NA | NA | Tree cutting work done and restringing Of conductor done. | Godhra
122 | Cows Of Mayurbhai Amrabhai Bharvad, Near Ganpati Chokadi, Near Railway fatak, Vill-Nava Bilodra, Tal-Nadiad, Dist-Kheda |  |  | 2023-09-17 | FA | [5 empty] | Due to Under Ground LT Line Fault At Santram Vatika Society Current Came Back In Nutural Of TC And by Nutral earth wire current ground at that time 3 nos of cow of Mayurbhai Amrabhai Bharvad Passing Near TC And due to Rain Water Logging at that plece so by nutral earth wire cows get electrcuted and died on spot | Awaited | NA | NA | U/G Cable Fault Rectified by santram villa society | Nadiad
123 | NITESHBHAI RAMESHBHAI RAJPUT, sonatekari vistar, Manjalpur, Vadodara |  |  | 2023-09-17 | FHO | [5 empty] | ON DATE 17.09.2023 AT AROUND 11:30 PM,GANESHA RIDE TOOK PLACE IN SONATEKARI AREA ALONG WITH DJ SYSTEM INSTALLED IN THE TEMPO.THE TEMPO WITH HIGHTED DJ SYSTEM MAY COME IN CONTACT OF OPEN LT LINE.THE STREET LIGHT WIRE BELOW AND OPEN LT LINE WIRE FELL DOWN ALONG WITH THE CEMENT POLE AND THE VICTIM WAS PROBABLY ELCTROCUTED TOUCHING WITH WIRE.NO COMPLAINT RECEIVED OF ELCTROCUTED,ONLY POLE BROKEN COMPLAINT RECIEVED ON THAT DAY | Awaited | NA | NA | Damange pole replaced by new one. LT open conductor line replaced by PVC Cable. | Baroda City
124 | SANGADA KAILASHBHAI ADIYABHAI'S COW, CHHAPRI SBI BANK, Vill-Chhapri, Tal/Dist-Dahod |  |  | 2023-09-17 | FA | [5 empty] | 11kv Jamnadasjgy fdr transformer center, the cow was wondering near transformer center. Transformer center and land was wet due to heavyrain, the cow may came in contact with transformer psc pole and electroduced.No leakage current found near transformer center. | Awaited | NA | NA | MAINTENANCE OF TRANSFORMER DONE, NEW EARTHING DONE,PVC PIPE IS ADDED IN EARTHING | Godhra
125 | Buffalo Of Shri Maheshbhai Vaghabhai, Near Mahesh Vagha Home, Vill-Dantla, Tal-Virpur, Dist-Mahisagar |  |  | 2023-09-17 | FA | [5 empty] | N THE DAY OF INCIDENT DUE TO HEAVY RAIN AND WIND 2 NOS OF PSC POLE FELL DOWN DUE TO SOIL EROSION, DUE TO WHICH 2 WIRE OPEN LT LINE FELL ON BUFFELO WHICH IS TIED NEAR LINE. AS THE BUFFELO OF SHRI MAHESHBHAI VAGHABHAI KHANT CAME INTO CONTACT WITH LIVE CONDUCTOR AND GOT ELECRICUTED AND MET WITH THE FATAL ELECTRICAL ACCIDENT. | Awaited | NA | NA | 2 nos of Pole erected and necessary stringing carried out | Godhra
126 | Buffalo-Surendrasinh girvatsinh chauhan, jantanagar soc tc, Vill-Jarod, Tal-Waghodia, Dist-Vadodara |  |  | 2023-09-18 | FA | [5 empty] | As per primary investigation report, it is found that when buffalo was grazing it reach to the transformer center, it touch the GI wire of TC where leakage current flows so buffalo got electrocuted. | Awaited | NA | NA | Maintanance done- Transformer erthing reactivated | Godhra
127 | BuffaloHimmatsinh Fulsinh Parmar, Amba Mata Faliya TC, Vill-Bhadroli(K), Tal-Kalol, Dist-PMS |  |  | 2023-09-18 | FA | [5 empty] | Leakage current started to flow from neutral wire of transformer center of Village. Bhadroli(K), Amba Mata Faliya due to broken of Service wire of WW connection, a cow grazing near the transformer might have came in contact with netral wire got electrocuted and met with fatal accident | Awaited | NA | NA | Servie wire replaced, transformer erthing reactivated - Maintanance done. | Godhra
128 | BARIA NARSINHBHAI SABURBHAI, Vill-JETPUR(DU), Tal-Limkheda, Dist-Dahod |  |  | 2023-09-19 | FHO | [5 empty] | ACCORDING TO PANCHNAMA ON DATED 19-09-2023 AROUND 03:00 PM VICTIM SHRI NARSINHBHAI SABURBHAI BARIA HOUSE HAD NO MGVCL METER AND WAS A NON CONSUMER AND WHILE TRYING TO CONNECT PRIVATE CABLE WITH NEARBY SINGLE PHASE TWO WIRE OPEN LT LINE DIRECTLY AND WHILE DOING SO GOT ELECTROCUTED | Awaited | NA | NA | THE VICTIM DIED BECAUSE WHILE TRYING TO CONNECT PRIVATE CABLE WITH NEARBY SINGLE PHASE TWO WIRE OPEN LT LINE DIRECTLY AND WHILE DOING SO GOT ELECTROCUTED | Godhra
129 | COW OF GOVINDBHAI RATABHAI RABARI, TC NO= KTL036, VACHCHLO BHAGH, Vill-Sarol, Tal-Borsad, Dist-Anand |  |  | 2023-09-19 | FA | [5 empty] | 4W LT ABC LT Line Of KTL036 VACHCHLO BHAG TC Founded Shorted, Due To That Leakage Current Start To Flowing In Transformer Neutral Earthing. When Cow Come In Contact With Neutral Earthing Of Transformer, Cow Died On Spot. | Awaited | NA | NA | damaged ab cable replaced with new 4 wire ab cable | Anand
130 | Buffalo-Arvindbhai Bhikhabhai Sindha, Pato Vistar, Vill-Kalamsar, Tal-Khmbhat, Dist-Anand |  |  | 2023-09-19 | FA | [5 empty] | Three buffelow were tied in a room of iron sheets, one of them died due to a sudden leakage currunt while rubbiung its head against an iron angle. on further investigation, the service wire coming in to the energy meter was jointed in the middle and the joint was touching the GI wire and the leakage current may appeared. it continued to rain throughout the event. | Awaited | NA | NA | dismental of gi wire & rectification done | Anand
131 | Buffalos of Karanbhai Sadurbhai Bharvad, Jorabandh Kalsar, Agarwa Gauchar Vistar, Vill-Agarva, Tal-Thasra, Dist-Kheda |  |  | 2023-09-24 | FA | [5 empty] | Due to heavy wind and rain a tree branch of subavad tree was broken and fallen on single phase two wire open LT line of Agarva AG and one conductor broken and laid down on land and during early morning two buffalo was passing nearby that place for drinking water and touched the conductor hence it was electrocuted and died. | Awaited | NA | NA | FALLEN TREE BRANCH CUT DOWN AND DAMAGED LT WIRE REPAIRED. | Nadiad
132 | Bariya Pragneshbhai Balvantbhai, karot faliya area, Vill-Salia, Tal-Devgadhbaria, Dist-Dahod |  |  | 2023-09-25 | FHO | [5 empty] | Victim was Removing and after his work had been completed jointing the LT line. During this unauthorised work sudden power switched on by unkhown person. So victim got electric shock and died on the spot | Awaited | NA | NA | POLICE FARIYAD IS DONE FOR ILLEGALLY ACCESSING OF OUR NETWORK. | Godhra
133 | 1)Amitbhai Gopalbhai thakor 2)Sandipbhai k thakor 3) Nirav rajeshbhaithakor 4 ) Darpan G Thakor, loc : paniyari urban /106-107, Khambhat, Dist-Anand |  |  | 2023-09-28 | FHO | [5 empty] | At above address, at the time of ganesh visarjan in paniyari area The Ladvada area ganpati murti was passing toward gulf of Cambay for ganpati visarjan, during this time the ganpati murti hight was observed to be approx .17.5 ft with trolley from ground ,was crossing the line of 11 kv paniyari urban feeder at loc paniyari /106 -107, at that time two victims who were fatal , were trying to lift up wire for passing the Murti of ganpati and they got electrocuted and died and other two person got el | Awaited | NA | NA | both side girder pole erected & line clearance increases as per standererd | Anand
134 | Rathwa Arjun Ambubhai, Nr. Wood Scape Villa, Bill, Vadodara |  |  | 2023-09-29 | FHO | [5 empty] | The electrical accident occurred despite the 11KV Chapad JGY power line being installed at the standard safety regulation height. However, the accident was a result of negligence on the part of the driver and the raised trolley. The Victim is fafailure to exercise caution and ensure the trolley did not contact the power line led to this unfortunate accident. The victim truck came into contact with the power line while emptying sand from the raised trolleyt. Althogh the power line height met safe | Awaited | NA | NA | due to negligance victim | Baroda O&M
135 | HORSE-Sikandar Sindhi, Tersa Road, Vill-Tersa, Tal-Sinor, Dist-Vadodara |  |  | 2023-09-29 | FA | [5 empty] | horse came in contact with broken LT wire of 11 kv Kukas ag feeder, electrocuted and died at spot | Awaited | NA | NA | one pole ercetion on long span and re-stringing of conductors. | Baroda O&M
136 | Chauhan Ashvinbhai Kanubhai, Near Hathnoli village dairy, Tal-Nadiad, Dist-Kheda | 2023-10-02 | FHO | On date 02.10.2023, new TC erection work was given to contractor near 100 KVA village TC. The victim climbed pole at loc-NAD/YGN/142 without any intimation to any contractor's worker. Suddenly the victim got electrocuted and fell on ground. Then some village local persons and contractors persons rushed to that place and went to hospital in private vehicle where the doctor declared him dead. | Awaited | NA | NA | Return leakage supply do not found but contractor is instructed to carry out the work with earthing on both side of pole. | Nadiad | 6 | On date 02.10.2023, new TC erection work was given to contractor near 100 KVA village TC. The victim climbed pole at loc-NAD/YGN/142 without any intimation to any contractor's worker. Suddenly the victim got electrocuted and fell on ground. Then some village local persons and contractors persons rushed to that place and went to hospital in private vehicle where the doctor declared him dead. | Awaited | NA | NA | Return leakage supply do not found but contractor is instructed to carry out the work with earthing on both side of pole. | Nadiad
137 | CHIMANBHAI GULABBHAI MAKWANA, NEAR FARM OF THAKOR RAJENDRASINH HIMMATSINH, Vill-Karsana, Tal-Godhra, Dist-PMS | 2023-10-06 | FHO-Pvt | THE ILLEGAL CURRENT MIGHT BE PASSING FROM TEMPORARY VAD OF RAJENDRA HIMMATSINH THAKOR FARM. DURING ANY TIME VICTIM MIGHT CAME IN CONTACT WITH LIVE WIRE AND GOT ELECTROCUTED | Awaited | NA | NA | Illegal wire removed, | Godhra | 8 | THE ILLEGAL CURRENT MIGHT BE PASSING FROM TEMPORARY VAD OF RAJENDRA HIMMATSINH THAKOR FARM. DURING ANY TIME VICTIM MIGHT CAME IN CONTACT WITH LIVE WIRE AND GOT ELECTROCUTED | Awaited | NA | NA | Illegal wire removed, | Godhra
138 | BIND RAMESHCHANDRA SHIVRATHI, VEGA CHOKADI, Tal-Dabhoi, Dist-Vadodara | 2023-10-06 | FHO | Around 11:10 Am At Vega Village (Vega Chokdi) Between Dabhoi Vadodara Highway Road There Was A Site New Site Named New Ramesh Motors In This Site Newly Metal Pipe Shade Fabrication Work Had Carried Out By Victim Ramesh Chandra Bind Under The HT Line Of 11 Kv Bhilapur JGY Line. Victim Was Climbed Upon Metal Pipe Shade For Some Welding Work At That Time Victim Metal Pipe Victim Lifted The Metal Pipe Which Touched The HT Line Of 11 Kv Bhilapur JGY Line Passing Above The Newly Metal Pipe Shade Victi | Awaited | NA | NA | due to negligance of victim | Baroda O&M | 6 | Around 11:10 Am At Vega Village (Vega Chokdi) Between Dabhoi Vadodara Highway Road There Was A Site New Site Named New Ramesh Motors In This Site Newly Metal Pipe Shade Fabrication Work Had Carried Out By Victim Ramesh Chandra Bind Under The HT Line Of 11 Kv Bhilapur JGY Line. Victim Was Climbed Upon Metal Pipe Shade For Some Welding Work At That Time Victim Metal Pipe Victim Lifted The Metal Pipe Which Touched The HT Line Of 11 Kv Bhilapur JGY Line Passing Above The Newly Metal Pipe Shade Victi | Awaited | NA | NA | due to negligance of victim | Baroda O&M
139 | PARMAR MAYURSINH HITENDRASINH, Vill-CHITLAV, Tal:-THASRA,Dist:-KHEDA | 2023-10-08 | NFHO | As per Site visit, The Victim was electrocuted when approx 3.5 meter iron rod used for plucking lemons was accidently coming into contact with live 11KV Bhadrasha AG line due to standing on Iron roof Shed. | Awaited | NA | NA | Notice issued for illegal construction THS/Tech/4889 dated 09.10.23 | Nadiad | 6 | As per Site visit, The Victim was electrocuted when approx 3.5 meter iron rod used for plucking lemons was accidently coming into contact with live 11KV Bhadrasha AG line due to standing on Iron roof Shed. | Awaited | NA | NA | Notice issued for illegal construction THS/Tech/4889 dated 09.10.23 | Nadiad
140 | Buffalo of solanki ajitsinh himatsinh, amatalav village tc, Tal-Waghodia, Dist-Vadodara | 2023-10-12 | FA | AS PER PRIMARY INVESTIGATION REPORT ,IT IS FOUND THAT WHEN BUFFALO WAS GRAZING IT REACH TO THE TRANSFORMER CENTER ,IT TOUCH THE GI WIRE OF TC WHERE LEAKAGE CURRENT FLOWS SO BUFFALO GOT ELECTROCUTED | Awaited | NA | NA | GI wire covered with GI PVC pipe | Godhra | 2 | AS PER PRIMARY INVESTIGATION REPORT ,IT IS FOUND THAT WHEN BUFFALO WAS GRAZING IT REACH TO THE TRANSFORMER CENTER ,IT TOUCH THE GI WIRE OF TC WHERE LEAKAGE CURRENT FLOWS SO BUFFALO GOT ELECTROCUTED | Awaited | NA | NA | GI wire covered with GI PVC pipe | Godhra
141 | DILIPBHAI MANUBHAI TADAVI, TOWN HALL, Vill/Tal/Dist-Vadodara | 2023-10-12 | FHO-Pvt | FATAL HUMAN ELECTRICAL ACCIDENT OCCURRED IN PRIVATE PREMISES OF TOWNHALL HT CON UNDER THE CONTROL OF VMC. AS PER THE SECURITY STAFF STATMENT AND BAPOD POLICE STATION LETTER IT IS CONCLUDED THAT VICTIM WAS CLIMBING ON IRON LADDER FOR THE WORK OF DISMANTLING OF TENT.DURING THE WORK ACCIDENTALY IRON PIPE OF TENT TOUCHED WITH LIVE 11KV WIRE OF LOAD SIDE HT CON AB DP AND VICTIM GOT AN ELECTRICAL SHOCK.IMMEDIATELY HE WAS ADMITTED TO JAMNABAI HOSPITAL WHERE HE WAS DECLARED DEAD. | Awaited | NA | NA | HT conn under VMC premices | Baroda City | 8 | FATAL HUMAN ELECTRICAL ACCIDENT OCCURRED IN PRIVATE PREMISES OF TOWNHALL HT CON UNDER THE CONTROL OF VMC. AS PER THE SECURITY STAFF STATMENT AND BAPOD POLICE STATION LETTER IT IS CONCLUDED THAT VICTIM WAS CLIMBING ON IRON LADDER FOR THE WORK OF DISMANTLING OF TENT.DURING THE WORK ACCIDENTALY IRON PIPE OF TENT TOUCHED WITH LIVE 11KV WIRE OF LOAD SIDE HT CON AB DP AND VICTIM GOT AN ELECTRICAL SHOCK.IMMEDIATELY HE WAS ADMITTED TO JAMNABAI HOSPITAL WHERE HE WAS DECLARED DEAD. | Awaited | NA | NA | HT conn under VMC premices | Baroda City
142 | Nareshbhai Pareshbhai Parmar, Green park society, Tandalja, Vill/Tal/Dist-Vadodara | 2023-10-12 | FHO-Pvt | Late Sh. Nareshbhai Rameshbhai Parmar was Works manual boaring work for airtel company. Victim was fainted and remain in pit when Akota sdn fault center line staff reached. fault center line staff had shut off power supply immediately from Transformer Distribution box. During that 108 ambulance reached and taken to the victim hospital where he was declared dead. Prima facie, The cause of the death is might be due to damage private LT UG service line of House no.14 or House no 03 of green park society. The detail investigation is under process which will be reported later on. It is pertinent to mention here that the said underground LT line was laid down by privately and the same was maintained by them privately | Awaited | NA | NA | LT UG Cable under Private Premises | Baroda City | 8 | Late Sh. Nareshbhai Rameshbhai Parmar was Works manual boaring work for airtel company. Victim was fainted and remain in pit when Akota sdn fault center line staff reached. fault center line staff had shut off power supply immediately from Transformer Distribution box. During that 108 ambulance reached and taken to the victim hospital where he was declared dead. Prima facie, The cause of the death is might be due to damage private LT UG service line of House no.14 or House no 03 of green park society. The detail investigation is under process which will be reported later on. It is pertinent to mention here that the said underground LT line was laid down by privately and the same was maintained by them privately | Awaited | NA | NA | LT UG Cable under Private Premises | Baroda City
143 | BAFALO (OWNER -Balvantbhai Maganbhai Solanki), nr.Solanki bhikhabhai nanabhai farm, Vill-Saliyav, Tal-Kalol, Dist-PMS | 2023-10-21 | FA | As the phone call recieved at office Complain centre.Our staff visited the site and observed observed LT ABC passing transformer centre to Pole top portion between DO DP and that location ABC cable insulation rubbing and touch DO DP angle and angle contact with earthing wire Bafelo was trying to rub her head with DP structure,got stuck in her horn and got electric shock and dead on spot. | Awaited | NA | NA | GI wire covered with GI PVC pipe | Godhra | 2 | As the phone call recieved at office Complain centre.Our staff visited the site and observed observed LT ABC passing transformer centre to Pole top portion between DO DP and that location ABC cable insulation rubbing and touch DO DP angle and angle contact with earthing wire Bafelo was trying to rub her head with DP structure,got stuck in her horn and got electric shock and dead on spot. | Awaited | NA | NA | GI wire covered with GI PVC pipe | Godhra
144 | Cow of Shri Bharvad Ranubhai Laxmanbhai, Bhalaniya Chokdi Village TC, Vill-Bhalaniya, Tal-Godhra, Dist-PMS | 2023-10-23 | FA | Leakage current may started to flow through neutral earthing of transformer center due to unbalance load and cow passing under the transformer center might have came in contact with the neutral earthing wire got electric shock and met with fatal accident | Awaited | NA | NA | NEW EARTHING WITH PVC PIPE PROVIDED AND LINE MAINTENANCE WORK DONE | Godhra | 2 | Leakage current may started to flow through neutral earthing of transformer center due to unbalance load and cow passing under the transformer center might have came in contact with the neutral earthing wire got electric shock and met with fatal accident | Awaited | NA | NA | NEW EARTHING WITH PVC PIPE PROVIDED AND LINE MAINTENANCE WORK DONE | Godhra
145 | Cow of Shri Laxmanbhai Lalabhai Taviyad, Vill-Motikyar, Tal-Santrampur, Dist-Mahisagar | 2023-09-19 | FA | As per Site Visit and Eye Witness Statement at the said location where the accident has happened has fired remains of Shackle Insulator to which Cow of Shri Laxmanbhai Lalabhai Taviyad has been tied. As per Eye Witness Statement Shackle Insulator has been blasted and fired and might caused the leakage current to flow through the wet land and causes the Cow to get Electrocuted. | Awaited | NA | NA | Pin Insulater replaced and neccessary maintenance carried out | Godhra | 2 | As per Site Visit and Eye Witness Statement at the said location where the accident has happened has fired remains of Shackle Insulator to which Cow of Shri Laxmanbhai Lalabhai Taviyad has been tied. As per Eye Witness Statement Shackle Insulator has been blasted and fired and might caused the leakage current to flow through the wet land and causes the Cow to get Electrocuted. | Awaited | NA | NA | Pin Insulater replaced and neccessary maintenance carried out | Godhra
146 | Safinmahammad Nurmahammad Malek,Kabrastan Road,Vill-Hathaj,Ta-Kheda,Dist-Kheda | 2023-11-03 | NFHD | To attain high voltage complain given from Nadiad Rural Sub Division Complain Center, he went to 100 kVA Hathaj village TC. He noticed that on TC DO, jumper on 11 kV side was sparking and was loose. So he decided to re-jumper it. So he called 66 kV Palaiya SS and asked the operator to handtrip 11 kV Jyotipura JGY for re-jumpering. 66 kV Palaiya SS operator handtripped 11 kV Jyotipura JGY. Shri. S N Malek, Electrical Assistant, shorted all 3 phases and earthed them properly and started his work. | Awaited | NA | NA | Line staff instructed to take line clear for any kind of work and earthing to be carried out both side of pole. | Nadiad | 3 | To attain high voltage complain given from Nadiad Rural Sub Division Complain Center, he went to 100 kVA Hathaj village TC. He noticed that on TC DO, jumper on 11 kV side was sparking and was loose. So he decided to re-jumper it. So he called 66 kV Palaiya SS and asked the operator to handtrip 11 kV Jyotipura JGY for re-jumpering. 66 kV Palaiya SS operator handtripped 11 kV Jyotipura JGY. Shri. S N Malek, Electrical Assistant, shorted all 3 phases and earthed them properly and started his work. | Awaited | NA | NA | Line staff instructed to take line clear for any kind of work and earthing to be carried out both side of pole. | Nadiad
147 | Yogeshbhai Brijbhanprasad Patel,Dumping yard,Vill-Jamiyatpura,Ta-Balasinor,Dist-Mahisagar | 2023-11-06 | FHO | TRUCK DRIVER(YOGESHBHAI BRIJBHAN PRASAD PATEL) PARKED THEIR VEHICAL UNDER 11 KV MANVARPURA JGY AT DUMPING YARD AND DRIVER CLIMB ON LOADED TRUCK TO REMOVE COVER AND ACCIDENTLY COME IN CONTACT WITH LIVE 11KV HT LINE | Awaited | NA | NA | Line ground clearance is done | Nadiad | 6 | TRUCK DRIVER(YOGESHBHAI BRIJBHAN PRASAD PATEL) PARKED THEIR VEHICAL UNDER 11 KV MANVARPURA JGY AT DUMPING YARD AND DRIVER CLIMB ON LOADED TRUCK TO REMOVE COVER AND ACCIDENTLY COME IN CONTACT WITH LIVE 11KV HT LINE | Awaited | NA | NA | Line ground clearance is done | Nadiad
148 | Buffalo of Shri Bharvad Ishvarbhai Kanjibhai,Near Grampanchayat Office,Vill-Jetpur,Ta-Limkheda,Dist-Dahod | 2023-11-09 | FA | THE BUFFALO WAS GRAZING NEAR 100 KVA DP STRUCTURE AND LT TAPPING POLE NEAR JETPUR DU GRAM PANCHAYAT OFFICE.DURING GRAZING THE BUFFALO STARTED RUBBING THE HORN WITH STAY WIRE OF LT TAPPING POLE AND DUE TO WHICH OUTGOING LT CABLE JUMPER GOT TOUCHED TO TURN BUCKLE, THE GUY INSULATOR OF THE STAY WIRE WAS ALREADY DAMAGED AND DUE TO WHICH THIS BUFFALO GOT ELECTROCUTED AND DIED | Awaited | NA | NA | MAINTENANCE OF TRANSFORMER DONE, NEW EARTHING DONE,PVC PIPE IS ADDED IN EARTHING | Godhra | 2 | THE BUFFALO WAS GRAZING NEAR 100 KVA DP STRUCTURE AND LT TAPPING POLE NEAR JETPUR DU GRAM PANCHAYAT OFFICE.DURING GRAZING THE BUFFALO STARTED RUBBING THE HORN WITH STAY WIRE OF LT TAPPING POLE AND DUE TO WHICH OUTGOING LT CABLE JUMPER GOT TOUCHED TO TURN BUCKLE, THE GUY INSULATOR OF THE STAY WIRE WAS ALREADY DAMAGED AND DUE TO WHICH THIS BUFFALO GOT ELECTROCUTED AND DIED | Awaited | NA | NA | MAINTENANCE OF TRANSFORMER DONE, NEW EARTHING DONE,PVC PIPE IS ADDED IN EARTHING | Godhra
149 | Rathwa Lalsingbhai Nanjibhai,B/H Primary School,Vill-Dholimar,Ta-Halol,Dist-Panchmahal | 2023-11-10 | FHO | ATSITE LALSINGBHAI WAS WORKING AT HIS FARM HIS FARM IS COVERD WITH BARE IRON WIRE FENSING FOR PROTECTION OF CROP AGINST WIDE PIG.11KV POYLI FDR PASSING OVER SAID LOCATION AS PER THE LI REPORT AND SITE SITUATION IT MAY BE PRESUMED THAT THE 11 KVTOP PH CONDUCTOR OF POYLI JGY WAS BROKEN AND FALLEN ON BARE IRON WIRE , THE VICTIM GOT ACCIDENTALLY TOUCHED HIS FEET WITH IRON WIRE FENSING AND GOT ELECTROCUTED AND DIED ON SPOT ON TRIPING WAS OBSERVED ON SAID FEEDER | Awaited | NA | NA | 11 KV TOP PIN REPLACED , RESTRINGING OF CONDUCTOR AND NEW EARTHING WITH PVC PIPE DONE AND LINE MAINTENANCE WORK DONE | Godhra | 1 | ATSITE LALSINGBHAI WAS WORKING AT HIS FARM HIS FARM IS COVERD WITH BARE IRON WIRE FENSING FOR PROTECTION OF CROP AGINST WIDE PIG.11KV POYLI FDR PASSING OVER SAID LOCATION AS PER THE LI REPORT AND SITE SITUATION IT MAY BE PRESUMED THAT THE 11 KVTOP PH CONDUCTOR OF POYLI JGY WAS BROKEN AND FALLEN ON BARE IRON WIRE , THE VICTIM GOT ACCIDENTALLY TOUCHED HIS FEET WITH IRON WIRE FENSING AND GOT ELECTROCUTED AND DIED ON SPOT ON TRIPING WAS OBSERVED ON SAID FEEDER | Awaited | NA | NA | 11 KV TOP PIN REPLACED , RESTRINGING OF CONDUCTOR AND NEW EARTHING WITH PVC PIPE DONE AND LINE MAINTENANCE WORK DONE | Godhra
150 | Pagi Parvatbhai Nanabhai,Vill-Pagiyawada,Ta-Lunawada,Dist-Mahisagar | 2023-11-20 | FHO | On checking the spot and taking the statement of an eyewitness, it is found that Patelia Bhupendrabhai Salambhai had gone from his house in the afternoon to plow the field on the outskirts of Pagiawad village. While plowing in his field, a sudden noise was heard and it was found that someone had climbed on the power transformer placed for the farm near his field, so he made a phone call to the line staff of his area and stopped the power line. Pagi Parvatbhai Nanabhai died after climbing on th | Awaited | NA | NA | Maintenance done | Godhra | 6 | On checking the spot and taking the statement of an eyewitness, it is found that Patelia Bhupendrabhai Salambhai had gone from his house in the afternoon to plow the field on the outskirts of Pagiawad village. While plowing in his field, a sudden noise was heard and it was found that someone had climbed on the power transformer placed for the farm near his field, so he made a phone call to the line staff of his area and stopped the power line. Pagi Parvatbhai Nanabhai died after climbing on th | Awaited | NA | NA | Maintenance done | Godhra
151 | Vanrajsinh C Jadeja,Nr shri Ram Shopping centre,Vill-Dakor,Ta-Thasra,Dist-Kheda | 2023-11-21 | NFHD | On Dtd.21.11.2023,there was no power complain recieved by telephonic on complain centre, so after line petrolling found that Jumper was burnt on location no.RAN/052 DODP Switchof 11 KV Ranchhodji (Urban) feeder.Shri M C ChauhanLM,Shri H B Parmar EA and shri V C Jadeja(EA-victim) went to DODP Switch to replace burnt jumper on pole,there was three Underground cable coming to shackle pole switch.(1) Main Cable from busbar to DODP Structure Switch which was charged due to R & B work in progress whic | Awaited | NA | NA | Notice board of dual power supply is provided at shri ram complex AB switch and 11 KV Cable disconnected. Show cause notice issued to M.C.Chauhan LM letter No NOD/HR/MCC/124 dated 13.12.23 H.B Parmar EA NOD/HR/HBP/125 dated 13.12.23 | Nadiad | 3 | On Dtd.21.11.2023,there was no power complain recieved by telephonic on complain centre, so after line petrolling found that Jumper was burnt on location no.RAN/052 DODP Switchof 11 KV Ranchhodji (Urban) feeder.Shri M C ChauhanLM,Shri H B Parmar EA and shri V C Jadeja(EA-victim) went to DODP Switch to replace burnt jumper on pole,there was three Underground cable coming to shackle pole switch.(1) Main Cable from busbar to DODP Structure Switch which was charged due to R & B work in progress whic | Awaited | NA | NA | Notice board of dual power supply is provided at shri ram complex AB switch and 11 KV Cable disconnected. Show cause notice issued to M.C.Chauhan LM letter No NOD/HR/MCC/124 dated 13.12.23 H.B Parmar EA NOD/HR/HBP/125 dated 13.12.23 | Nadiad
152 | Dindor Sardarbhai Hirsingbhai,Vill-Dhamanbari,Ta-Singvad,Dist-Dahod | 2023-11-23 | NFHO | ACCORDING TO PANCHNAMA, ON DATED 23-11-2023 AROUND 01:30 PM SHRI DINDOR SARDARBHAI HIRSINGBHAI WAS GOING THROUGH THE FARM OF SHRI AD CHHAGANBHAI MANGLABHAI FOR FUNERAL.11 KV WAGHNALA AG FEEDER HT LINE PASSES THROUGH THIS FARM.THE HT TAPPING POLE ON ONE SIDE OF THE FARM WAS TILTED DUE TO A WATER PATH CREATED EXACTLY NEARBY THIS POLE.ALSO THE SPAN LENGTH OF THE SPAN WAS AROUND 80 MTR.DUE TO THIS CONDUCTOR GOT LOOSE AND THE FARM LAND HAD WET DUE TO WATER SPREAD AROUND FARM FOR FARMING. SHRI DIND | Awaited | NA | NA | LOCATION IS RECTIFED, LINE RESTRINGING IS DONE. | Godhra | 2 | ACCORDING TO PANCHNAMA, ON DATED 23-11-2023 AROUND 01:30 PM SHRI DINDOR SARDARBHAI HIRSINGBHAI WAS GOING THROUGH THE FARM OF SHRI AD CHHAGANBHAI MANGLABHAI FOR FUNERAL.11 KV WAGHNALA AG FEEDER HT LINE PASSES THROUGH THIS FARM.THE HT TAPPING POLE ON ONE SIDE OF THE FARM WAS TILTED DUE TO A WATER PATH CREATED EXACTLY NEARBY THIS POLE.ALSO THE SPAN LENGTH OF THE SPAN WAS AROUND 80 MTR.DUE TO THIS CONDUCTOR GOT LOOSE AND THE FARM LAND HAD WET DUE TO WATER SPREAD AROUND FARM FOR FARMING. SHRI DIND | Awaited | NA | NA | LOCATION IS RECTIFED, LINE RESTRINGING IS DONE. | Godhra
153 | Buffalo of Alpesh Ghanshyam Chauhan,Vill-Rinza,Ta-Tarapur,Dist-Anand | 2023-11-25 | FA | DUE TO HEAVY RAIN AND WIND PRESSURE LT ABC SLIIPED FROM LT SHACKLE INSULATOR AND TOUCHED TO U-CLAMP AND THROUGH IT LEAKAGE CURRENT PASSED IN G.I.WIRE AND WHICH CONVERTED INTO ACCIDENT. | Awaited | NA | NA | Maintenance done | Anand | 2 | DUE TO HEAVY RAIN AND WIND PRESSURE LT ABC SLIIPED FROM LT SHACKLE INSULATOR AND TOUCHED TO U-CLAMP AND THROUGH IT LEAKAGE CURRENT PASSED IN G.I.WIRE AND WHICH CONVERTED INTO ACCIDENT. | Awaited | NA | NA | Maintenance done | Anand
154 | Cow Of Shri Vaghabhai Ramabhi Bharvad,Patak Vistar,Vill-Boriavi,Ta-Anand,Dist-Anand | 2023-11-26 | FA | GI Wire was in leakage current due to LT ABC insulation damage and live wire came in Contact with U Clamp and from U Clamp to GI Wire direct current was reflected. Cow was wondering and came in contact with GI wire at Ground.Cow was died on spot due to electroinductioned. | DUE TO LEACKAGE CURRENT FLOWN TO GI WIRE FROM U CLAMP TO GROUND | NOT SUGGESTED |  | PIPE PROVIDED TO GI WIRE UP TO GROUND LEVEL | Anand | 2 | GI Wire was in leakage current due to LT ABC insulation damage and live wire came in Contact with U Clamp and from U Clamp to GI Wire direct current was reflected. Cow was wondering and came in contact with GI wire at Ground.Cow was died on spot due to electroinductioned. | DUE TO LEACKAGE CURRENT FLOWN TO GI WIRE FROM U CLAMP TO GROUND | NOT SUGGESTED |  | PIPE PROVIDED TO GI WIRE UP TO GROUND LEVEL | Anand
155 | Madhavbhai Nathubhai Ninama,Nr avalon Green Society ,Vill-Sevasi,Ta-Vadodara,Dist-Vadodara | 2023-11-26 | NFHD | ON DT.26.11.23 ,UG cable charging work of sevasi jgy was carried out. at a time of two ends of XLPE cable jumpring work on AB switch a heavy induction /return supply felt by the victim. | Awaited | NA | NA | Instruction of all line staff for use of safety articals at that time of work. | Baroda O&M | 3 | ON DT.26.11.23 ,UG cable charging work of sevasi jgy was carried out. at a time of two ends of XLPE cable jumpring work on AB switch a heavy induction /return supply felt by the victim. | Awaited | NA | NA | Instruction of all line staff for use of safety articals at that time of work. | Baroda O&M
156 | Bhalabhai Somabhai Bariya,Nr. Nima Rice Mill,Vill-Vega,Ta-Dabhoi,Dist-Vadodara | 2023-11-26 | FHO | ON DATE 26/11/23, LINE CLEAR WAS TAKEN FOR 11 KV BHILAPUR JGY AS WELL AS HT LINE OF BHILAPUR JGY WAS SHORTED AND EARTHED ON BOTH SIDE OF WORK PLACE.WHILE WORKING ON NEWLY CONSTRUCTED DODP NR NIMA RICE MILL VICTIM FELT A LIKE ELECTRIC SHOCK AND HE FALL DOWN FROM DODP STRUCTURE.RESON IS UNKNOWN FOR ELECTRIC SHOCK AS NO BURNT MARK RECEIVED ON VICTIM BODY. | Awaited | NA | NA | NA | Baroda O&M | 8 | ON DATE 26/11/23, LINE CLEAR WAS TAKEN FOR 11 KV BHILAPUR JGY AS WELL AS HT LINE OF BHILAPUR JGY WAS SHORTED AND EARTHED ON BOTH SIDE OF WORK PLACE.WHILE WORKING ON NEWLY CONSTRUCTED DODP NR NIMA RICE MILL VICTIM FELT A LIKE ELECTRIC SHOCK AND HE FALL DOWN FROM DODP STRUCTURE.RESON IS UNKNOWN FOR ELECTRIC SHOCK AS NO BURNT MARK RECEIVED ON VICTIM BODY. | Awaited | NA | NA | NA | Baroda O&M
157 | HE Buffalo of Mafatbhai Bhagvanbhai Bharvad, Harijanwalu naku,Vill-Dumral,Ta-Nadiad,Dist-Kheda | 2023-12-06 | FA | Owner Of A Herd Of Buffalo Residing Hanumanpura Dumral Was Taking Them For Grazing. While Going From Hanumanpura To Piplata Chokdi One He Buffalo Came Near DO Structure For Itching Which Is Near Harjanwalu Naku Area. Both The Stays On DO Structure Were Cut From Ground And Winded On DO Structure Poles. DO Jumpers Both Incoming And Outgoing Are Coated. Outgoing Jumpers Are Having Open Joint In The Lower Part. HE Buffalo Started Itching On Pole Where The Stay Is Winded. So Stay Wire Came In Contact | Awaited | NA | NA | Line maintenance carried out with re-jumpering and removal of broken stay wire. | Nadiad | 2 | Owner Of A Herd Of Buffalo Residing Hanumanpura Dumral Was Taking Them For Grazing. While Going From Hanumanpura To Piplata Chokdi One He Buffalo Came Near DO Structure For Itching Which Is Near Harjanwalu Naku Area. Both The Stays On DO Structure Were Cut From Ground And Winded On DO Structure Poles. DO Jumpers Both Incoming And Outgoing Are Coated. Outgoing Jumpers Are Having Open Joint In The Lower Part. HE Buffalo Started Itching On Pole Where The Stay Is Winded. So Stay Wire Came In Contact | Awaited | NA | NA | Line maintenance carried out with re-jumpering and removal of broken stay wire. | Nadiad
158 | She-Buffalo of Shree Ravidasbhai Kalubhai Rathwa,Vill-Vakaner,Ta-Kawant,Dist-Chhota Udepur | 2023-12-09 | FA | AS PER PRIMARY INVESTIGATION INFORMATION RECIEVED FROM VILLEGERS LT AB CABLE WAS SLIPPED FROM LT SHACKLE AND JOINT TOUCHED WITH U CLAMP AND MEANWHILE THE EARTHING WIRE WAS ALSO BROKEN AND IT TOUCHED THE GUY WIRE WHILE BUFFALO WAS GOING TO EAT FODDER OF BAMBOO AND CAME IN CONTACT WITH GUY WIRE OF LT POLE AND GOT ELECTROCUTED. | Awaited | NA | NA | NEW EARTHING PROVIDED AND RECTIFICATRION OF STAY WIRE | Baroda O&M | 2 | AS PER PRIMARY INVESTIGATION INFORMATION RECIEVED FROM VILLEGERS LT AB CABLE WAS SLIPPED FROM LT SHACKLE AND JOINT TOUCHED WITH U CLAMP AND MEANWHILE THE EARTHING WIRE WAS ALSO BROKEN AND IT TOUCHED THE GUY WIRE WHILE BUFFALO WAS GOING TO EAT FODDER OF BAMBOO AND CAME IN CONTACT WITH GUY WIRE OF LT POLE AND GOT ELECTROCUTED. | Awaited | NA | NA | NEW EARTHING PROVIDED AND RECTIFICATRION OF STAY WIRE | Baroda O&M
159 | Sh Gopalbhai Madhavbhai Parmar, Beside Nijanand Ashram,Vill-Ankhol,Ta-Waghodia,Dist-Vadodara | 2023-12-11 | NFHD | On dtd 11.12.2023, Work for reconnection of meter and complain of transformer voltage fluctuations at Rudraksh county society on Ankhol JGY feeder was carried out by local line staff (Sh. Shankarbhai Rathva & Gopalbhai Parmar). Both of them started work after wearing helmet. Before starting of work, DO of DODP was taken off and needed work like verification of HT & LT side stud and lugging position etc on TCDP was started by Victim - Sh. Gopalbhai Parmar & needful rectification work also starte | Awaited | NA | NA | at the accident place not any rectification require and line staff awarness programe made by sdo | Baroda O&M | 3 | On dtd 11.12.2023, Work for reconnection of meter and complain of transformer voltage fluctuations at Rudraksh county society on Ankhol JGY feeder was carried out by local line staff (Sh. Shankarbhai Rathva & Gopalbhai Parmar). Both of them started work after wearing helmet. Before starting of work, DO of DODP was taken off and needed work like verification of HT & LT side stud and lugging position etc on TCDP was started by Victim - Sh. Gopalbhai Parmar & needful rectification work also starte | Awaited | NA | NA | at the accident place not any rectification require and line staff awarness programe made by sdo | Baroda O&M
160 | 1)Baldevbhai Arjanbhai Parmar-Fatal 2)Tusharsinh Badesinh Parmar-Non Fatal 3)Mahobatsinh Kesarisinh Parmar-Non-Fatal ,Vill-Hirapura Alawa,Ta-Kapadwanj,Dist-Kheda | 2023-12-12 | FHO | On dated 12.12.23 at around 12:30 pm Victim Late Shri. Baldevbhai Parmar & Two Others Shri.Tusharsinh Badebhai Parmar and Shri. Mahobatsinh Kesarisinh Parmar were working in the bore well of Prabhudas Karsandas Patel's farm to Downward the submersible motor into the bore well with Tower (Ladder) hight is 18.5 Feet & it attached on 2.5 feet tractor Connected cart. So, Total High is 21.5 Feet. After completing the operation of Downward the motor into Bore well. The Drive The Tractor front side and | Awaited | NA | NA | After Electric Shock All 3 Victim Shifted In Kapadvanj Private Hospital For Treatment By A Private Vehicle. After The Further Instruction As Per Doctor From There They Were Shifted Civil Hospital For Further Treatment Where Shri. Baldevbhai Parmar Was Declared Death And Shri. Tusharsinh And Mahobatsinh Parmar Are Currently Under Treatment. | Nadiad | 6 | On dated 12.12.23 at around 12:30 pm Victim Late Shri. Baldevbhai Parmar & Two Others Shri.Tusharsinh Badebhai Parmar and Shri. Mahobatsinh Kesarisinh Parmar were working in the bore well of Prabhudas Karsandas Patel's farm to Downward the submersible motor into the bore well with Tower (Ladder) hight is 18.5 Feet & it attached on 2.5 feet tractor Connected cart. So, Total High is 21.5 Feet. After completing the operation of Downward the motor into Bore well. The Drive The Tractor front side and | Awaited | NA | NA | After Electric Shock All 3 Victim Shifted In Kapadvanj Private Hospital For Treatment By A Private Vehicle. After The Further Instruction As Per Doctor From There They Were Shifted Civil Hospital For Further Treatment Where Shri. Baldevbhai Parmar Was Declared Death And Shri. Tusharsinh And Mahobatsinh Parmar Are Currently Under Treatment. | Nadiad
161 | Cow of Shri Waghabhai Rajabhai Sasla,Pureta Vistar,Vill-Nandoli,Ta-Matar,Dist-Kheda | 2023-12-13 | FA | on dt 13.12.2023 cow of Shri Waghabhai Rajabhai Sasla passing near to DO structure of 11 KV NANDOLI AG feeder which is located at pureta vistar and ag line of kalabhai budhabhai parmar and suddenly outgoing do wire is broken and cow came in to the contact with wire and got electic shock and died on the spot. | Awaited | NA | NA | NEW JUMPER PROVIDED | Nadiad | 1 | on dt 13.12.2023 cow of Shri Waghabhai Rajabhai Sasla passing near to DO structure of 11 KV NANDOLI AG feeder which is located at pureta vistar and ag line of kalabhai budhabhai parmar and suddenly outgoing do wire is broken and cow came in to the contact with wire and got electic shock and died on the spot. | Awaited | NA | NA | NEW JUMPER PROVIDED | Nadiad
162 | Nadimsha S Diwan,Near Chorpura Tapline,Vill-Gothda,Ta-Savli,Dist-Vadodara | 2023-12-13 | NFHD | The non fatal accident occurd to Shri N.S.Diwan EA(VS) of savli sub divi.by having leakage of current through cut off AB Switch As the snake Fallen between the male female part of ab swich which cut off. | Awaited | NA | NA | A B Switch Maint including with New Jumper and Preper and proper Clearnce between two contacat work done. | Baroda O&M | 3 | The non fatal accident occurd to Shri N.S.Diwan EA(VS) of savli sub divi.by having leakage of current through cut off AB Switch As the snake Fallen between the male female part of ab swich which cut off. | Awaited | NA | NA | A B Switch Maint including with New Jumper and Preper and proper Clearnce between two contacat work done. | Baroda O&M
163 | Smt Kokilaben Arvindbhai Chauhan(Fatal human) , Sonalben Arvindbhai Chauhan(Non Fatal human), Bhatiyapura Sim, Vill-Haripura, Tal-Khambhat, Dist-Anand | 2023-12-23 | FHO | During primary investigation accident occurred on 2W open LT line of Bhatiyapura Sim vistar Transformer of 11 KV Amiyad JGY Feeder. The LT pole (AMD057/0018) on which accident occurred is open LT line and one wire was found escaped from LT shackle binding and touched the C Clamp. The earth wire of LT pole was found broken from earth and wrapped around pole at the time of site visit. It seems the Victim came in contact with the earth wire and got electrocuted. The nonfatal accident occurred to ot | Awaited | NA | NA | Binding & maintenance done | Anand | 2 | During primary investigation accident occurred on 2W open LT line of Bhatiyapura Sim vistar Transformer of 11 KV Amiyad JGY Feeder. The LT pole (AMD057/0018) on which accident occurred is open LT line and one wire was found escaped from LT shackle binding and touched the C Clamp. The earth wire of LT pole was found broken from earth and wrapped around pole at the time of site visit. It seems the Victim came in contact with the earth wire and got electrocuted. The nonfatal accident occurred to ot | Awaited | NA | NA | Binding & maintenance done | Anand
164 | Jyotiben Jivabhai Gujarati (Fatal) Vasuben Madeva Ahir (Non Fatal) Trikambhai Gopalbhai Chhanga(Non Fatal) ,Vill-Dakor,Ta-Thasra,Dist-Kheda | 2023-12-26 | FHO | ON DT 26.12.13 AN Accident took place at dakor near pahiyari ashram ,bharat buvan to gayo no vado road at around 2 00 pm a luxury sleeper coach bus with 30 passengers get take reverse from on kacha canal road to main road ,a one lady passenger was running toward bus and climb on stairs of bus.one step is onbus stair and other foot is on eatrh,at that time a tree branch on bus was touch to live live wires of muliyad jgy fdr so lady passenger got electric shock and othr two passengers had touch | Awaited | NA | NA | 11 Meter RSJ pole erected .Ground clearance is done and dead span removed | Nadiad | 2 | ON DT 26.12.13 AN Accident took place at dakor near pahiyari ashram ,bharat buvan to gayo no vado road at around 2 00 pm a luxury sleeper coach bus with 30 passengers get take reverse from on kacha canal road to main road ,a one lady passenger was running toward bus and climb on stairs of bus.one step is onbus stair and other foot is on eatrh,at that time a tree branch on bus was touch to live live wires of muliyad jgy fdr so lady passenger got electric shock and othr two passengers had touch | Awaited | NA | NA | 11 Meter RSJ pole erected .Ground clearance is done and dead span removed | Nadiad
165 | Ketanbhai Ramanbhai Baria,Shikari Faliya,Vill-Guna,Ta-D'Baria,Dist-Dahod | 2023-12-28 | FHO-Pvt | A fatal human outsider Electrical accident occurred at village guna on MGVCL Network on dtd. 28.12.2023 at 17:30 HRS Approximately.The people of Guna village shri Gopsingbhai sartanbhai & saylabhai sartanbhai had fenced iron wire around the farm to protect the standing crops in their field from wild animals. Then, in this iron fence, one end of the private wire is illegally connected to the wire of that fence and the other end of the wire is connected to the LT line on the pole and electric cu | Awaited | NA | NA | Part Of Of Wire Which Was Attached To Low Tension Line Was Removed And Police Fariyad Done On Two People Mr. Gopsingbhai Sartanbhai And Sayabhai Sartanbhai FIR No 02/01.01.2024. | Godhra | 6 | A fatal human outsider Electrical accident occurred at village guna on MGVCL Network on dtd. 28.12.2023 at 17:30 HRS Approximately.The people of Guna village shri Gopsingbhai sartanbhai & saylabhai sartanbhai had fenced iron wire around the farm to protect the standing crops in their field from wild animals. Then, in this iron fence, one end of the private wire is illegally connected to the wire of that fence and the other end of the wire is connected to the LT line on the pole and electric cu | Awaited | NA | NA | Part Of Of Wire Which Was Attached To Low Tension Line Was Removed And Police Fariyad Done On Two People Mr. Gopsingbhai Sartanbhai And Sayabhai Sartanbhai FIR No 02/01.01.2024. | Godhra
166 | 1)Shri Brijesh Madan Yadav (fatal) 2)Shri Baharan Jagu Chauhan (Non-fatal) Gorva-Undera Road,Vill-Undera,Ta-Vadodara,Dist-Vadodara | 2023-12-29 | FHO | On dtd 29.12.2023, i.e.today, Victims were carrying Aluminium ladder handcart for Construction site behind Reliance jio Petrol pump. While they were trying to pass below the 11 kv Undera jgy line, Ladder touched the 11 KV Undera Jgy conductor and electrocuted. Further investigation is under progress. | Awaited | NA | NA | due to negligance of victim | Baroda O&M | 6 | On dtd 29.12.2023, i.e.today, Victims were carrying Aluminium ladder handcart for Construction site behind Reliance jio Petrol pump. While they were trying to pass below the 11 kv Undera jgy line, Ladder touched the 11 KV Undera Jgy conductor and electrocuted. Further investigation is under progress. | Awaited | NA | NA | due to negligance of victim | Baroda O&M
167 | Charpot Rahulbhai Arvindbhai,Holi faliya,Vill-Karodia,Tal-Fatepura, Dist-Dahod | 2023-12-30 | NFHO | as per primary investigation and eye witness statement it came to know that on date 30.12.2023 victim(Charpot Rahulbhai Arvindbhai) at time around 16:30 was playing behind his home where an iron shed was constructed under HT line of Dungar jgy feeder Saraswa S/S while playing victim climbed on top of iron shed to pick the toy from the top of shed where he may be accidently came contact with the HT line of Dungar feeder and got electrocation and victim fall down on the ground and then after vict | Awaited | NA | NA | NOTICE ISSUED TO PARTY FOR UN AUTHORISED CONSTRUCTION | Godhra | 6 | as per primary investigation and eye witness statement it came to know that on date 30.12.2023 victim(Charpot Rahulbhai Arvindbhai) at time around 16:30 was playing behind his home where an iron shed was constructed under HT line of Dungar jgy feeder Saraswa S/S while playing victim climbed on top of iron shed to pick the toy from the top of shed where he may be accidently came contact with the HT line of Dungar feeder and got electrocation and victim fall down on the ground and then after vict | Awaited | NA | NA | NOTICE ISSUED TO PARTY FOR UN AUTHORISED CONSTRUCTION | Godhra
168 | Suraj Hirubhai Meda,Smashan Road,Vill-Dahod,Ta-Dahod,Dist-Dahod |  |  | 2024-01-01 | FHO | [5 empty] | VICTIM MAY BE PUT HIS HAND IN THE LT DISTRIBUTION BOX AND GOT SHOCKED AND DIED ON THE SPOT | Awaited | NA | NA | The accident is suicidal/intentional, the victim has intentionally put his hand into distribution box. | Godhra
169 | Pagi Pankajbhai Arjanbhai,Zarakhala Faliyu,Vill-Kolvan,Ta-Lunawada,Dist-Mahisagar |  |  | 2024-01-02 | FHO-Pvt | [5 empty] | While Site Visiting It Is Found That , On That Location As per the information received from Sarpanchshri kolvan at Zarkhala faliya a fatal and non fatal accident occured to Shri Pagi Pankajbhai Arjanbhai and Pagi Arjanbhai Ramabhai. Whenever Pagi Pankajbhai Arjanbhai was repair fuse board in his AG connection room during the repairing of the fuse board at that time he was suddenly contact with live fuse wire and electrocuted. He was loudly shrick and at that time his father Pagi Arjanbhai Ramabhai | Awaited | NA | NA | due to negligance of victim | Godhra
170 | Bullock,Nishal Faliya,Vill-Kotara,Ta-Santrampur,Dist-Mahisagar |  |  | 2024-01-03 | FA | [5 empty] | As per Site Visit and Eye Witness Statement at the said location Shardaben Savjibhai Tadvi Eye Witness was grazing her Cattles at the top of the hill. Meanwhile strong wind was also blowing and due to that the HT Conductor of nearby passing line of 11 KV Simaliya AG Feeder broken down and fell on one of the bullock. This ultimately results in electrocution of the bullock and another bullock gets electrocuted due to potential gradient created nearby it. | Awaited | NA | NA | Broken conductor repair and necessary maintenance carried out for avoid accident. | Godhra
171 | Mr Piyush Chauhan,Jay Ambe Nagar,Vill-Vadodara,Ta-Vadodara,Dist-Vadodara |  |  | 2024-01-06 | FHO | [5 empty] | Victim met accident while flyig kite on the roof of his house , moved to hospital through 108 on dt.06.01.2024 at time 3:30 approx. & found dead. | Victim meet accident by completing circuit between roof ( iron) & nearby passing street light earthing wire as there is leakage current coming from fan hang on iron rod under iron roof without any insulation between them. Also found that polarity is reversed in the said house switchboard .i.e. phase is always ON in switch ON & OFF both condition. | Installation of RCCB is important to avoid such accident |  | Advised to remove such structure ( IRON ROOF supported by IRON ROD & Electrical equipment hang on IT) | Baroda City
172 | Alpesh Bipinbhai Vagela,Kheda Faliya,Vill-Vagela,Ta-Zalod,Dist-Dahod |  |  | 2024-01-08 | NFHD | [5 empty] | AS PER INVESTIGATION AND INFORMATION RECEIVED, VICTIM WAS ATTENDING LT LINE COMPLAIN,POWER MADE OF TRANSFORMER BY DOING PHASE WIRE CUT IN DISTRIBUTION BOX THEN AFTER VICTIM CLIMBED ON LT LINE POLE, HE TOUCHES LT NUETRAL WIRE AND ELECTROCUTED AND HE LOST HIS BALANCE AND SLIPPED FROM LT POLE AND INJURED ON BACKSIDE OF HEAD AND LEFT HAND PALM. | Awaited | NA | NA | LT LINE ONE CONDUCTOR SLIPPED FROM LT SHACKLE INSULATOR IS RECTIFIED AND LT LINE PATROLLING DONE ALSO FUSE OF TRANSFORMER LT DISTRIBUTION BOX REPLACED AND NEW EARTHING DONE | Godhra
173 | Mudasir Abdulkayum Parey (FHO), Manzoorul Hamid (NFHO),B/H Goodluck Hotel,Vill-Hariyala,Ta-Kheda,Dist-Kheda |  |  | 2024-01-12 | FHO | [5 empty] | THE TRUCK DRIVER WAS DRIVING TRUCK ON ROAD PASSING THTOUGH FARMS. THE EXTENDED HOOK CAME IN CONTACT WITH LIVE 11 KV CONDUCTOR. THE CLEANER WAS ELECTROCUTED AND DIED ON THE SPOT. WHILE DRIVER WAS GOT BURNT AND SHIFTER TO KHEDA CIVIL HOSPITAL FOR MORE TREATMENTS. | Awaited | NA | NA | To Increase The Height Of Line Two PSC Pole Below The Line And On Both Side Of Elevated RCC Road Has Been Proposed. | Nadiad
174 | Smt Januben Haribhai Bharvad,Near Mahadev Faliyu,Vill-Valotri,Ta-Matar,Dist-Kheda |  |  | 2024-01-13 | FHO | [5 empty] | AT VILLAGE VALOTRI THE VICTIM SMT JANUBEN HARIBHAI BHARVAD WAS PASSING FROM NEAR TO MAHADEV FALIYA FOR WASTE DISPOSAL AND SUDDENLY 11 KV HADEVA JGY FEEDER ONE CONDUCTOR IS BROKEN DUE TO KITE FESTIVAL KITE THREAD AND FALL ON VICTIM AND SHE GOT ELECTRIC SHOCKED.SHE IS SHIFTED IMMEDIATLY TO HOSPITAL FOR FURTHER TREATMENT. | Awaited | NA | NA | Maintenace was done and power supply restored | Nadiad
175 | Dangi Siddharthkumar Virsingbhai,Vill-Katholiya,Ta-Limkheda,Dist-Dahod |  |  | 2024-01-14 | FHO | [5 empty] | ACCORDING TO EYEWITNESS STATEMENT ON DTD 14-01-2024 AROUND 09:15 AM VICTIM WAS FLYING KITE ON THE GROUND IN THE FARMLAND OF DANGI MALABHAI DITABHAI WITH NO NEARBY HOUSEHOLD OR ANY OTHER TYPE OF STRUCTURE.11 KV MATWA AG FEEDER HT LINE WAS PASSING NEARBY FARMLAND.DUE TO DEW AND FOG THE FARMLAND WAS WET.WHILE FLYING THE KITE WITH A WHITE COTTON THREAD WHICH WAS ALSO WET DUE TO FOG AND DEW, THEKITE GOT STRUCK IN THE HT LINE AND WHILE REMOVING THE KITE WITH THE HELP OF THE WET THREAD AS PER EYEWITNES | Awaited | NA | NA | The accident was occurred due to climatic condition.i.e. fog and dew. | Godhra
176 | Nayak Kishanbhai Rangitbhai,Thori Vas Sati Talavdi Halol,Vill-Halol,Ta-Halol,Dist-Panchmahal |  |  | 2024-01-16 | NFHO | [5 empty] | ACCORDING TO INVESTIGATION REPORT, AROUND 02:00 PM SHRI KISHANBHAI RANGITBHAI NAYAK WAS CLIMBED ON ROOF OF SHACK WHICH WAS MADE BESIDE HIS HOUSE,THE TOP OF WHICH WAS MADE OF METAL SHEET APPROX 06 FOOT ABOVE THE GROUND. 11 K.V LINE OF SHUBHAM URBAN FDR IS PASSING JUST BESIDE THIS SHACK. AS PER EYE WITNESS STATEMENT, THE VICTIM CLIMBED ON THIS SHACK ROOF FOR KITE CATCHING PURPOSE HOLDING A METAL ROD OF APPROX 09 FOOT LENGTH,THE KITE WAS HANGING ON 11 K.V O/H LINE OF SHUBHAM FDR SO THE VICTIM TRIED | Awaited | NA | NA | NOTICE ISSUED TO VICTIM FOR ILLEGAL CONSTRUCTION | Godhra
177 | Chavad Dalpatbhai Ratilal,Near New Dudh Dairy,Vill-Dhundhaliya,Ta-Balasinor,Dist-Mahisagar |  |  | 2024-01-18 | NFHO | [5 empty] | Painting work executed by victim with the help of extended paint roller on the terrace of New Dairy building which has constructed under the 11 KV Kambopa ag feeder line. During painting work, victim came in contact with live 11 KV feeder line conductor and he had electrocuted. | Awaited | NA | NA | Notice is issued to owner of building not to carried out construction work under line | Nadiad
178 | Gelot Vishalbhai Punamchandbhai,Vill-Kanthaghar,Ta-Fatepura,Dist-Dahod |  |  | 2024-01-20 | FHO | [5 empty] | Huge mounds of soil have been erected illegally under 11 KV Afwa JGY line at Village Kanthagar Brickyard. According to an eyewitness statement, the victim was working in a brickyard and while talking on a mobile phone, he suddenly stepped on a pile of soil and unfortunately came in contact with an electric wire. He was immediately rushed to a nearby hospital where he was declared Died. A Dark spot visible on 11 KV conductor. | Awaited | NA | NA | NOTICE GIVEN TO BRICKSYARD OWNER FOR REMOVE PILE OF SOIL ERECTED UNDER HT LINE | Godhra
179 | Nakshkumar Kanjibhai Zala,Vill-Kathlal,Ta-Kathlal,Dist-Kheda |  |  | 2024-01-20 | FHO | [5 empty] | Natubhai Udesinh Zala who planted brinjal in his farm at Fulavat Village: Khalal. To save their Brinjal crop, Fencing is done by erecting peices of wood and wire is wound. A LT line of Barmuvada Jgy is passing through his farm. from which thay had punctured the LT Abc 2 wire and connected it to the earthing of that LT Pole and connected to the fencing wire. Nakshkumar kanjibhai zala is playing around this fencing wire and Died on spot. | Awaited | NA | NA | LT Pole Earthing Is Dismentalled And LT Abc Cable Insulation Is Done With LT Insulator | Nadiad
180 | Rajeshkumar (urfe Rajubhai) Ramanbhai pateliya,patel falia,Vill-Mahunala,Ta-Dhanpur,Dist-Dahod |  |  | 2024-01-26 | FHO | [5 empty] | As per statement of ALM Shri RC rathod 2 nos of labor of contractor AK luhar had climbed the xmer structure to replace fail xmer without any intimation/instruction given by him and even before LC of 11kv line could be taken. 1 labor got electric shock and other fell down due to shock from tc structure .Shri Rajeshkumar pateliya after treatement at dahod zydus hospital and thereafter at godhra private hospital passed away on dtd 29.01.2024 so now it is reported as fatal | Awaited | NA | NA | Staff Have Been Instructed To Not Allow Persons Working Under Them To Start Work Without Making Power Off And Other Safety Precautions Taken. | Godhra
181 | BHAILALBHAI SHANKARBHAI MACHHI,Vrajbhumi Socity,Vill-Vadodara,Ta-Vadodara,Dist-Vadodara |  |  | 2024-02-04 | FHO | [5 empty] | FATAL HUMAN(OUTSIDER) ELECTRICAL ACCIDENT OCCURRED AT SECOND FLOOR TERRACE OF HOUSE NO.H/233,VRAJ BHUMI SOC. AS PER THE SITE PANCHANAMA IT IS CONCLUDED THAT VICTIM WAS CLIMBING ON SECOND FLOOR TERRACE FOR THE WORK OF SERIES LIGHT DECORATION DUE TO UPCOMING MARRIAGE FUNCTION ON DT.6.2.2024. DURING THE WORK VICTIM HAS THROWN ELECTRICAL WIRE ON HOUSE NO.H/233 ACCIDENTALLY PRIVATE ELECTRICAL WIRE ARE FALL DOWN ON 11KV OVERHEAD LIVE CONDUCTOR. AND VICTIM GOT ELECTRIC SHOCK,BLACK COLOR FLASH OBSERVED | Awaited | NA | NA | LETTER WRITTEN TO HOUSE OWNER FOR MAINTENING SAFE DISTANCE FROM HT LINE VIDE LETTER NO: SARDAR ESTATE/590, 07.02.24 | Baroda City
182 | DEEPAKKUMAR KAMLESHBHAI CADI,Anand Nagar,Vill-Waghodia,Ta-Waghodia,Dist-Vadodara |  |  | 2024-02-10 | NFHO | [5 empty] | ON DT:-10.02.2024, VICTIM CLIMBED ON THE ROOF(IRON SHEET)illegally constructed house under HT line of 11 KV Madodhar AG feeder of SHRI SIKANDARBHAI ISMAILBHAI QURESHI'S HOUSE WHERE HT LINE OF 11 KV MADODHAR FEEDER WAS PASSING, TRYING TO GET KITE STUCK ON HT LINE CONDUCTOR OF 11 KV MADODHAR AGDOM FEEDR AND GOT TOUCH WITH 11 KV LINE AND GOT ELECTROCUTED. FURTHER INVESTIGATION IS UNDER PROGRESS. | Awaited | NA | NA | Extention provided to Maintain Clearance for avoid Accident . | Baroda O&M
183 | Shri Dalsukhbhai Mansukhbhai Parmar,Vill-Dabhasa,Ta-Padra,Dist-Vadodara |  |  | 2024-02-20 | FHO | [5 empty] | On dtd 20.02.2024, After marriage ceremony, for dismantling the Mandap fabrication the Victim climbed on the iron ladder to remove the illegally constructed mandap in farm of Manojbhai Patel below 11KV Dabhasa Agdom feeder. While trying to dismantle fabricated horizontal support angle, this angle was accidentally touched to live HT line conductor of 11 KV Dabhasa Agdom feeder and got electrocuted. Further investigation is under process. | Awaited | NA | NA | accident occurred due to victim's negligency no any action required | Baroda O&M
184 | BHAVSINGBHAI GAMIRBHAI BARIA,Vill-Gollav,Ta-Godhra,Dist-Panchmahal |  |  | 2024-02-22 | NFHD(Mech) | [5 empty] | As per statement and information recieved from eye witness Shri Divyesh H. Patel sarsav JGY was in fault and victim Shri BG Baria Lineman has taken the line clear No. 020 at 13.00 for attending the feeder.In gentry there was Y and B jumper burn from sarsav JGY feeder and B G Bariya climb on gentry switch for rejumper work and due to unbalance of body he fell down from middle channel and mechanical injury happen on his head and face.Getting this information 108 ambulance was called and taken hi | Awaited | NA | NA | Staffs Have Been Instructed To work with Safety Precautions, in order to avoid such type of accidents. | Godhra
185 | HITESHBHAI MUKESHBHAI RATHOD,Gokulpura Colony Vistar,Vill-Ambali,Ta-Anklav,Dist-Anand |  |  | 2024-02-23 | FHO | [5 empty] | on dated 23.2. 2024 approx. 09.40 am, As per the statement of eyewitness Victim late. Shri Hiteshbhai Mukeshbhai Rathod, while taking the towel from the PSC pole after taking bath ,He might get electrocuted and stuck with GI wire (earthing of lt pole) due to lekage current in GI wire. | Awaited | NA | NA | LT ABC Provided | Anand
186 | Mukeshbhai Bhanubhai Parmar,Gokulpura Colony Vistar,Vill-Betasi,Ta-Anklav,Dist-Anand |  |  | 2024-02-25 | NFHO | [5 empty] | On dt 25.02.2025 time approx 17.30 Victim shri Maheshbhai Babubhai Parmar who is Mentally Unstable was walking near hanumanji temple and all of a sudden he climed TC Structure and touch to live 11 kv HT side Bushing of Transformer and got shocked and fell down on the road from TC Structure. | Awaited | NA | NA | Barbed wire provided | Anand
187 | Smt Parulben maheshbhia jadav,Vill-Gajapura,Ta-Halol,Dist-Panchmahal |  |  | 2024-02-28 | NFHO | [5 empty] | As per the primary investigation the LT line passing from the farm of Shri Vikrambhai chaganbhai ahir was broken suddenly. Fencing of two Wire zhatka machine was done around this farm. Broken LT conductor touched this fencing wire. The victim was working near this fencing wire on the other side of the farm . The victim came in contact with this fencing wire with the right knee and got electric shock. The victim was taken to a nearby hospital and discharged after treatment. | Awaited | NA | NA | OPEN CONDUCTOR IS REPLACED BY LT ABC EARTHING OF PSC POLE WITH PVC PIPE DONE | Godhra
188 | BUFFALO,Segva-Malpur Road,Vill-Malpur,Ta-Sinor,Dist-Vadodara |  |  | 2024-02-29 | FA | [5 empty] | The Buffalo is laying in field with in contact of HT wire around body of buffalo which was broken from one end of span. | Awaited | NA | NA | conuctor rejoint work done. | Baroda O&M
189 | PRATHVIRAJBHAI LILESHBHAI DAHMA,Vill-Kaliyawad,Ta-Dhanpur,Dist-Dahod |  |  | 2024-02-29 | NFHO | [5 empty] | VICTIM CONTACT WITH 11KV DODP AND HT ABC CABLE EARTHING WIRE AND ELECTROCUTION BY LEAKAGE CURRENT | Awaited | NA | NA | Earthing Wire Disconnected With HT ABC Earthing Strip And Leakage Current Flow Stop And Unbundling Of HT ABC | Godhra
190 | Mohmad Yusuf lasi Mohmmad vani<near Nyra Petrolpump,Vill-Sankheda,Ta/Dist-Vadodara |  |  | 2024-03-01 | FHO | [5 empty] | From CCTV footage it is observed that container coming from wrong side and parked under 11kv HT line looking around and immediaely climbed upon the roof of container again without looking around he bend over and walk upright,with the help of mobile battery he was trying to search something on the roof,as soon as he start walking and go ahead few steps he came in contact with live 11 kv line of Bharat Chemical Feeder eminating from 66KV Nandesari S/s.Near NAyra Petrol Pump which is not functioni | Awaited | NA | NA | V-Cross Extention provided to Maintain Clearance for avoid Accident . | Baroda(O&M)
191 | NARPATBHAI G. BARIYA (ALM), Vill-Moti Rasli, Tal-Jetpur Pavi, Dist-C'udepur |  |  | 2024-03-01 | NFHD | [5 empty] | THE VICTIM SH. NARPATBHAI G. BARIYA (ALM) WAS CARRYING OUT THE WORK OF HT LINE RE JUMPERING ON 11 KV PAVI JETPUR JGY FEEDER AT AB SWITCH LOC. NO. PJR/JGY/52 AFTER TAKING LCP & EARTHING AT THE LOCATION. WHILE WORKING, THE VICTIM GOT ELECTRIC SHOCK & FELL DOWN ON GROUND. THE VICTIM WAS IMMEDIATELY MOVED TO NEARBY HOSPITAL IN OFFICE VEHICLE. AS ASSURED BY THE DOCTOR THE CONDITION OF VICTIM IS NOW STABLE. | Awaited | NA | NA | In the safety meeting conducted with line staff at sub division office post the said non fatal departmental human electrical accident was discussed in detail at length with all the present staff and the staff was made aware and strictly instructed to be thorough and vigilant while working on line and due earthing is to be done on both sides before commencement of the work. | Baroda(O&M)
192 | Buffalo of Dilipsinh Dhulabhai Chauhan,Purshottam nagar,Vill-Modaj,Ta-Memdabad,Dist-Kheda |  |  | 2024-03-02 | FA | [5 empty] | The Buffalo was tied to the front of the house with wooden nails at shri. Dilipsinh Dhulabhai Chauhan's farm. on dtd. 02.03.2024 due to heavy rain and wind started in the evening, buffalo was scared and started running around in the farm. the buffalo suddenly fell down when running between transformer centre psc pole. when shri. dilipsinh dhulabhai chauhan felt that his son harpal who was running behind the buffalo was electrocuted, he put the tester on the buffalo and the tester recieved electr | Awaited | NA | NA | To Prevent More Casualties Line Clear Taken Of 11 Kv Kuna Ag Fdr And Jumper Cut After Accident To Stop Supply To This Transformer | Nadiad
193 | Solanki Suryaben Manharsinh,Vill-Bhakhrani Muvadi,Ta-Kalol,Dist-Panchmahal |  |  | 2024-03-16 | NFHO | [5 empty] | TOUCH 11KV LINE ON ROOF TOP OF VICTIM HOUSE AND ELECTRODUCED | Awaited | NA | NA | NOTICE ISSUED TO VICTIM | Godhra
194 | Sunilbhai surpanbhai Pargi,Vill-Karodia,Ta-Fatepura,Dist-Dahod |  |  | 2024-03-17 | NFHO | [5 empty] | The line shifting work was carried out by the contractor person. Under the supervision of line inspector and Line man he take Line Clear of 11 KV Fatepura JGY feeder at 11:35 hrs and cut the nearby switch and earthed it and then instruct contractor supervisor to start the work. The victim and another contractor person were working on the Fatepura JGY feeder HT PSC pole at around 12:10 hrs when the victim was pin binding on the top phase of the HT extension, the power suddenly came on and they | Awaited | NA | NA | Staff Have Been Instructed To Not Allow Persons Working Under Them To Start Work Without Making Power Off And Other Safety Precautions Taken. | Godhra
195 | ZALA DALPATBHAI KARANSINH,Vill-Dudhathal,Ta-Kapadwanj,Dist-Kheda |  |  | 2024-03-17 | FHO | [5 empty] | On dated 17.03.2024 around 08.00 A.M. Person of unstable mind who's name is Shree Dalpatbhai Karansinh Zala(From village Reliya)Suddenly climed up Tc structure of3 ph ag cooncetion of shri Rajeshbhai Shnatilal Patel (Which is located at sim vistar of Dudhathal Village)and got elecrocuted and died. | Awaited | NA | NA | Maintenace was done and power supply restored | Nadiad
196 | BUFFALO,Muvadi faliyu, Vill-Paroli, Tal-Ghoghamba, Dist-Panchmahal |  |  | 2024-03-24 | FA | [5 empty] | CAME IN CONTACT WITH EARTHING WIRE OF POLE | Awaited | NA | NA | LT ABC RECTIFIED EARTHING WITH PVC PIPE DONE | Godhra

## MG SoP 03
Name of Distribution Licensee: M G V C L
Annual
Year: 2023-24
REGISTER FOR COMPILING THE COMPLAINTS CLASSIFICATIONWISE FY 2023-24
Performa SoP 003 B: |  |  |  | APPENDIX-B (already in the SoP regulation)
Classification | Nature of Complaints | Pending complaints of previous qtr. | Complaints received during the qtr. | Total Complaints =2+3 | No. of Complaints redressed during the quarter. |  |  |  |  | Balance Complaints to be redressed. (4) – (9)
[5 empty] | In stipulated time |  | Beyond stipulated time |  | Total (5) to (8)
[5 empty] | Within 50% of stipulated time. | Within stipulated time. | Up to double the stipulated time | More than double the stipulated time
| 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10
A(i) | Loose Connection | 0 | 353883.1823 | 353883.1823 | 160452.6334 | 193430.5489 | 0 | 0 | 353883.1823 | 0
A(ii) | Intruption due to line Break down | 0 | 222205.3129 | 222205.3129 | 100336.405 | 121868.9079 | 0 | 0 | 222205.3129 | 0
A(iii) | Intruption due to T/C Fail | 0 | 24841.6104 | 24841.6104 | 12163.9578 | 12677.6526 | 0 | 0 | 24841.6104 | 0
B(i) | Quality of power supply,ordinary case which require no Augmentation | 0 | 31032.1881 | 31032.1881 | 21361.3071 | 9670.881 | 0 | 0 | 31032.1881 | 0
B(ii) | Quality of power supply,ordinary case which require Augmentation | 0 | 18908.6142 | 18908.6142 | 11388.0441 | 7520.5701 | 0 | 0 | 18908.6142 | 0
C(i) | Meters- Stoped/Defective meter | 0 | 58601.4012 | 58601.4012 | 37402.4683 | 21198.9328 | 0 | 0 | 58601.4012 | 0
C(ii) | Meters- Billing on average basis for > two bills | 0 | 23065.9942 | 23065.9942 | 14200.7466 | 8865.2476 | 0 | 0 | 23065.9942 | 0
D(i) | Over head lines - loose wires | 0 | 19468.5854 | 19468.5854 | 12238.023 | 7230.5624 | 0 | 0 | 19468.5854 | 0
D(ii) | Over head lines - in adiquate ground clearance | 0 | 6856.4971 | 6856.4971 | 5044.2073 | 1812.2898 | 0 | 0 | 6856.4971 | 0
E(i) | Bills- for current bills where no addl information required | 0 | 22561.6833 | 22561.6833 | 16276.2319 | 6285.4514 | 0 | 0 | 22561.6833 | 0
E(ii) | Bills- for current bills where addl information required | 0 | 13317.19 | 13317.19 | 8016.2265 | 5300.9635 | 0 | 0 | 13317.19 | 0
F(i) | Service connections- where extention of mains is not required | 0 | 36471.4722 | 36471.4722 | 25648.9386 | 10822.5336 | 0 | 0 | 36471.4722 | 0
F(ii) | Service connections- where extention of mains is required | 0 | 15224.3493 | 15224.3493 | 9476.0299 | 5748.3194 | 0 | 0 | 15224.3493 | 0
F(iii) | Service connections- Modification in connected load | 0 | 10995.5355 | 10995.5355 | 5521.172 | 5474.3635 | 0 | 0 | 10995.5355 | 0
F(iv) | Service connections- Name change/reconnection | 0 | 15117.7985 | 15117.7985 | 8559.8484 | 6557.9501 | 0 | 0 | 15117.7985 | 0
G | Refund of amount due inregard to temp conn | 0 | 2232.3013 | 2232.3013 | 1276.1109 | 956.3904 | 0 | 0 | 2232.5013 | -0.2
H | Others | 0 | 102786.2841 | 102786.2841 | 54150.7083 | 48635.5758 | 0 | 0 | 102786.2841 | 0
| TOTAL | 0 | 977570 | 977570 | 503513.0591 | 474057.1409 | 0 | 0 | 977570.2 | -0.2

## MG SoP 04
Name of Distribution Licensee: M G V C L
Annual
Year 2023-24
Performa SoP 002 : Publicity carried out while displaying the contact details of consumer complaints centers
Particulars should also cover the details of consumer awareness program conducted, advertisement done through various media like TV, newspaper, radio, pamphlets & booklet distributions, Displays etc. The development of website and any medium through which public education is carried out can be included.
Sr. No | Actions or steps carried out by distribution licensee towards public awareness in the quarter | Likely number of consumers influenced
1 | RTI Officers Name is displayed at customer care centre on each office | 14153079
2 | Necessary information regarding time schedule for new connection and solving complaints is display on the board. | 14153079
3 | Contact nos. of various officers of the company for emergency contact is also displayed at customer care centre. | 14153079
4 | Displayed safety posters at various S/dn,Divisions | 15047
5 | Safety Meeting with Line Staff at various S/dn,Divisions on Every Monday (Line staff influenced) | 11092

## SOP-05
Name of Distribution Licensee: M G V C L
Annual
Year :2023-24
Performa – SoP 005 B: Action taken report by the Redressal Committee
Sr. No | Month | Name of Office | Date and Time Meeting conducted | No of complaints registered at the meeting | No. of complaints pending at the end of the meeting
1 | 1st Month of the quarter (APRIL-23) | Cororate Office | 27.04.23 11:30 AM at corporate office vadodara | 1 | 0
|  | Godhra C.O. | NIL | 0 | 0
2 | 2nd Month of the quarter (MAY23) | Cororate Office | 25.05.23 11:30 AM at corporate office vadodara | 3 | 0
|  | Godhra C.O. | 06.05.23 11:30 AM at Godhra Circle Office Godhra. | 1 | 0
3 | 3rd Month of the quarter (JUNE23) | Cororate Office | 26.06.23 11:30 AM at corporate office vadodara | 3 | ***2
|  | Godhra C.O. | NIL | 0 | 0
4 | 1st Month of the quarter (JULY-23) | Cororate Office | 25.07.23 11:30 AM at corporate office vadodara | 2 | 0
|  | Godhra C.O. | NIL | 0 | 0
5 | 2nd Month of the quarter (AUGUST-23) | Cororate Office | 25.08.23 11:30 AM at corporate office vadodara | 5 | 0
|  | Godhra C.O. | NIL | 0 | 0
6 | 3rd Month of the quarter (SEPTEMBER-23) | Cororate Office | 26.09.23 11:30 AM at corporate office vadodara | 4 | 0
|  | Godhra C.O. | 16.09.23 11:30 AM at Godhra circle office Godhra | 2 | 0
7 | 1st Month of the quarter (OCT-23) | Corporate Office | 26.10.23 11:30 AM at corporate office vadodara | 4 | 0
|  | Godhra C.O. | NIL | 0 | 0
8 | 2nd Month of the quarter (NOV-23) | Corporate Office | NIL | 0 | 0
|  | Godhra C.O. | NIL | 0 | 0
9 | 3rd Month of the quarter (DEC-23) | Corporate Office | 28.12.23 11:30 AM at corporate office vadodara | 4 | 1 Consumer not Present
|  | Godhra C.O. | 16.12.23 & 30.12.23 11:30 AM at Godhra circle office Godhra | 11 | 6
10 | 1st Month of the quarter (JAN-24) | Corporate Office | 24.01.24 11:15 AM at corporate office vadodara | 4 | **2 Nos. complainant has asked adjournment
|  | Godhra C.O. | 06/01/24 & 20/01/24 11.30 AM at Godhra Circle Office | 7 | 7
11 | 2nd Month of the quarter (FEB-24) | Corporate Office | NIL | 0 | **2 Nos. complainant has asked adjournment
|  | Godhra C.O. | 03/02/24, 17/02/24 & 21/02/24 11.30 AM at Godhra Circle Office | 10 | 9
12 | 3rd Month of the quarter (MAR-24) | Corporate Office | 27.03.24 11:30 AM at corporate office vadodara | 6 | 0
|  | Godhra C.O. | 06/03/24, 16/03/24,19/03/24 & 30/03/24 11.30 AM at Godhra Circle Office | 9 | **1 Applicant was absent

## MG SoP -06
Name of Distribution Licensee: M G V C L
Financial Year: 2023-24
Annual
Performa SoP 006: Failure of Distribution Transformer
Sr. No. | Name of Circle | Nos. of existing Distribution Transformers at the start of the quarter | Nos. of Distribution Transformers added during the quarter | Total number of Distribution Transformers on end of quarter | Total number of Distribution transformer failed during quarter | % failure rate of Distribution transformer
|  | A | B | C=A+B | D | H = (D)*100/C
1 | Baroda O&M | 56779 | 1711 | 58490 | 3468 | 5.9292
2 | Baroda City | 9503 | 966 | 10469 | 75 | 0.7164
3 | Anand | 25316 | 1484 | 26800 | 924 | 3.4478
4 | Nadiad | 32905 | 1592 | 34497 | 1466 | 4.2496
5 | Godhra | 61887 | 37 | 61924 | 4516 | 7.2928
| MGVCL | 186390 | 5790 | 192180 | 10449 | 5.4371

## SoP008
Name of Distribution Licensee: M G V C L
Annual
Year: 2023-24
Performa SoP 008: Sample Test result for Neutral Voltage
Compliance Sample Test Report for Neutral Voltage
-1 | -2 | -3 | -4 | -5 | -6
Sr. No | Category of consumers | Sample Size | Standard specified in regulation | Deviation of results from the sample test (Numbers) | % age compliance
|  | (Numbers) |  |  | (6) = (5)*100/(3)
| LT consumers | 5764 | 2% | 0 | 0
1 | Domestic | 4092 | 2% | 0 | 0
2 | Commercial | 968 | 2% | 0 | 0
3 | Industrial | 92 | 2% | 0 | 0
4 | Agricultural | 572 | 2% | 0 | 0
5 | Public water works | 40 | 2% | 0 | 0
| HT consumers | 0 | 2%
6 | HT industrial | 20 | 2% | 0 | 0

## SoP009
Name of Distribution Licensee: M G V C L
Annual
Year: 2023-24
Performa SoP 009: Sample Test result for Voltage variations
Compliance Sample Test Report for voltage variations
-1 | -2 | -3 | -4 | -5
Voltage Level | Sample Size (numbers) | Limit or prescribed standard | Deviation of results from the sample test (Numbers) | % age compliance
(5) = (4)*100/(2)
Low Voltage | 224 | +6% to -6% | 0 | 0
High Voltage | 96 | +6% to -9% | 0 | 0
Extra High Voltage | 4 | +10% to -12.50% | 0 | 0

## SoP010
Name of Distribution Licensee: M G V C L
Annual
Year: 2023-24
Performa SoP 010: Sample Test result for Harmonics
Compliance Sample Test Report for Harmonics
-1 | -2 | -3 | -4 | -5 | -6
Sr. No | Category of consumers | Sample size (Numbers) | Limit or standard prescribed | Deviation of results from the sample test (Numbers) | %age compliance
(6) = (5)*100/(3)
1 | LT consumers | 132 | 3.5% | 0 | 0
2 | HT consumers | 16 | 3% | 0 | 0
3 | EHT consumers | 4 | 3% | 0 | 0
Note: The licensee shall also submit along with the above harmonic data, the records of customer wise drawls of harmonic currents measured at various strategic points.
The formats SoP 008, SoP 009 and SoP 010 have to be sent annually.
For the purpose of annual submissions, the year end has to be considered as the end of December month of a particular year.

## 11A
Annual
Year: 2023-24
SoP 011 –A: System Average Interruption Frequency Index (SAIFI)
Sr. No | Month | Ni - Total no of customers for each momentary interruptions | NT - Total no of customers served |  |  | Past year corrosponding Month
1 | 2 | 3 | 4 | 5 | 6=5/4
1 | April' 23 | 3150519 | 3487488 | 9352346 | 2.6817 | 2.32
2 | May' 23 | 3303725 | 3488823 | 15374696 | 4.4068 | 3.74
3 | June' 23 | 3367367 | 3497411 | 32258711 | 9.2236 | 4.88
1 | July' 23 | 3310911 | 3506961 | 23060758 | 6.5757 | 5.9
2 | Aug' 23 | 3197040 | 3483209 | 15232925 | 4.3732 | 4.4
3 | Sep' 23 | 3293122 | 3523731 | 25385368 | 7.2041 | 4.59
1 | Oct' 23 | 3333120 | 3531569 | 13466304 | 3.8131 | 3.28
2 | Nov' 23 | 3242236 | 3542129 | 12933304 | 3.6513 | 2.42
3 | Dec' 23 | 3279248 | 3550350 | 12096162 | 3.407 | 2.26
1 | Jan' 24 | 3371285 | 3558247 | 15152695 | 4.2585 | 3.21
2 | Feb'24 | 3311163 | 3567783 | 11877305 | 3.329 | 1.89
3 | Mar'24 | 3029664 | 3578282 | 18816339 | 5.2585 | 3.22
|  |  | 42315983 | 205006913 | 4.8447 | 2.7733

## 11B
Annual
Year: 2023-24
SoP 011 – B System Average Interruption Duration Index (SAIDI)
Sr. No | Month | ri = Restoration Time for each interruption event | Ni - no of interrupted customers for each sustained interruption event | ri * Ni – Total customer interruption Duration | ri=Restoration Time for each interruption event | Ni= No of Interrupted customers for each sustained Interruption | NT - Total no of customers served | Customer Interruption Duration |  |  | Past year corrosponding Months
[9 empty] | MINS. | HRS.
1 | 2 | 3 | 4 | 5= 3 X 4 | 3 | 4 | 5 | 6 | 7=4/3 | 7A | MINS. | HRS.
1 | April' 23 | July |  |  | 616755 | 3150519 | 3487488 | 822074405 | 235.7211 | 3:56 | 181 | 3:01
2 | May' 23 | August |  |  | 972655 | 3303725 | 3488823 | 1255184194 | 359.773 | 6:00 | 385 | 6:25
3 | June' 23 |  |  |  | 1894299 | 3367367 | 3497411 | 2161775562 | 618.1074 | 10:18 | 413 | 6:53
1 | July' 23 | July |  |  | 3310911 | 3506961 | 3506961 | 1362751258 | 388.5847 | 6:29 | 351 | 5:51
2 | Aug' 23 | August |  |  | 3197040 | 3483209 | 3483209 | 967193886 | 277.6732 | 4:38 | 253 | 4:13
3 | Sep' 23 |  |  |  | 3293122 | 3523731 | 3523731 | 1620159863 | 459.7853 | 7:40 | 325 | 5:25
1 | Oct' 23 | July |  |  | 1033890 | 3333120 | 3531569 | 1410609067 | 399.4284 | 6:39 | 233 | 3:53
2 | Nov' 23 | August |  |  | 730835 | 3242236 | 3542129 | 910569288 | 257.0684 | 4:17 | 227 | 3:47
3 | Dec' 23 |  |  |  | 744226 | 3279248 | 3550350 | 908423495 | 255.8687 | 4:16 | 196 | 3:16
1 | Jan' 24 | July |  |  | 781472 | 3371285 | 3558247 | 1039643166 | 292.1785 | 4:52 | 271 | 4:31
2 | Feb'24 | August |  |  | 586570 | 3311163 | 3567783 | 765209787 | 214.4777 | 3:34 | 178 | 2:58
3 | Mar'24 |  |  |  | 543886 | 3029664 | 3578282 | 610171248 | 170.5207 | 2:51 | 170 | 2:50
[6 empty] | 39902228 | 42315983 | 13833765219 | 326.9158 | 5:27 | 206.3333 | 3:26

## 11C
Annual
Year: 2023-24
SoP 011 – C: Momentary Average Interruption Frequency Index (MAIFI)
Sr. No | Month | Number of Momentary interruptions Imi | Nmi - Total no of customers for each momentary interruptions | NT - Total no of customers served |  |  | Past year corrosponding Month
1 | 2 | 3 | 4 | 5 | 6 | 7
1 | April' 23 | 19548 | 2917572 | 3487488 | 31721246 | 9.0957 | 8.11
2 | May' 23 | 22548 | 2984391 | 3488823 | 34594398 | 9.9158 | 8.87
3 | June' 23 | 47873 | 3201236 | 3497411 | 77273633 | 22.0945 | 9.77
1 | July' 23 | 40243 | 3136591 | 3506961 | 66248720 | 18.8906 | 12.28
2 | Aug' 23 | 33467 | 2992170 | 3483209 | 52078356 | 14.9513 | 11.07
3 | Sep' 23 | 38505 | 3128098 | 3523731 | 62499748 | 17.7368 | 10.26
1 | Oct' 23 | 33152 | 3078284 | 3531569 | 47235426 | 13.3752 | 10.29
2 | Nov' 23 | 33176 | 3004686 | 3542129 | 47517870 | 13.4151 | 8.53
3 | Dec' 23 | 30978 | 3059259 | 3550350 | 43342505 | 12.208 | 8.07
1 | Jan' 24 | 34827 | 3217969 | 3558247 | 55180485 | 15.5078 | 10.37
2 | Feb'24 | 28565 | 3039745 | 3567783 | 38295093 | 10.7336 | 6.64
3 | Mar'24 | 37574 | 2888760 | 3578282 | 51804906 | 14.4776 | 11.29
|  |  |  | 42315983 | 607792386 | 14.3632 | 9.4333

## MG SoP - 13
Name of Distribution Licensee: M G V C L
Financial Year: 2023-24
Annual
Performa SoP 013: Faulty Meters Replacement
Consumer Category | No. of faulty meters at the start of the quarter | No. of faulty meters added during the quarter | Total no. of defective / faulty Meter | No. of faulty Meters repaired and replaced | No of faulty meters pending at the end of the quarter | Remark
| 1 | 2 | (3)=(2)+(1) | 4 | (5)=(3)-(4)
1 PHASE
MGVCL | 10105 | 121967 | 132072 | 121959 | 10113
3 PHASE |  |  |  |  | 0
MGVCL | 3802 | 23216 | 27018 | 23514 | 3504

## SoP_15
Performa SoP 015: Release of New Connection status for FY 2023-24
Qtr | Consumer category | Total no. of consumers connected at the beginning of half-year/year | Pending at the Beginning of the of the Half year/year | New Applications received during the half-year / year | No. of connections released during the half-year / year | No. of applications pending at the end of half-year / year | Total no. of consumers connected at the end of half-year/year
Annual 2023-24 | Domestic | 2845327 | 1304 | 75468 | 76437 | 335 | 2910777
| Commercial (NRGP_C+LTMD_C) | 331866 | 304 | 19662 | 19815 | 151 | 342405
| Industrial LT (NRGP_L+LTMD_L) | 40602 | 164 | 1798 | 1939 | 23 | 41048
| Agriculture (Total) | 190931 | 8099 | 11755 | 13611 | 8044 | 204542
| Industrial HT | 2869 | 64 | 307 | 291 | 70 | 3155
| Total | 3411595 | 9935 | 108990 | 112093 | 8623 | 3501927

## MG SoP 16
Name of Distribution Licensee: M G V C L
Annual
Year: 2023-24
Performa SoP 016: Compensation details
COMPENSATION DETAILS
Sr.No. | Event | Compensation | No of cases where compensation was given (in numbers) | Amt of compensation paid (in Rs.)
1 | Duty to provide supply | Rs. 50 per day of delay from the limit specified in the performance regulations | 0 | 0
| a) New Connection |  | 0 | 0
| b) Additional Load |  | 0 | 0
| c) Temporary supply |  | 0 | 0
| d) Shifting service connection |  | 0 | 0
| e)Transfer of service connection |  | 0 | 0
| f) Change in tariff category of consumer |  | 0 | 0
2 | Complaints in billing | Rs. 50 for non reply within the period prescribed in Regulations | 0 | 0
3 | Replacement of meters | LT- Rs. 25 per day of delay - maximum Rs.2,500 and HT - Rs. 250 per day of delay - maximum of Rs.5,000 | 0 | 0
4 | Interruption of supply | LT- Rs. 25 for every 6 hrs of delay- maximum of Rs. 500 and HT- Rs. 50 for every 6 hrs delay- maximum Rs. 1000/- | 0 | 0
5 | Voltage fluctuations and complaints | Rs. 50 for failure to visit or convey findings within the stipulated period | 0 | 0
6 | Responding to consumer's complaints | Rs. 25 for each day of delay- maximum Rs. 500 | 0 | 0
7 | Grievance Handling | Rs.25 for failure in handling grievance | 0 | 0
TOTAL |  |  | 0 | 0