## MG COVER PAGE
Name of Distribution Licensee: M G V C L
Quarter : Q-IV (Jan-Feb-March- 2024)
Year: 2023-24

## MG SoP 01
Name of Distribution Licensee: M G V C L
Quarter IV (Jan-24 to March-24)
Year:2023-24
Performa - SoP 001: Fatal and Non-Fatal electrical accident report
NUMBER OF ACCIDENTS FOR THE 4th QUARTER OF 2023-24
Sr. No | Name of Area/Circle | No of accidents in the quarter |  |  |  |  | Cumulative since the first quarter of the current FY 2023-24 |  |  | Cumulative since the first quarter of the Last FY 2022-23
|  | Departmental |  | Outside |  |  | TOTAL |  |  | TOTAL
|  | FH | NFH | FH | FA | NFH | FH | FA | NFH | FH | FA | NFH
1 | Baroda (City) | 0 | 0 | 2 | 0 | 0 | 8 (3-Pvt) | 2 | 1 | 1 | 0 | 3
2 | Baroda (O&M) | 0 | 1 | 2 | 1 | 1 | 11 | 23 (1-Pvt) | 9 | 12 (1-Pvt) | 19 | 11
3 | Anand | 0 | 0 | 1 | 0 | 1 | 12 (3-Pvt) | 13 | 4 | 3 | 5 | 2
4 | Godhra | 0 | 2 | 5(1-Pvt) | 2 | 5 | 21 (6-Pvt) | 44 (1-Pvt) | 10 | 17 (9-Pvt) | 25 (2-Pvt) | 9
5 | Nadiad | 0 | 0 | 4 | 1 | 1 | 11 (1-Pvt) | 20 | 7 | 11 (2-Pvt) | 23 | 11
| TOTAL | 0 | 3 | 14(1-Pvt) | 4 | 8 | 63 (13-Pvt) | 102 (2-Pvt) | 31 | 44 (12-Pvt) | 72 (2-Pvt) | 36
FH – Fatal Human, FA – Fatal Animal, NFH – Non-fatal Human | [5 empty] | 29 |  |  | 196 |  |  | 152
PVT - Private Premises Accident.

## SoP 002
Performa – SoP 003: Action taken report for safety measures complied for the electrical accidents occurred
ACTION TAKEN REPORT FOR SAFETY MEASURES COMPLIED FOR THE ELECTRICAL ACCIDENTS OCCURED IN THE FOURTH QUARTER OF FY 2022-23
1 | 2 |  |  | 3 | 4 |  |  | 5 | 6 | 7 | 8 | 9 | 10
Sr. No | Location of Accident and details of the victim | Address | sdn | Date of occurrence | Type of Accident | Installation | Accident Type | Cause of Accident | Findings of CEI / EI / AEI | Remedies suggested by CEI /EI / AEI in various cases | Whether the remedy suggested is complied | Action taken to avoid recurrence of such Accident | Circle office | Reason
1 | Suraj Hirubhai Meda,Smashan Road,Vill-Dahod,Ta-Dahod,Dist-Dahod |  |  | 2024-01-01 | FHO |  |  | VICTIM MAY BE PUT HIS HAND IN THE LT DISTRIBUTION BOX AND GOT SHOCKED AND DIED ON THE SPOT | Awaited | NA | NA | The accident is suicidal/intentional, the victim has intentionally put his hand into distribution box. | Godhra | 6
2 | Pagi Pankajbhai Arjanbhai,Zarakhala Faliyu,Vill-Kolvan,Ta-Lunawada,Dist-Mahisagar |  |  | 2024-01-02 | FHO-Pvt |  |  | While Site Visiting It Is Found That , On That Location As per the information received from Sarpanchshri kolvan at Zarkhala faliya a fatal and non fatal accident occured to Shri Pagi Pankajbhai Arjanbhai and Pagi Arjanbhai Ramabhai. Whenever Pagi Pankajbhai Arjanbhai was repair fuse board in his AG connection room during the repairing of the fuse board at that time he was suddenly contact with live fuse wire and electrocuted. He was loudly shrick and at that time his father Pagi Arjanbhai Ramabhai | Awaited | NA | NA | due to negligance of victim | Godhra | 8
3 | Bullock,Nishal Faliya,Vill-Kotara,Ta-Santrampur,Dist-Mahisagar |  |  | 2024-01-03 | FA |  |  | As per Site Visit and Eye Witness Statement at the said location Shardaben Savjibhai Tadvi Eye Witness was grazing her Cattles at the top of the hill. Meanwhile strong wind was also blowing and due to that the HT Conductor of nearby passing line of 11 KV Simaliya AG Feeder broken down and fell on one of the bullock. This ultimately results in electrocution of the bullock and another bullock gets electrocuted due to potential gradient created nearby it. | Awaited | NA | NA | Broken conductor repair and necessary maintenance carried out for avoid accident. | Godhra | 1
4 | Mr Piyush Chauhan,Jay Ambe Nagar,Vill-Vadodara,Ta-Vadodara,Dist-Vadodara |  |  | 2024-01-06 | FHO |  |  | Victim met accident while flyig kite on the roof of his house , moved to hospital through 108 on dt.06.01.2024 at time 3:30 approx. & found dead. | Victim meet accident by completing circuit between roof ( iron) & nearby passing street light earthing wire as there is leakage current coming from fan hang on iron rod under iron roof without any insulation between them. Also found that polarity is reversed in the said house switchboard .i.e. phase is always ON in switch ON & OFF both condition. | Installation of RCCB is important to avoid such accident |  | Advised to remove such structure ( IRON ROOF supported by IRON ROD & Electrical equipment hang on IT) | Baroda City | 8
5 | Alpesh Bipinbhai Vagela,Kheda Faliya,Vill-Vagela,Ta-Zalod,Dist-Dahod |  |  | 2024-01-08 | NFHD |  |  | AS PER INVESTIGATION AND INFORMATION RECEIVED, VICTIM WAS ATTENDING LT LINE COMPLAIN,POWER MADE OF TRANSFORMER BY DOING PHASE WIRE CUT IN DISTRIBUTION BOX THEN AFTER VICTIM CLIMBED ON LT LINE POLE, HE TOUCHES LT NUETRAL WIRE AND ELECTROCUTED AND HE LOST HIS BALANCE AND SLIPPED FROM LT POLE AND INJURED ON BACKSIDE OF HEAD AND LEFT HAND PALM. | Awaited | NA | NA | LT LINE ONE CONDUCTOR SLIPPED FROM LT SHACKLE INSULATOR IS RECTIFIED AND LT LINE PATROLLING DONE ALSO FUSE OF TRANSFORMER LT DISTRIBUTION BOX REPLACED AND NEW EARTHING DONE | Godhra | 4
6 | Mudasir Abdulkayum Parey (FHO), Manzoorul Hamid (NFHO),B/H Goodluck Hotel,Vill-Hariyala,Ta-Kheda,Dist-Kheda |  |  | 2024-01-12 | FHO |  |  | THE TRUCK DRIVER WAS DRIVING TRUCK ON ROAD PASSING THTOUGH FARMS. THE EXTENDED HOOK CAME IN CONTACT WITH LIVE 11 KV CONDUCTOR. THE CLEANER WAS ELECTROCUTED AND DIED ON THE SPOT. WHILE DRIVER WAS GOT BURNT AND SHIFTER TO KHEDA CIVIL HOSPITAL FOR MORE TREATMENTS. | Awaited | NA | NA | To Increase The Height Of Line Two PSC Pole Below The Line And On Both Side Of Elevated RCC Road Has Been Proposed. | Nadiad | 2
7 | Smt Januben Haribhai Bharvad,Near Mahadev Faliyu,Vill-Valotri,Ta-Matar,Dist-Kheda |  |  | 2024-01-13 | FHO |  |  | AT VILLAGE VALOTRI THE VICTIM SMT JANUBEN HARIBHAI BHARVAD WAS PASSING FROM NEAR TO MAHADEV FALIYA FOR WASTE DISPOSAL AND SUDDENLY 11 KV HADEVA JGY FEEDER ONE CONDUCTOR IS BROKEN DUE TO KITE FESTIVAL KITE THREAD AND FALL ON VICTIM AND SHE GOT ELECTRIC SHOCKED.SHE IS SHIFTED IMMEDIATLY TO HOSPITAL FOR FURTHER TREATMENT. | Awaited | NA | NA | Maintenace was done and power supply restored | Nadiad | 1
8 | Dangi Siddharthkumar Virsingbhai,Vill-Katholiya,Ta-Limkheda,Dist-Dahod |  |  | 2024-01-14 | FHO |  |  | ACCORDING TO EYEWITNESS STATEMENT ON DTD 14-01-2024 AROUND 09:15 AM VICTIM WAS FLYING KITE ON THE GROUND IN THE FARMLAND OF DANGI MALABHAI DITABHAI WITH NO NEARBY HOUSEHOLD OR ANY OTHER TYPE OF STRUCTURE.11 KV MATWA AG FEEDER HT LINE WAS PASSING NEARBY FARMLAND.DUE TO DEW AND FOG THE FARMLAND WAS WET.WHILE FLYING THE KITE WITH A WHITE COTTON THREAD WHICH WAS ALSO WET DUE TO FOG AND DEW, THEKITE GOT STRUCK IN THE HT LINE AND WHILE REMOVING THE KITE WITH THE HELP OF THE WET THREAD AS PER EYEWITNES | Awaited | NA | NA | The accident was occurred due to climatic condition.i.e. fog and dew. | Godhra | 8
9 | Nayak Kishanbhai Rangitbhai,Thori Vas Sati Talavdi Halol,Vill-Halol,Ta-Halol,Dist-Panchmahal |  |  | 2024-01-16 | NFHO |  |  | ACCORDING TO INVESTIGATION REPORT, AROUND 02:00 PM SHRI KISHANBHAI RANGITBHAI NAYAK WAS CLIMBED ON ROOF OF SHACK WHICH WAS MADE BESIDE HIS HOUSE,THE TOP OF WHICH WAS MADE OF METAL SHEET APPROX 06 FOOT ABOVE THE GROUND. 11 K.V LINE OF SHUBHAM URBAN FDR IS PASSING JUST BESIDE THIS SHACK. AS PER EYE WITNESS STATEMENT, THE VICTIM CLIMBED ON THIS SHACK ROOF FOR KITE CATCHING PURPOSE HOLDING A METAL ROD OF APPROX 09 FOOT LENGTH,THE KITE WAS HANGING ON 11 K.V O/H LINE OF SHUBHAM FDR SO THE VICTIM TRIED | Awaited | NA | NA | NOTICE ISSUED TO VICTIM FOR ILLEGAL CONSTRUCTION | Godhra | 2
10 | Chavad Dalpatbhai Ratilal,Near New Dudh Dairy,Vill-Dhundhaliya,Ta-Balasinor,Dist-Mahisagar |  |  | 2024-01-18 | NFHO |  |  | Painting work executed by victim with the help of extended paint roller on the terrace of New Dairy building which has constructed under the 11 KV Kambopa ag feeder line. During painting work, victim came in contact with live 11 KV feeder line conductor and he had electrocuted. | Awaited | NA | NA | Notice is issued to owner of building not to carried out construction work under line | Nadiad | 2
11 | Gelot Vishalbhai Punamchandbhai,Vill-Kanthaghar,Ta-Fatepura,Dist-Dahod |  |  | 2024-01-20 | FHO |  |  | Huge mounds of soil have been erected illegally under 11 KV Afwa JGY line at Village Kanthagar Brickyard. According to an eyewitness statement, the victim was working in a brickyard and while talking on a mobile phone, he suddenly stepped on a pile of soil and unfortunately came in contact with an electric wire. He was immediately rushed to a nearby hospital where he was declared Died. A Dark spot visible on 11 KV conductor. | Awaited | NA | NA | NOTICE GIVEN TO BRICKSYARD OWNER FOR REMOVE PILE OF SOIL ERECTED UNDER HT LINE | Godhra | 2
12 | Nakshkumar Kanjibhai Zala,Vill-Kathlal,Ta-Kathlal,Dist-Kheda |  |  | 2024-01-20 | FHO |  |  | Natubhai Udesinh Zala who planted brinjal in his farm at Fulavat Village: Khalal. To save their Brinjal crop, Fencing is done by erecting peices of wood and wire is wound. A LT line of Barmuvada Jgy is passing through his farm. from which thay had punctured the LT Abc 2 wire and connected it to the earthing of that LT Pole and connected to the fencing wire. Nakshkumar kanjibhai zala is playing around this fencing wire and Died on spot. | Awaited | NA | NA | LT Pole Earthing Is Dismentalled And LT Abc Cable Insulation Is Done With LT Insulator | Nadiad | 6
13 | Rajeshkumar (urfe Rajubhai) Ramanbhai pateliya,patel falia,Vill-Mahunala,Ta-Dhanpur,Dist-Dahod |  |  | 2024-01-26 | FHO |  |  | As per statement of ALM Shri RC rathod 2 nos of labor of contractor AK luhar had climbed the xmer structure to replace fail xmer without any intimation/instruction given by him and even before LC of 11kv line could be taken. 1 labor got electric shock and other fell down due to shock from tc structure .Shri Rajeshkumar pateliya after treatement at dahod zydus hospital and thereafter at godhra private hospital passed away on dtd 29.01.2024 so now it is reported as fatal | Awaited | NA | NA | Staff Have Been Instructed To Not Allow Persons Working Under Them To Start Work Without Making Power Off And Other Safety Precautions Taken. | Godhra | 3
14 | BHAILALBHAI SHANKARBHAI MACHHI,Vrajbhumi Socity,Vill-Vadodara,Ta-Vadodara,Dist-Vadodara |  |  | 2024-02-04 | FHO |  |  | FATAL HUMAN(OUTSIDER) ELECTRICAL ACCIDENT OCCURRED AT SECOND FLOOR TERRACE OF HOUSE NO.H/233,VRAJ BHUMI SOC. AS PER THE SITE PANCHANAMA IT IS CONCLUDED THAT VICTIM WAS CLIMBING ON SECOND FLOOR TERRACE FOR THE WORK OF SERIES LIGHT DECORATION DUE TO UPCOMING MARRIAGE FUNCTION ON DT.6.2.2024. DURING THE WORK VICTIM HAS THROWN ELECTRICAL WIRE ON HOUSE NO.H/233 ACCIDENTALLY PRIVATE ELECTRICAL WIRE ARE FALL DOWN ON 11KV OVERHEAD LIVE CONDUCTOR. AND VICTIM GOT ELECTRIC SHOCK,BLACK COLOR FLASH OBSERVED | Awaited | NA | NA | LETTER WRITTEN TO HOUSE OWNER FOR MAINTENING SAFE DISTANCE FROM HT LINE VIDE LETTER NO: SARDAR ESTATE/590, 07.02.24 | Baroda City | 2
15 | DEEPAKKUMAR KAMLESHBHAI CADI,Anand Nagar,Vill-Waghodia,Ta-Waghodia,Dist-Vadodara |  |  | 2024-02-10 | NFHO |  |  | ON DT:-10.02.2024, VICTIM CLIMBED ON THE ROOF(IRON SHEET)illegally constructed house under HT line of 11 KV Madodhar AG feeder of SHRI SIKANDARBHAI ISMAILBHAI QURESHI'S HOUSE WHERE HT LINE OF 11 KV MADODHAR FEEDER WAS PASSING, TRYING TO GET KITE STUCK ON HT LINE CONDUCTOR OF 11 KV MADODHAR AGDOM FEEDR AND GOT TOUCH WITH 11 KV LINE AND GOT ELECTROCUTED. FURTHER INVESTIGATION IS UNDER PROGRESS. | Awaited | NA | NA | Extention provided to Maintain Clearance for avoid Accident . | Baroda O&M | 2
16 | Shri Dalsukhbhai Mansukhbhai Parmar,Vill-Dabhasa,Ta-Padra,Dist-Vadodara |  |  | 2024-02-20 | FHO |  |  | On dtd 20.02.2024, After marriage ceremony, for dismantling the Mandap fabrication the Victim climbed on the iron ladder to remove the illegally constructed mandap in farm of Manojbhai Patel below 11KV Dabhasa Agdom feeder. While trying to dismantle fabricated horizontal support angle, this angle was accidentally touched to live HT line conductor of 11 KV Dabhasa Agdom feeder and got electrocuted. Further investigation is under process. | Awaited | NA | NA | accident occurred due to victim's negligency no any action required | Baroda O&M | 2
17 | BHAVSINGBHAI GAMIRBHAI BARIA,Vill-Gollav,Ta-Godhra,Dist-Panchmahal |  |  | 2024-02-22 | NFHD(Mech) |  |  | As per statement and information recieved from eye witness Shri Divyesh H. Patel sarsav JGY was in fault and victim Shri BG Baria Lineman has taken the line clear No. 020 at 13.00 for attending the feeder.In gentry there was Y and B jumper burn from sarsav JGY feeder and B G Bariya climb on gentry switch for rejumper work and due to unbalance of body he fell down from middle channel and mechanical injury happen on his head and face.Getting this information 108 ambulance was called and taken hi | Awaited | NA | NA | Staffs Have Been Instructed To work with Safety Precautions, in order to avoid such type of accidents. | Godhra | 7
18 | HITESHBHAI MUKESHBHAI RATHOD,Gokulpura Colony Vistar,Vill-Ambali,Ta-Anklav,Dist-Anand |  |  | 2024-02-23 | FHO |  |  | on dated 23.2. 2024 approx. 09.40 am, As per the statement of eyewitness Victim late. Shri Hiteshbhai Mukeshbhai Rathod, while taking the towel from the PSC pole after taking bath ,He might get electrocuted and stuck with GI wire (earthing of lt pole) due to lekage current in GI wire. | Awaited | NA | NA | LT ABC Provided | Anand | 2
19 | Mukeshbhai Bhanubhai Parmar,Gokulpura Colony Vistar,Vill-Betasi,Ta-Anklav,Dist-Anand |  |  | 2024-02-25 | NFHO |  |  | On dt 25.02.2025 time approx 17.30 Victim shri Maheshbhai Babubhai Parmar who is Mentally Unstable was walking near hanumanji temple and all of a sudden he climed TC Structure and touch to live 11 kv HT side Bushing of Transformer and got shocked and fell down on the road from TC Structure. | Awaited | NA | NA | Barbed wire provided | Anand | 2
20 | Smt Parulben maheshbhia jadav,Vill-Gajapura,Ta-Halol,Dist-Panchmahal |  |  | 2024-02-28 | NFHO |  |  | As per the primary investigation the LT line passing from the farm of Shri Vikrambhai chaganbhai ahir was broken suddenly. Fencing of two Wire zhatka machine was done around this farm. Broken LT conductor touched this fencing wire. The victim was working near this fencing wire on the other side of the farm . The victim came in contact with this fencing wire with the right knee and got electric shock. The victim was taken to a nearby hospital and discharged after treatment. | Awaited | NA | NA | OPEN CONDUCTOR IS REPLACED BY LT ABC EARTHING OF PSC POLE WITH PVC PIPE DONE | Godhra | 1
21 | BUFFALO,Segva-Malpur Road,Vill-Malpur,Ta-Sinor,Dist-Vadodara |  |  | 2024-02-29 | FA |  |  | The Buffalo is laying in field with in contact of HT wire around body of buffalo which was broken from one end of span. | Awaited | NA | NA | conuctor rejoint work done. | Baroda O&M | 1
22 | PRATHVIRAJBHAI LILESHBHAI DAHMA,Vill-Kaliyawad,Ta-Dhanpur,Dist-Dahod |  |  | 2024-02-29 | NFHO |  |  | VICTIM CONTACT WITH 11KV DODP AND HT ABC CABLE EARTHING WIRE AND ELECTROCUTION BY LEAKAGE CURRENT | Awaited | NA | NA | Earthing Wire Disconnected With HT ABC Earthing Strip And Leakage Current Flow Stop And Unbundling Of HT ABC | Godhra | 4
23 | Mohmad Yusuf lasi Mohmmad vani<near Nyra Petrolpump,Vill-Sankheda,Ta/Dist-Vadodara |  |  | 2024-03-01 | FHO |  |  | From CCTV footage it is observed that container coming from wrong side and parked under 11kv HT line looking around and immediaely climbed upon the roof of container again without looking around he bend over and walk upright,with the help of mobile battery he was trying to search something on the roof,as soon as he start walking and go ahead few steps he came in contact with live 11 kv line of Bharat Chemical Feeder eminating from 66KV Nandesari S/s.Near NAyra Petrol Pump which is not functioni | Awaited | NA | NA | V-Cross Extention provided to Maintain Clearance for avoid Accident . | Baroda(O&M) | 2
24 | NARPATBHAI G. BARIYA (ALM), Vill-Moti Rasli, Tal-Jetpur Pavi, Dist-C'udepur |  |  | 2024-03-01 | NFHD |  |  | THE VICTIM SH. NARPATBHAI G. BARIYA (ALM) WAS CARRYING OUT THE WORK OF HT LINE RE JUMPERING ON 11 KV PAVI JETPUR JGY FEEDER AT AB SWITCH LOC. NO. PJR/JGY/52 AFTER TAKING LCP & EARTHING AT THE LOCATION. WHILE WORKING, THE VICTIM GOT ELECTRIC SHOCK & FELL DOWN ON GROUND. THE VICTIM WAS IMMEDIATELY MOVED TO NEARBY HOSPITAL IN OFFICE VEHICLE. AS ASSURED BY THE DOCTOR THE CONDITION OF VICTIM IS NOW STABLE. | Awaited | NA | NA | In the safety meeting conducted with line staff at sub division office post the said non fatal departmental human electrical accident was discussed in detail at length with all the present staff and the staff was made aware and strictly instructed to be thorough and vigilant while working on line and due earthing is to be done on both sides before commencement of the work. | Baroda(O&M) | 3
25 | Buffalo of Dilipsinh Dhulabhai Chauhan,Purshottam nagar,Vill-Modaj,Ta-Memdabad,Dist-Kheda |  |  | 2024-03-02 | FA |  |  | The Buffalo was tied to the front of the house with wooden nails at shri. Dilipsinh Dhulabhai Chauhan's farm. on dtd. 02.03.2024 due to heavy rain and wind started in the evening, buffalo was scared and started running around in the farm. the buffalo suddenly fell down when running between transformer centre psc pole. when shri. dilipsinh dhulabhai chauhan felt that his son harpal who was running behind the buffalo was electrocuted, he put the tester on the buffalo and the tester recieved electr | Awaited | NA | NA | To Prevent More Casualties Line Clear Taken Of 11 Kv Kuna Ag Fdr And Jumper Cut After Accident To Stop Supply To This Transformer | Nadiad | 2
26 | Solanki Suryaben Manharsinh,Vill-Bhakhrani Muvadi,Ta-Kalol,Dist-Panchmahal |  |  | 2024-03-16 | NFHO |  |  | TOUCH 11KV LINE ON ROOF TOP OF VICTIM HOUSE AND ELECTRODUCED | Awaited | NA | NA | NOTICE ISSUED TO VICTIM | Godhra | 2
27 | Sunilbhai surpanbhai Pargi,Vill-Karodia,Ta-Fatepura,Dist-Dahod |  |  | 2024-03-17 | NFHO |  |  | The line shifting work was carried out by the contractor person. Under the supervision of line inspector and Line man he take Line Clear of 11 KV Fatepura JGY feeder at 11:35 hrs and cut the nearby switch and earthed it and then instruct contractor supervisor to start the work. The victim and another contractor person were working on the Fatepura JGY feeder HT PSC pole at around 12:10 hrs when the victim was pin binding on the top phase of the HT extension, the power suddenly came on and they | Awaited | NA | NA | Staff Have Been Instructed To Not Allow Persons Working Under Them To Start Work Without Making Power Off And Other Safety Precautions Taken. | Godhra | 3
28 | ZALA DALPATBHAI KARANSINH,Vill-Dudhathal,Ta-Kapadwanj,Dist-Kheda |  |  | 2024-03-17 | FHO |  |  | On dated 17.03.2024 around 08.00 A.M. Person of unstable mind who's name is Shree Dalpatbhai Karansinh Zala(From village Reliya)Suddenly climed up Tc structure of3 ph ag cooncetion of shri Rajeshbhai Shnatilal Patel (Which is located at sim vistar of Dudhathal Village)and got elecrocuted and died. | Awaited | NA | NA | Maintenace was done and power supply restored | Nadiad | 2
29 | BUFFALO,Muvadi faliyu, Vill-Paroli, Tal-Ghoghamba, Dist-Panchmahal |  |  | 2024-03-24 | FA |  |  | CAME IN CONTACT WITH EARTHING WIRE OF POLE | Awaited | NA | NA | LT ABC RECTIFIED EARTHING WITH PVC PIPE DONE | Godhra | 8

## MG SoP 03
Name of Distribution Licensee: M G V C L
Quarter : Q-IV (Jan-Feb-Mar-2023-24)
Year: 2023-24
REGISTER FOR COMPILING THE COMPLAINTS CLASSIFICATIONWISE Q-IV 2024
Performa SoP 003 B: |  |  |  | APPENDIX-B (already in the SoP regulation)
Classification | Nature of Complaints | Pending complaints of previous qtr. | Complaints received during the qtr. | Total Complaints =2+3 | No. of Complaints redressed during the quarter. |  |  |  |  | Balance Complaints to be redressed. (4) – (9)
[5 empty] | In stipulated time |  | Beyond stipulated time |  | Total (5) to (8)
[5 empty] | Within 50% of stipulated time. | Within stipulated time. | Up to double the stipulated time | More than double the stipulated time
| 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10
A(i) | Loose Connection | 0 | 66643 | 66643 | 35716 | 30927 | 0 | 0 | 66643 | 0
A(ii) | Intruption due to line Break down | 0 | 46808 | 46808 | 25560 | 21248 | 0 | 0 | 46808 | 0
A(iii) | Intruption due to T/C Fail | 0 | 5318 | 5318 | 3147 | 2171 | 0 | 0 | 5318 | 0
B(i) | Quality of power supply,ordinary case which require no Augmentation | 0 | 7164 | 7164 | 4782 | 2382 | 0 | 0 | 7164 | 0
B(ii) | Quality of power supply,ordinary case which require Augmentation | 0 | 4379 | 4379 | 2593 | 1786 | 0 | 0 | 4379 | 0
C(i) | Meters- Stoped/Defective meter | 0 | 13089 | 13089 | 8928 | 4161 | 0 | 0 | 13089 | 0
C(ii) | Meters- Billing on average basis for > two bills | 0 | 5357 | 5357 | 3321 | 2036 | 0 | 0 | 5357 | 0
D(i) | Over head lines - loose wires | 0 | 4089 | 4089 | 2773 | 1316 | 0 | 0 | 4089 | 0
D(ii) | Over head lines - in adiquate ground clearance | 0 | 1593 | 1593 | 1123 | 470 | 0 | 0 | 1593 | 0
E(i) | Bills- for current bills where no addl information required | 0 | 5514 | 5514 | 4396.2 | 1117.8 | 0 | 0 | 5514 | 0
E(ii) | Bills- for current bills where addl information required | 0 | 3152 | 3152 | 1929 | 1223 | 0 | 0 | 3152 | 0
F(i) | Service connections- where extention of mains is not required | 0 | 7282 | 7282 | 5479 | 1803 | 0 | 0 | 7282 | 0
F(ii) | Service connections- where extention of mains is required | 0 | 3323 | 3323 | 2013.4 | 1309.6 | 0 | 0 | 3323 | 0
F(iii) | Service connections- Modification in connected load | 0 | 2938 | 2938 | 1308.4 | 1629.6 | 0 | 0 | 2938 | 0
F(iv) | Service connections- Name change/reconnection | 0 | 3658 | 3658 | 2133 | 1525 | 0 | 0 | 3658 | 0
G | Refund of amount due inregard to temp conn | 0 | 557 | 557 | 324.2 | 232.8 | 0 | 0 | 557 | 0
H | Others | 0 | 23951 | 23951 | 12576 | 11375 | 0 | 0 | 23951 | 0
| TOTAL | 0 | 204815 | 204815 | 118102.2 | 86712.8 | 0 | 0 | 204815 | 0
The format is to be sent quarterly
The quarterly reporting of the year means reporting for the period 1st Quarter as Jan – Mar, 2nd Quarter as Apr – Jun, 3rd Quarter as Jul – Sep and 4th Quarter as Oct – Dec of the year.
For any other complaints not mentioned in the classification, the sequence for (H) can be used.

## MG SoP 04
Name of Distribution Licensee: M G V C L
Quarter : Q-IV (Jan-Feb-Mar-2023-24)
Year: 2023-24
Performa SoP 002 : Publicity carried out while displaying the contact details of consumer complaints centers
Particulars should also cover the details of consumer awareness program conducted, advertisement done through various media like TV, newspaper, radio, pamphlets & booklet distributions, Displays etc. The development of website and any medium through which public education is carried out can be included.
Sr. No | Actions or steps carried out by distribution licensee towards public awareness in the quarter | Likely number of consumers influenced
1 | RTI Officers Name is displayed at customer care centre on each office | 3578282
2 | Necessary information regarding time schedule for new connection and solving complaints is display on the board. | 3578282
3 | Contact nos. of various officers of the company for emergency contact is also displayed at customer care centre. | 3578282
4 | Displayed safety posters at various S/dn,Divisions | 1488
5 | Safety Meeting with Line Staff at various S/dn,Divisions on Every Monday (Line staff influenced) | 540

## SOP-05
Name of Distribution Licensee: M G V C L
SOP Q-IV
Year :2023-24
Performa – SoP 005 B: Action taken report by the Redressal Committee
Sr. No | Month | Name of Office | Date and Time Meeting conducted | No of complaints registered at the meeting | No. of complaints pending at the end of the meeting
1 | 1st Month of the quarter (JAN-24) | Corporate Office | 24.01.24 11:15 AM at corporate office vadodara | 4 | **2 Nos. complainant has asked adjournment
|  | Godhra C.O. | 06/01/24 & 20/01/24 11.30 AM at Godhra Circle Office | 7 | 7
2 | 2nd Month of the quarter (FEB-24) | Corporate Office | NIL | 0 | **2 Nos. complainant has asked adjournment
|  | Godhra C.O. | 03/02/24, 17/02/24 & 21/02/24 11.30 AM at Godhra Circle Office | 10 | 9
3 | 3rd Month of the quarter (MAR-24) | Corporate Office | 27.03.24 11:30 AM at corporate office vadodara | 6 | 0
|  | Godhra C.O. | 06/03/24, 16/03/24,19/03/24 & 30/03/24 11.30 AM at Godhra Circle Office | 9 | **1 Applicant was absent

## MG SoP -06
Name of Distribution Licensee: M G V C L
Financial Year: 2023-24
Quarter : Q-IV (Jan to Mar-2024)
Performa SoP 006: Failure of Distribution Transformer
Sr. No. | Name of Circle | Nos. of existing Distribution Transformers at the start of the quarter | Nos. of Distribution Transformers added during the quarter | Total number of Distribution Transformers on end of quarter | Total number of Distribution transformer failed during quarter | % failure rate of Distribution transformer
|  | A | B | C=A+B | D | H = (D)*100/C
1 | Baroda O&M | 57589 | 901 | 58490 | 629 | 1.0754
2 | Baroda City | 10218 | 251 | 10469 | 11 | 0.10507
3 | Anand | 26254 | 546 | 26800 | 102 | 0.3806
4 | Nadiad | 34200 | 297 | 34497 | 165 | 0.4783
5 | Godhra | 60464 | 1460 | 61924 | 753 | 1.216
| MGVCL | 188725 | 3455 | 192180 | 1660 | 0.86377

## SoP008
Name of Distribution Licensee: M G V C L
Quarter : Q-IV (Jan-Feb-March- 2024)
Year: 2023-24
Performa SoP 008: Sample Test result for Neutral Voltage
Compliance Sample Test Report for Neutral Voltage
-1 | -2 | -3 | -4 | -5 | -6
Sr. No | Category of consumers | Sample Size | Standard specified in regulation | Deviation of results from the sample test (Numbers) | % age compliance
|  | (Numbers) |  |  | (6) = (5)*100/(3)
| LT consumers | 1441 | 2% | 0 | 0
1 | Domestic | 1023 | 2% | 0 | 0
2 | Commercial | 242 | 2% | 0 | 0
3 | Industrial | 23 | 2% | 0 | 0
4 | Agricultural | 143 | 2% | 0 | 0
5 | Public water works | 10 | 2% | 0 | 0
| HT consumers |  | 2%
6 | HT industrial | 5 | 2% | 0 | 0

## SoP009
Name of Distribution Licensee: M G V C L
Quarter : Q-IV (Jan-Feb-March- 2024)
Year: 2023-24
Performa SoP 009: Sample Test result for Voltage variations
Compliance Sample Test Report for voltage variations
-1 | -2 | -3 | -4 | -5
Voltage Level | Sample Size (numbers) | Limit or prescribed standard | Deviation of results from the sample test (Numbers) | % age compliance
(5) = (4)*100/(2)
Low Voltage | 56 | +6% to -6% | 0 | 0
High Voltage | 24 | +6% to -9% | 0 | 0
Extra High Voltage | 1 | +10% to -12.50% | 0 | 0

## SoP010
Name of Distribution Licensee: M G V C L
Quarter : Q-IV (Jan-Feb-March- 2024)
Year: 2023-24
Performa SoP 010: Sample Test result for Harmonics
Compliance Sample Test Report for Harmonics
-1 | -2 | -3 | -4 | -5 | -6
Sr. No | Category of consumers | Sample size (Numbers) | Limit or standard prescribed | Deviation of results from the sample test (Numbers) | %age compliance
(6) = (5)*100/(3)
1 | LT consumers | 33 | 3.5% | 0 | 0
2 | HT consumers | 4 | 3% | 0 | 0
3 | EHT consumers | 1 | 3% | 0 | 0
Note: The licensee shall also submit along with the above harmonic data, the records of customer wise drawls of harmonic currents measured at various strategic points.
The formats SoP 008, SoP 009 and SoP 010 have to be sent annually.
For the purpose of annual submissions, the year end has to be considered as the end of December month of a particular year.

## 11A
Q-4(Jan-Mar-24)
Year: 2023-24
SoP 011 –A: System Average Interruption Frequency Index (SAIFI)
Sr. No | Month | Ni - Total no of customers for each momentary interruptions | NT - Total no of customers served |  |  | Past year corrosponding Month
1 | 2 | 3 | 4 | 5 | 6=5/4
1 | Jan' 24 | 3371285 | 3558247 | 15152695 | 4.2585 | 3.21
2 | Feb'24 | 3311163 | 3567783 | 11877305 | 3.329 | 1.89
3 | Mar'24 | 3029664 | 3578282 | 18816339 | 5.2585 | 3.22
|  |  | 10704312 | 45846339 | 4.283 | 2.7733

## 11B
Q-4(Jan-Mar-24)
Year: 2023-24
SoP 011 – B System Average Interruption Duration Index (SAIDI)
Sr. No | Month | ri = Restoration Time for each interruption event | Ni - no of interrupted customers for each sustained interruption event | ri * Ni – Total customer interruption Duration | ri=Restoration Time for each interruption event | Ni= No of Interrupted customers for each sustained Interruption | NT - Total no of customers served | Customer Interruption Duration |  |  | Past year corrosponding Months
[9 empty] | MINS. | HRS.
1 | 2 | 3 | 4 | 5= 3 X 4 | 3 | 4 | 5 | 6 | 7=4/3 | 7A | MINS. | HRS.
1 | Jan' 24 | July |  |  | 781472 | 3371285 | 3558247 | 1039643166 | 292.1785 | 4:52 | 271 | 4:31
2 | Feb'24 | August |  |  | 586570 | 3311163 | 3567783 | 765209787 | 214.4777 | 3:34 | 178 | 2:58
3 | Mar'24 |  |  |  | 543886 | 3029664 | 3578282 | 610171248 | 170.5207 | 2:51 | 170 | 2:50
[6 empty] | 9712112 | 10704312 | 2415024201 | 225.6123 | 3:46 | 206.3333 | 3:26

## 11C
Q-4(Jan-Mar-24)
Year: 2023-24
SoP 011 – C: Momentary Average Interruption Frequency Index (MAIFI)
Sr. No | Month | Number of Momentary interruptions Imi | Nmi - Total no of customers for each momentary interruptions | NT - Total no of customers served |  |  | Past year corrosponding Month
1 | 2 | 3 | 4 | 5 | 6 | 7
1 | Jan' 24 | 34827 | 3217969 | 3558247 | 55180485 | 15.5078 | 10.37
2 | Feb'24 | 28565 | 3039745 | 3567783 | 38295093 | 10.7336 | 6.64
3 | Mar'24 | 37574 | 2888760 | 3578282 | 51804906 | 14.4776 | 11.29
|  |  |  | 10704312 | 145280484 | 13.5721 | 9.4333

## MG SoP - 13
Name of Distribution Licensee: M G V C L
Financial Year: 2023-24
Quarter : Q-IV (JAN to MAR-2024)
Performa SoP 013: Faulty Meters Replacement
Consumer Category | No. of faulty meters at the start of the quarter | No. of faulty meters added during the quarter | Total no. of defective / faulty Meter | No. of faulty Meters repaired and replaced | No of faulty meters pending at the end of the quarter | Remark
| 1 | 2 | (3)=(2)+(1) | 4 | (5)=(3)-(4)
1 PHASE
MGVCL | 10105 | 23474 | 33579 | 23466 | 10113
3 PHASE
MGVCL | 3802 | 4294 | 8096 | 4592 | 3504

## SoP_15
Performa SoP 015: Release of New Connection status for FY 2023-24
Qtr | Consumer category | Total no. of consumers connected at the beginning of half-year/year | Pending at the Beginning of the of the Half year/year | New Applications received during the half-year / year | No. of connections released during the half-year / year | No. of applications pending at the end of half-year / year | Total no. of consumers connected at the end of half-year/year
2nd Half (Oct-March24)) | Domestic | 2883539 | 3387 | 35173 | 38225 | 335 | 2910777
| Commercial (NRGP_C+LTMD_C) | 340946 | 1581 | 9305 | 10735 | 151 | 342405
| Industrial LT (NRGP_L+LTMD_L) | 41421 | 264 | 879 | 1120 | 23 | 41048
| Agriculture (Total) | 198105 | 8729 | 6715 | 6437 | 8044 | 204542
| Industrial HT | 3001 | 76 | 152 | 154 | 70 | 3155
| Total | 3467012 | 14037 | 52224 | 56671 | 8623 | 3501927

## MG SoP 16
Name of Distribution Licensee: M G V C L
Quarter : Q-IV (Jan-Feb-March- 2024)
Year: 2023-24
Performa SoP 016: Compensation details
COMPENSATION DETAILS
Sr.No. | Event | Compensation | No of cases where compensation was given (in numbers) | Amt of compensation paid (in Rs.)
1 | Duty to provide supply | Rs. 50 per day of delay from the limit specified in the performance regulations | 0 | 0
| a) New Connection |  | 0 | 0
| b) Additional Load |  | 0 | 0
| c) Temporary supply |  | 0 | 0
| d) Shifting service connection |  | 0 | 0
| e)Transfer of service connection |  | 0 | 0
| f) Change in tariff category of consumer |  | 0 | 0
2 | Complaints in billing | Rs. 50 for non reply within the period prescribed in Regulations | 0 | 0
3 | Replacement of meters | LT- Rs. 25 per day of delay - maximum Rs.2,500 and HT - Rs. 250 per day of delay - maximum of Rs.5,000 | 0 | 0
4 | Interruption of supply | LT- Rs. 25 for every 6 hrs of delay- maximum of Rs. 500 and HT- Rs. 50 for every 6 hrs delay- maximum Rs. 1000/- | 0 | 0
5 | Voltage fluctuations and complaints | Rs. 50 for failure to visit or convey findings within the stipulated period | 0 | 0
6 | Responding to consumer's complaints | Rs. 25 for each day of delay- maximum Rs. 500 | 0 | 0
7 | Grievance Handling | Rs.25 for failure in handling grievance | 0 | 0
TOTAL |  |  | 0 | 0