## MG COVER PAGE
Name of Distribution Licensee: M.G.V.C.L.
Quarter of the year : Q-I (Apr-May-June-2025-26)
Year: 2025-26

## MG SoP 01
Name of Distribution Licensee: M G V C L
Quarter I (Apr-25 to Jun-25)
Year:2025-26
Performa - SoP 001: Fatal and Non-fatal accident report
NUMBER OF ACCIDENTS FOR THE FIRST QUARTER 2025-26
Sr. No | Name of Area/Circle | No of accidents in the quarter |  |  |  |  | Cumulative since the first quarter of the current FY year
|  | Departmental |  | Outside |  |  | Departmental |  | Outside
|  | FH | NFH | FH | FA | NFH | FH | NFH | FH | FA | NFH
1 | Baroda City |  |  | 2 | 1 |  |  |  | 2 | 1
2 | Baroda (O&M) |  | 1 | 8 | 12 |  |  | 1 | 8 | 12
3 | Anand |  | 1 | 4 | 8 | 2 |  | 1 | 4 | 8 | 2
4 | Godhra |  |  | 6(1-Pvt) | 15 | 3 |  |  | 6(1-Pvt) | 15 | 3
5 | Nadiad |  | 2 | 6 | 7 | 1 |  | 2 | 6 | 7 | 1
| TOTAL | 0 | 4 | 26(1-Pvt) | 43 | 6 | 0 | 4 | 26 (1-Pvt) | 43 | 6
[6 empty] | 79 |  |  |  |  | 79
FH – Fatal Human, FA – Fatal Animal, NFH – Non-fatal Human
The format is to be sent quarterly

## MG SoP 01 (GERC) (hidden)
Name of Distribution Licensee: M G V C L
Quarter I (Apr-25 to Jun-25)
Year:2025-26
Performa - SoP 001: Fatal and Non-Fatal electrical accident report
NUMBER OF ACCIDENTS FOR THE 1st QUARTER OF 2025-26
Sr. No | Name of Area/Circle | No of accidents in the quarter |  |  |  |  | Cumulative since the first quarter of the current FY 2024-25
|  | Departmental |  | Outside |  |  | TOTAL
|  | FH | NFH | FH | FA | NFH | FH | FA | NFH
1 | Baroda (City) |  |  | 2 | 1 |  | 2 | 1
2 | Baroda (O&M) |  | 1 | 8 | 12 |  | 8 | 12
3 | Anand |  | 1 | 4 | 8 | 2 | 4 | 8 | 2
4 | Godhra |  |  | 6(1-Pvt) | 15 | 3 | 6(1-Pvt) | 15 | 3
5 | Nadiad |  | 2 | 6 | 7 | 1 | 6 | 7 | 1
| TOTAL | 0 | 4 | 26 (1-Pvt) | 43 | 6 | 26 (1-Pvt) | 43 | 6
FH – Fatal Human, FA – Fatal Animal, NFH – Non-fatal Human | [5 empty] | 79 |  |  | 75
PVT - Private Premises Accident.

## SoP 002
Performa – SoP 002: Action taken report for safety measures complied for the accidents occurred
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14
Sr. No | Location of Accident and details of the victim | Date of occurrence | Type of Accident | Installation |  | Accident Type |  |  | Cause of Accident | Findings of CEI / EI / AEI | Remedies suggested by CEI /EI / AEI in various cases | Whether the remedy suggested is complied | Action taken to avoid recurrence of such Accident | CEI REPORT received YES/NO | If No then , mention letter no. and date written to CEI/EI/AEI office. | Findings of CEI / EI / AEI | Remedies suggested by CEI /EI / AEI in various cases | Whether the remedy suggested is complied | Action taken to avoid recurrence of such Accident | Amount of compensation and date of compensation paid | Circle office | Division | Sub-division | Reason
1 | Sanjaybhai Shivabhai Parmar,Jetholi to Vavli Road,Vill-Jetholi,Tal-Balasinor,Dist-Mahisagr | 2025-04-11 | FHO | [5 empty] | Direct hooking of 11kv line on fencing or other under police investigation | [6 empty] | Awaited | NA | NA | Advertisment is published in news paper to informe not to connect direct power from electrical line to fencing. |  | Nadiad | Nadiad | Balasinor-II
2 | Amarsinh Ghelabhai Solanki,Vill-Zarol,Tal-Nadiad,Dist-Kheda | 2025-04-15 | FHO | [5 empty] | At farm of kusumben d mekwan con no 01411004507 RGPR from 3 rd pole of lt 2w abc from ganesh ag feeder tc having power off at their premises so their reprentetive joyel d mekwan present at place amarsinh g Solanki was trying to solve power issue by climbing the pole while at that time of on pole he got Electric Shock and fall down then near by people called 108 ambulunce taken to Nadiad Civil hospital | [6 empty] | Awaited | NA | NA | Advertisment is published in news paper for not to work on live line (unauthorised work) | 100000/-Dt-13.06.25 | Nadiad | Nadiad City | Nadiad R
3 | Solanki Dilipbhai Rameshbhai,Dev ni pol,Vill-Khambhat,Tal-Khambhat,Dist-Anand | 2025-04-19 | FHO | [5 empty] | After site verification above said fatal human outsider accident occurred due to improper & unsafe activity by frt employees | [6 empty] | Awaited | NA | NA | Instructions given to all FRT staff to wear safety gadgets while working on line & not to work on live line & work in presence of MGVCL line staff |  | Anand | Petlad | Cambay T
4 | Ambalal Shankarbhai Rathwa,Bilgam Chokdi,Vill-Lavakoi,Tal-Naswadi,Dist-Chhotaudepur | 2025-04-20 | FHO | [5 empty] | Farm owner was working in his farm.by that time, he was passing near by do structure of 11 kv lavakoi ag feeder. One of the guy, with guy rod was outside (someone may have removed). The guy road wire were away from land approximately 3 feet from pole. By the time of passing from near by do structure, victim touched the guy wire and due to his weight, guy wire touched momentarily to the live do conductor on upper side and victim got electric shock. | [6 empty] | Awaited | NA | NA | Proper maintenance is carried out |  | Baroda O&M | Bodeli | Naswadi
5 | Bariya Khumanbhai Somjibhai,Near mokshdham,Vill-Karodiya,Tal-Vadodara,Dist-Vadodara | 2025-04-20 | FHO | [5 empty] | on dt-20.04.2025 at around 11 to 11:30am the victim Mr. Bariya Khumanbhai Somjibhai had approched a hut made of iron sheets near the site to eat goras aambli.As eyewitness had warned the victim not to climb onto the hut and goras aambli tree. While he was standing on both goras aambli tree and hut, the goras aambli tree branch brock and fall down to near by 11KV Mahapura Ag feeder line,reasulting in the victim got electric shock. Also it is found that no any tripping obsvered on 11KV Mahapura Ag | [6 empty] | Awaited | NA | NA | Due to negligancy of victim accident was occurred, no need to do any rectification. |  | Baroda O&M | Baroda O&M | Koyali
6 | Virambhai Hazabhai Khambhala,At garmala sim maruti traders,Vill-Garmala,Tal-Matar,Dist-Kheda | 2025-05-01 | FHO | [5 empty] | On date 01.01.2025 at aprrox 23:30 hrs at village garmala maruti traders civtim shri virambhai hazabhai khambhala unloading the grit by hydrolic trolly of truck and after unloading of grit without getting lock of hydrolic trolly move forward and trolley touched 11 kv koshiyal ag feeder line(power of alindra ag feeder)and he got electric shocked.he is shifted immediatly to hospital for further treatment but doctor on duty delared him dead. | [6 empty] | Awaited | NA | NA | Stringing of conductor work is carried out. |  | Nadiad | Mehmdabad | Limbasi
7 | Chauhan Tanmaybhai Chetanbhai,Dabgarvas,Vill-Zalod,Tal-Zalod,Dist-Dahod | 2025-05-01 | NFHO | [5 empty] | On ,01.05.2025 ,chauhan chetanbhai rajubhai's son was playing cricket in front of his house.after a while,his boll got stuck in the service wire running in frount of his house.when he went to take out a ball on the balcony of his house, he come in contect with the service wire break(open)portion and got an electric shock.when chauhan chetanbhai rajubhai came to know about it.he immediatally took his son to the hospital,where he is currently doing well and is out of danger,according to the doct | [6 empty] | Awaited | NA | NA | At Location All Service Wire Replacement & One Span To LT ABC Cable Replacement Done |  | Godhra | Dahod | Zalod
8 | 01 Buffalo and 01 Goat,Vill-Mahudha,Tal-Mahudha,Dist-Kheda | 2025-05-05 | FA | [5 empty] | As per the information, the accident occurred due to the breaking of the service wire for consumer no. 04901-05098-2 during heavy rain and cyclone on 05/05/2025. The broken service wire came into contact with the iron roof behind the house, resulting in leakage current. One buffalo and one goat came into contact with the leakage current and got electrocuted. | [6 empty] | Awaited | NA | NA | Service wire of consumer is replaced by new service wire |  | Nadiad | Nadiad | Mahudha
9 | Jiteshbhai More,LT line pole near jay ambe TC,Vill-Vadodara,Tal-Vadodara,Dist-Vadodara | 2025-05-05 | FHO | [5 empty] | Due to heavy wind and rain,lt aaac cond. Broken and fell down there was water logging, jiteshbhai was passing there and came in contact with live wire and he got an electrocuted and died on the spot. | [6 empty] | Awaited | NA | NA | LT line is provided with Spacer and Guarding | Not Paid | Baroda City | Vishvamitri(W) | Gorva
10 | Fatesinh Chagansinh Zala,Tarpoz vistar,Vill-Kaniyel,Tal-Kathlal,Dist-Kheda | 2025-05-06 | NFHO | [5 empty] | Due to heavy wind and cyclone,pato jgy 1 ph 2 wire lt line broken due to tree branch fallen,when victim came for saving his son passing to these area,his neck came in contact with live wire and he got electric shock and addmitted in carewell hospital kathlal.now his condition is stable | [6 empty] | Awaited | NA | NA | Proper maintenance is carried out |  | Nadiad | Mehmdabad | Kathlal - II
11 | Ravat Dineshsinh Bhavarsinh,Derol station road, opp bajaj showroom,Vill-Kalol,Tal-Kalol,Dist-Panchmahal | 2025-05-06 | FHO | [5 empty] | On Dtd 06.05.2025, At 11.30 Hrs, Contractor Gang Of Shri P L Ravat Was Asked To Join 11Kv Wire Of Derol Station JGY Feeder, The Work Was Completed After That Unknowingly Contractor Man Late Shri Dineshsinh Bhavarsinh Ravat Climb Nearby MEHTA Society TC Structure Where LT AB Line Is Loose Later But 11Kc MGS Urban Feeder Was On Said Mehta Society TC And Victim Came In Contact With The 11 Kv MGS Urban Feeder And He Was Immediately Shifted To Hospital. After Primary Treatment He Was Declared Dead, PM Report And Police Panchnama Are Still Awaiting From Officials. | [6 empty] | Awaited | NA | NA | Distribution Box maintenance done and fencing cleaning work done |  | Godhra | Halol | Kaalol
12 | Cow of Prabhatbhai Memabhai Rabari,Rabariwad TC,Vill-Shakarpur,Tal-Khambhat,Dist-Anand | 2025-05-07 | FA | [5 empty] | According To The Statement Of Owner Rabari 7Prabhat Bhai Memabhai,He Had Gone Out To Graze His Cows On Dt 07.05.2025 At 9 Am. Around 3 Pm,Cows Were Grazing In The Area Nr. Shakarpur Rabariwas Transformer Center, One Of The Cow Came In Contact With Leakage Current Path On Wet Ground Through Outgoing Cable Puncture.The Cow Got Electrocuted Through Momentary Leakage Currents. | [6 empty] | Awaited | NA | NA | Transformer Center Outgoing Cable was replaced by new cable |  | Anand | Petlad | Cambay T
13 | Cow of Bhavibhai Gopalbhai Rabari, Jogni mata Mandir Pase,Vill-Shakarpur,Tal-Khambhat,Dist-Anand | 2025-05-07 | FA | [5 empty] | According To The Statement Of The Owner Rabari Bhavinbhai Gopal Bhai ,He Had Gone To Grase His Cows On Dtd 07.05.2025 At 9 Am. Around 3Pm Cows Were Grazing In The Area Nr. Shakarpur Jogni Mata Mandir TC Area , One Of The Cow Came In Contact With Leakage Current Path On Wet Ground Through Ongoing Cable Punctre .The Cow Got Electrocuted Through Momentary Leakage Currents. | [6 empty] | Awaited | NA | NA | Transformer Center Outgoing Cable was replaced by new cable |  | Anand | Petlad | Cambay T
14 | Cow Owner Khodabhai Hanubhai Bharwad,Nr Bharwad Jok,Vill-Padra,Tal-Tarapur,Dist-Anand | 2025-05-07 | FA | [5 empty] | At above location there is 3 ph 4w lt abc wire. Streetlight bulg connected to lt line where joint is opened and insullation damaged. Due to cyclone and rain on this date cow contact with earthing wire of gi wire of pole lekage current passed and cow was passing near by pole and electrocuted. | [6 empty] | Awaited | NA | NA | New insulation wire provided and rectification work carried out |  | Anand | Petlad | Tarapur
15 | Cow of Ishwarbhai Ranchhodbhai Bharvad,Ganeshnagar,Vill-Chhani,Tal-Vadodara,Dist-Vadodara | 2025-05-07 | FA | [5 empty] | While passing near psc lt line cow got electrocued due to wwet land due to rain as defective part of live wire 2.5mm2pvc cable used for ltg connection touches streetlight clamp and leakage current passes to wet land. | [6 empty] | Awaited | NA | NA | Service wire of lighting connection is replaced by new service wire |  | Baroda O&M | Baroda O&M | Chhani
16 | Cow of Owner Rabari Dharmeshbhai Jitubhai,Vill-Kelanpur,Tal-Vadodara,Dist-Vadodara | 2025-05-07 | FA | [5 empty] | As per information received from owner and site panchanama, cow came in contact with mgvcl lt pole which was electrocuted due to lt abc insulation was damaged and touching c clamp.it was happened as a neem tree was fallen on lt abc wire of cyclone dated 5.5.2025 due to electrocution the cow was die | [9 empty] | LT ABC Replaced Dtd. 08-05-2025 |  | Baroda O&M | Jambuva | Khatamba
17 | She cow of Rajpalbhai Palanibhai Nayar,Jamla chokdi, Near forest quarters ,Vill-Chhotaudepur,Tal-Chhotaudepur,Dist-Chhotaudepur | 2025-05-07 | FA | [5 empty] | Cow was grazing and passing nearby 100 kva transformer structure nearby forest quarters, jamla chokadi, chhotaudepur. Meanwhile momentarily leakage current passed in earthing wire of that transformer structure. At that same time cow may be came in contact with that earthing wire while grazing and may got electrocuted, she cow of owner shree rajpalbhai palnibhai nayar age approx 4 year | [6 empty] | Awaited | NA | NA | Proper maintenance is carried out |  | Baroda O&M | Bodeli | Chhota Udaipur
18 | Smt. Ramaben Bhikhabhai Patel,Patel Faliyu,Vill-Mota Kanesar,Tal-Khanpur,Dist-Mahisagar | 2025-05-08 | FHO | [5 empty] | According to eyewitness testimony, the victim was passing through a narrow courtyard gate near a lt pole situated on the gate stairs. While using the pole for support , the victim's hand contacted a gi earthing wire. Simultaneously, due to heavy wind a phase of the lt abc 3p4w accidentally contacted the gi wire, resulting in the victim receiving an electric shock and falling. She was taken to the hospital later, but died on the way. | [6 empty] | Awaited | NA | NA | LT ABC restinging carried out and maintain distance between LT & U-clamp also Insulated earthing provided. |  | Godhra | Lunawada | Bakor
19 | Geetaben Rohitbhai Bhuriya,Vill-Galaliyawad,Tal-Dahod,Dist-Dahod | 2025-05-08 | FHO | [5 empty] | Due to heavy wind and rain, lt conductor snapped from lt shackel insulator and came in contact with u clamp, which might resulted into leakage current throught psc pole's gi wire. Another 2nd gi wire was tied by victim's family, between psc pole and tree, which was used for drying clothes. Victim accidently came in contact with 2nd gi wire and got electrocuted. Victim was taken to zydus hospital and declared as dead. | [6 empty] | Awaited | NA | NA | Lt conductor rebinding and GI wire used for drying clothes is removed |  | Godhra | Dahod | Dahod R
20 | Firozbhai I Vohra,Vill-Khorvad,Tal-Umreth,Dist-Anand | 2025-05-08 | NFHD | [5 empty] | Upon receiving the complaint, Shri Firojbhai Vora visited the site to attend to the issue. At the location, two Drop Out (DO) fuses were found to be in a blown condition. While attempting to rectify the issue, it is suspected that his hand accidentally came in contact with the 11 KV side DO or its jumper, resulting in an electric shock. He fell to the ground due to electrocution. | [6 empty] | Awaited | NA | NA | Awareness of such accident given to line staff & ask them to verify the line power is sitche off or not before climbing the pole | departmental case | Anand | Anand | Anand S
21 | Bullock of Ramanbhai Ranchhodbhai Bhil,Near station faliya,Vill-Goyawant,Tal-Naswadi,Dist-Chhotaudepur | 2025-05-08 | FA | [5 empty] | Bullock was grazing and passing near by the 63 kva transformer structure of station faliy . Meanwhile momentarily leakage current passed in earthing wire of that transformer structure due to rainy atmosphere. At that same time bullock may be came in contact with that earthing wire while grazingand may got electroted. | [6 empty] | Awaited | NA | NA | Earthing Wire of Transformer Structure was made properly and Maintainance done for Transformer Centre on Dt: 12/05/2025 |  | Baroda O&M | Bodeli | Naswadi
22 | Ghelabhai Popatbhai Bharvad,Behind shiv farm,near deva bharvad farm,Vill-Undera,Tal-Vadodara,Dist-Vadodara | 2025-05-09 | FHO | [5 empty] | On dtd 09.05.2025, at 07.30 hrs, victim shri ghellabhai popatbhai bharvad of vill undera, ta undera di vadodara came to farm of vinubhai m patel nearby farm of shri deva bhai bharvad of vill undera. Vinubhai m patel's farm is covered with fencing and fencing was tided(joint) with last lt psc pole and earthing wire. A insulation of main service wire near pole was cut by squirrel so when victim shri ghellabhai popatbhai bharvad was crossing the fencing at that time due to wind main service wire to | [6 empty] | Awaited | NA | NA | Defective service wire replaced and fencing was removed. |  | Baroda O&M | Baroda O&M | Koyali
23 | Buffalo Owner Parmar Kanaksinh Dalpatsinh,Near prathmik aarogya kendra,Vill-Kanjari,Tal-Halol,Dist-Panchamahal | 2025-05-10 | FA | [5 empty] | On Dated 10.05.25 At 12.45 Hrs, A Buffalo Owned By Parmar Kanaksinh Dalpatsinh Is Passing From Tc Structure Which Was Installed Near Prathmik Kendra Village Kanjari And During Grazing Near Tc Structure Due To Leakage Current From Earthing Wire Of TC Buffalo Might Have Got Electric Shock And Died As Informed By Eyewitness. | [6 empty] | Awaited | NA | NA | New earthing at the Transformer center with PVC insulation pipe done |  | Godhra | Halol | Halol T
24 | Pinkalben Jigneshbhai Vaghela,Nana boriya ag land,Vill-Sodpur,Tal-Nadiad,Dist-Kheda | 2025-05-12 | FHO | [5 empty] | Due to cyclone wind lt abc 2w unbound from shackle and detoretedinsulation came in contact with u clamp and gi wire energized and victim came in contact of gi earth wire and electrocuted | [6 empty] | Awaited | NA | NA | Proper Binding With LT Shackle Insulator and LT ABC 2W & Insulation Tap Provided On Detoriated Insulation Of 2W ABC | 100000/-Dt-23.05.25 | Nadiad | Nadiad City | Chaklasi
25 | Bariya Gaurangbhai Ramanbhai,Bhathiji mandir faliyu,Vill-Timbi,Tal-Waghodia,Dist-Vadodara | 2025-05-13 | FHO | [5 empty] | On dated 13.05.2025, frt team went to village timbi to solve the complaint. A victim from frt bariya gaurang ramanbhai climbed on the pole where ht is also paaing on same pole. By mistake he touched to ht line and got electrocuted, fell down and hospitalized. During the treatment of 5 hrs he was declared as dead. | [6 empty] | Awaited | NA | NA | Awareness of such accident given to line staff and FRT Staff & ask them to verify the line power is switch off or not before climbing the pole |  | Baroda O&M | Baroda O&M | Wagodia
26 | Buffalow owner Mahendrabhai Bhavanbhai Bharvad,Vill-Rangpur,Tal-Khambhat,Dist-Anand | 2025-05-14 | FA | [5 empty] | As per eye witness, shri mahendrabhai bhavanbhai bharvad's statement he had gone out to graze his cows & buffaloes on dt:14.05.2025 at 09:00 am. Arounf 3 pm, cows & buffaloes were grazing in the area behind rangpur bus stand. One of the buffalo reached the farm of shri balvantbhai keshavbhai patel. There the buffalo came in contact with broken live lt wire, so it got electrocution and found dead at site. | [6 empty] | Awaited | NA | NA | New Pole erected and restringing of the line carried out |  | Anand | Petlad | Cambay R
27 | Raval Dashrathbhai Niteshbhai,Nani raval vas,Vill-,Tal-Kapadwanj,Dist-Kheda | 2025-05-17 | FHO | [5 empty] | On dated 17.05.2025, around 07:00pm a truck was parked on the roadside beneath the 11kv amabliyara jgy overhead line at antroli canal road (nr. Nano raval vas). The truck cleaner/conductor-raval dashrathbhai niteshbhai, climbed onto the bonnet of the vehicle to retrieve a tarpaulin (tadpatri). While attempting to handle the tarpaulin, he raised his hand holding it, which accidentally came into contact with the r-phase conductor of the 11kv line passing above.as a result of the high-voltage conta | [6 empty] | Awaited | NA | NA | Snapped Conductor Was Safely Reconnected By The Line Staff, And The Feeder Was Restored To Normal Condition. |  | Nadiad | Mehmdabad | Kathlal
28 | Pravinbhai P Tadvi,front of Bharat petrol pump,Vill-Tandalja,Tal-Bodeli,Dist-Chhotaudepur | 2025-05-19 | NFHD | [5 empty] | While working on ganeswad ag feeder pravinbhai-ea kosindra told ladhod ss operator to start govindpura jgy if any tripping in that feeder but due to miscommunication/understanding operator started ganeshwad ag feeder and due to that accident took place | [6 empty] | Awaited | NA | NA | Awareness of such accident given to line Staff & instruct them to do proper communication while working with S S Staff | Not eligible | Baroda O&M | Dabhoi | Kosindra
29 | Rameshbhai Jenabhai Bariya,Vill-Bhimpur,Tal-Lunawada,Dist-Mahisagar | 2025-05-22 | FHO | [5 empty] | According to the preliminary information and police, the victim was mentally unstable. He had climbed the tc dp structure of the agriculture connection located in the farm of shri narsinhbhai balvantbhai bariya of bhimpur village. When the victim climbed the tcdp structure, the power supply was on and hence he might have come in contact with the ht or lt supply, which caused his death. The real cause of death can be know after the pm report comes. | [6 empty] | Awaited | NA | NA | In safety awareness program people are advised not to do any activity near MGVCL distribution network by themselves |  | Godhra | Lunawada | Kotamba
30 | Cows 2 Nos Unknown,Bhumipark,jalavatika,karamsad road,Vill-V V Nagar,Tal-Anand,Dist-Anand | 2025-05-23 | FA | [5 empty] | 2 nos. Of cows short due to leakage current. Possible reason for that is lt cable from lt bushing tc center to dist box was found short and touch to angle of transformer center which may cause return current to pole of tc center, due to this reason the cows may got possible contact with pole of transformer center and got electrocuted and dead on site. | [6 empty] | Awaited | NA | NA | Maintenace of distribution box with lug & 150 mm carried out and LT cable from TC is replaced | Stray cow so no application submit by sdn | Anand | Anand City | V V Nagar
31 | Cow of Shri Arjunbhai Rahabhai Bharvad,Near Dalwadi Kuvo,Vill-Porda,Tal-Petlad,Dist-Anand | 2025-05-23 | FA | [5 empty] | Cow of Shri Arjunbhai Rahabhai Bharvad was passing near Kans near Dalwadi kuvo in Porda village. The 3-ph 4W open LT line passes through said location. Due to rain & storm, LT pole damaged, hence conductor snapped & fell down. Cow came in contact with broken wire & died due to electrocution | [6 empty] | Awaited | NA | NA | New Pole erected and restringing of the line carried out |  | Anand | Petlad | Petlad R
32 | Buffalo of Shrimati Sumitraben Malsingbhai Machhar,karath kheda faliya,Vill-karath kheda,Tal-Zalod,Dist-Dahod | 2025-05-25 | FA | [5 empty] | Both the buffalos were grazing nearby lt pole in farm of hasubhai ratnabhai ninama. Due to cyclone on date 24/05/2025 big tree was fallen on lt line and due to that there was broken lt conductor in farm which was already isolated just after cyclone on date 24/05/2025. During raining time there may be leakage current in neutral conductor of another circuit of same tc and due to that leakage current on tc neutral and for that reason may be leakage current in lt conductor where incident occurred an | [6 empty] | Awaited | NA | NA | Broken open LT conductor was repaired and joined and in another circuit of the same TC which was found with LT ABC open joint was picked with LT tap. |  | Godhra | Dahod | Limdi
33 | Charel Valiben Rakeshbhai,Amba fadiyu,Vill-Lakhanpur,Tal-Fatepura,Dist-Dahod | 2025-05-27 | NFHO | [5 empty] | According to the eyewitness statement, on 27/05/2025 at around 2:00 PM , the victim, Valiben Rakeshbhai Charel, went to start the motor of the well. For some reason, she came into contact with the(open insulated) service wire of the electricity meter and got electrocuted. It was observed that the service wire in near the electricity meter and above the consumer fuse was found to be peeled off and that portion appeared to be burnt. Currently, she is hospitalized and has sustained injuries to her | [6 empty] | Awaited | NA | NA | New service cable provided to the consumer to prevent future occurrence of such accidents. |  | Godhra | Dahod | Fatepura
34 | Ashvinbhai P Chavda,Vill-Bhadkad,Tal-Sojitra,Dist-Anand | 2025-05-27 | NFHD | [5 empty] | As per the statement of eye witness and fellow employees (line staff ) working with him during attending of complaint left hand touchde to dist box of transformer there was a leakage currents on box not known by victim and second hand toched to nearest stay wire during electrocution path completed and electricity shocked to victim suddenly fellow employees has pull backed victims hand and get him immediately to hospital and checked by doctor his health is stable and no major abnormalality found | [6 empty] | Awaited | NA | NA | line staff has been instructed in various safety meeting that due care has been taken while working on line |  | Nadiad | Nadiad City | Vaso R
35 | Pavankumar Bhagatram Bharma,Ranoli GIDC,Vill-Vadodara,Tal-Vadodara,Dist-Vadodara | 2025-05-27 | FHO | [5 empty] | The truck driver was reversing the vehicle under an overhead 11kv power line while the overhead door of the truck was looks open. During the reversing process, the door came into contact with a live wire of 11kv gidc-1 feeder, wire hooked up in the door. The victim, who was running near the truck at the time, accidentally came into contact with the vehicle and was electrocuted | [6 empty] | Awaited | NA | NA | In safety awareness program people are advised not to do any activity near MGVCL distribution network by themselves |  | Baroda O&M | Baroda O&M | Nandesari
36 | Kiranbhai Kanchanbhai Rathva, Kidi Faliyu ,Vill-Ghoghadev,Tal-Chhotaudepur,Dist-Chhotaudepur | 2025-05-28 | FHO | [5 empty] | Victim climb LT Pole of Ghoghadev JGY feeder and carried out unauthorized electrical work and accidentally in contact with live wore and get electrocuted. | [6 empty] | Awaited | NA | NA | In safety awareness program people are advised not to do any activity near MGVCL distribution network by themselves |  | Baroda O&M | Bodeli | Chhotaudepur
37 | Narsinh Udesinh Mahida,New zin,At Mobha road,Tal-Padra,Dist-Vadodara | 2025-05-29 | FHO | [5 empty] | On dtd 29.05.2025 in the morning during heavy wind and rain 1 nos of piludi tree falln on the lt 2.5 sqmm service line supportd through gi wire supplyng 1ph power from pole to consumer meter of late shri narsinh udesinh mahida near zin area mobha road village. Due to whch service lne along with the support gi wire got broken from the middle and the damaged service line section supplying from the pole falls on the wet broken tree. Then the victim was trying to move the fallen tree to clean his sp | [6 empty] | Awaited | NA | NA | Tree removed and service line replaced on 30-06-2025 | 100000/-Dt-25.06.25 | Baroda O&M | Jambuva | Mobha
38 | Jalpaben Hiteshkumar Parmar,Victim's farm,Vill-Gorsan,Tal-Desar,Dist-Vadodara | 2025-05-29 | FHO | [5 empty] | The electrical accidentoccurred due to a broken lt line wire,which snapped during a cyclone at night in the victi's farm located behind her house the accident took place when the victim went to cut grass in the farm, and the broken wire came into contact with her leg,resulting in electrocution. | [6 empty] | Awaited | NA | NA | Broken LT line restringing is carried out with proper LT maintenance work. |  | Baroda O&M | Baroda O&M | Desar
39 | Katara Khimatnbhai Pangalabhai,Behind mama lilava temple,Vill-Pij,Ta-Vaso,Dist-Kheda | 2025-06-05 | FHO | [5 empty] | As per the statement of first eye witness and employees of vaso SDN (line staff ) LT line bare conductor is broken and victim passing near it and came in contact with broken conductor and got electrocuted and 108 ambulance came at the place and declared dead on the spot. | [6 empty] | Awaited | NA | NA | Broken LT line restringing is carried out with proper LT maintenance work. |  | Nadiad | Nadiad City | Vaso R
40 | Het Mihirbhai Patel,Behind Prathmik Shala,Vill-Lambhvel,Ta-Anand,Dist-Anand | 2025-06-08 | NFHO | [5 empty] | Victim (Divyang Child) Had touched line passing near house | [6 empty] | Awaited | NA | NA | coated HT AB Cable provided | departmental case | Anand | Anand | Anand N
41 | Buffalo She,Khanpura Kenal,Vill-Khanpura,Ta-Dabhoi,Dist-Vadodara | 2025-06-10 | FA | [5 empty] | A buffalo was grazing in the field near Khanpura canal then suddenly she touch 11 kv Dangikuva ag long span ht line in clay pot area Then buffalo must have come in contact with these wires and died of electrocution. The real cause of death of the buffalo will be known only after the doctor's PM report. | [6 empty] | Awaited | NA | NA | Restriging of 11 KV HT line conductor Carried at this loaction | under process DBD/T/598/2469 DT:30.06.2025 | Baroda O & M | Dabhoi | Dabhoi (R)
42 | Mithalal Galiyaji Ravat,Vill-Anvarpura,Ta-Zalod,Dist-Dahod | 2025-06-12 | FHO | [5 empty] | Today, on 12/06/2025, at 8:36 am, the residents of Anwarpura village informed the staff of the office attached to Anwarpura village about the death of Mithalal Galiyaji Rawat through telephonically. Competent officers/staff from this office arrived at the scene. At the scene, there is an office of Ultratech Cement on the Jalod-Banswada road in Anwarpura village of Jhalod, in front of which truck no. MP 11 H 1082 was seen below the 11 KV Velpura agricultural line between pole no. 18/26/107 and 18 | [6 empty] | Awaited | NA | NA | In safety awareness program people are advised not to do any activity near MGVCL distribution network by themselves |  | Godhra | Dahod | Zalod
43 | Yusufkhan Mohmadkhan Pathan,Khara kuva,Zanda bazar,Vill-Petlad,Ta-Petlad,Dist-Anand | 2025-06-13 | NFHO | [5 empty] | At time victim (frt line man) is clime on ledar. The power on rsj pole is live he suddenly contact with wire and fall down brife report kept at office and also reppoted to do & ele.insp.latter no petlad(t)/tech/accident/1863dt:16-6-25 | [6 empty] | Awaited | NA | NA | Instructions given to all FRT staff to wear safety gadgets while working on line & not to work on live line & work in presence of MGVCL line staff |  | Anand | Petlad | Petlad T
44 | Owner Zala Raijibhai Gandabhai,Ranchhodpura,Vill-Haldarwas,Ta-Mehemadabad,Dist-Kheda | 2025-06-14 | FA | [5 empty] | the she buffalo of raijibhai gandabhai zala was fasten on small tree it accidentaly came in contact with broken lt wire of 11 kv chandiyel ag fdr due to heavy wind big tree fallen on lt line and pole broken she buffalo died on the spot then site visit done by officer lt line temporarily disconnected from the pole | [6 empty] | Awaited | NA | NA | Proper maintenance is carried out |  | Nadiad | Mehmdabad | Haldarwas
45 | Cow owned by Arjunbhai Dolabhai Parmar,Raghukul Residency near Kanjari bypass raod,Vill-Kanjari,Ta-Halol,Dist-Panchmahal | 2025-06-16 | FA | [5 empty] | On dtd 16.06.2025, at 14.30 hrs, a Cow owned by Arjunbhai Dolabhai Parmar is passing from under the Transformer structure which was installed near gate of Radhukul Residency and during grazing and passing under the Transformer structure suddenly Buffalo was falling down which is inform by eyewitness. | [6 empty] | Awaited | NA | NA | New earthing at the Transformer center with PVC insulation pipe provided |  | Godhra | Halol | Halol T
46 | Shri Sandip Sureshbhai Nayak,Bhikha Faliyu,Vill-Ghoghadava,Ta-Halol,Dist-Panchmahal | 2025-06-16 | NFHO | [5 empty] | While stringing 11 kv conductor for new water works coneectionthe victim and his co worker has asked for isolating the 11kv adia feeder switching to p m ninama alm after his confirmation the victim climed on 11 kv psc pin pole and while stringin conductor he got electric shock in his left shoulder and fell down from the pole and got injuries in his hand and leg | [6 empty] | Awaited | NA | NA | Instruction given to contractor to ensure power dissconnected before line work , use of line earthing before starting line work , Notice given to respective Line Staff . |  | Godhra | Halol | Jambughoda
47 | Chauhan Kalpeshkumar Kalibhai,Vill-Nani Kanod,Ta-Kalol,Dist-Panchmahal | 2025-06-16 | FHO(Pvt.) | [5 empty] | Victim was took bath and after bath, due to liakage of current inside house he got electrocuted and died | [6 empty] | Awaited | NA | NA | New Test Report of RGPR Taken, service wire replaced and condute wiring from open wiring in load side done . |  | Godhra | Halol | Kalol
48 | Cow of Chandakantbhai Rameshbhai Koli,Vill-Koli Faliyu,Vill-Tandalja,Ta-Bodeli,Dist-Chhotaudepur | 2025-06-16 | FA | [5 empty] | A She Cow was grazing in the field near Transformer Center of Tandalja Village Koli Faliya then suddenly she cow may get in touch with earthing wire of transformer center where may be coming the leackage current / return current. Hence, it may got electrical shock & she cow died on the sight. | [6 empty] | Awaited | NA | NA | Maintenace work done at TC Center, Clean surrounding the TC Center | P.M & P.P AWAITED L.NO KSD/T/5863 DT:18.06.2025 | Baroda O & M | Dabhoi | Kosindra
49 | Cow of Shrimati Pagi Hansaben Rameshbhai,Behind Primary School,Vill-Bhadrala,Ta-Shahera,Dist-Vadodara | 2025-06-17 | FA | [5 empty] | On dt.17.06.2025 at 16.30 hrs approx. A cow of shrimati pagi hansaben rameshbhai was passing nearby transformer structure which is installed behind primary school vill. Bhadrala and during grazing near transformer structure cow suddenly fell down and died on spot as per eyewitness statement. Veterinary doctor pm states that victim cow died due to electric shock.no leakage current found at spot but cow might have died due to electric induction around transformer structure because of rainy weather | [6 empty] | Awaited | NA | NA | GI Wire covered with earthing pipe. |  | Godhra | Godhra | Sahera-II
50 | Cow and Bufellow of Shri Gagjibhai Jahabhai Bharwad,Vill-Vanoda,Ta-Galteshwar,Dist-Kheda | 2025-06-17 | FA | [5 empty] | the accident occurred due to the snapping of LT conductor of 4W open LT line because of snapping of Conductor due to heavy rain and wind. The broken conductor came in direct contact with one cow and one buffalo while grazing and got electrocuted and died on the spot. | [6 empty] | Awaited | NA | NA | LT line maintenance carried out |  | Nadiad | Nadiad | Balasinor R
51 | Cows & Bull of Darshanbhai Madhubhai Rabari,Vill-Sayma,Ta-Khambhat,Dist-Anand | 2025-06-17 | FA | [5 empty] | As per eye winess, Darshanbhai Madhubhai Rabari statement had gone out to graze his Cows & Bull on Dt:17.06.2025 around 10:00 Am. In distribution box of Sayma School TC one phase insulation was deteriorated and touch the box. When Bull was passing near to transformer center of Sayma school, it may be came in contact with leakage current due to heavy rain & it got electrocuted & died at site. | [6 empty] | Awaited | NA | NA | Distribution Box maintenance carried out |  | Anand | Petlad | Cambay R
52 | Cow of Shri Sartanbhai Dalabhai Rathava,Liti Faliyu,Vill-Ranipura,Ta-Halol,Dist-Panchmahal | 2025-06-17 | FA | [5 empty] | A Cow While Grazing Came Near Tc And Touched The Earthing Wire Of Tc And Due To Leakage Curreent Got Electrocuted | [6 empty] | Awaited | NA | NA | New eathing of TC with PVC Insulation carried out. | Initial compensation of 15,000 done on 03-07-2025 with UTI No 60009 | Godhra | Halol | Jambughoda
53 | Cow of Braman Laxamanbhai Govindbhai,Near gardan,Vill-Parathampura,Ta-Savli,Dist-Vadodara | 2025-06-17 | FA | [5 empty] | On date 17.6.2025, at approximately 5:30 pm, a cow belonging to shri Braman laxmanbhai govindbhai was returning from grazing as usual. When the cow’s foot touched the earthling wire near the DODP electricity pole of the 11 kv dholeshvar jgy feeder near the garden in prathampura village, due the rainy weather, due to the moisture effect, the cow got electrocuted and died. | [6 empty] | Awaited | NA | NA | DODP maintenance carried out with earthing |  | Baroda O & M | Baroda O&M | Savli
54 | She Buffalo of Damor Kantiben Situbhai,Padaliya falyu,Vill-Panam,Ta-Dhanpur,Dist-Dahod | 2025-06-18 | FA | [5 empty] | On dated 18.06.25 she buffalo of kantiben situbhai damor was grazing near tc structure of bsnl tower. While grazing it came in contact with gi earthing wire of transformer and due to leakage current on gi wire it got electrocuted | [6 empty] | Awaited | NA | NA | Gi earthing wire of transformer is provided with pvc pipe. |  | Godhra | Dahod | Dhanpur
55 | She Cow & She Bufallo Shri. Raijibhai Masurbhai Khant,Vill-Ghandhari (Khant),Ta-Virpur,Dist-Mahisagar | 2025-06-18 | FA | [5 empty] | On June 18, 2025, at approximately 16:00 Hrs, a fatal accident occurred in Village Khant Gandahri resulting in the electrocution and death of one cow and one buffalo, both belonging to Shri. Raijibhai Masurbhai Khant. Preliminary investigation indicates that the animals came into contact with a live, snapped Low Tension (LT) overhead conductor. The snapping of the conductor was attributed to a heavy Gorus Ambli tree falling onto the LT line due to heavy wind and rain. The affected LT line was co | [6 empty] | Awaited | NA | NA | Tree cutting and proper maintenance work done. |  | Godhra | Lunawada | Virpur
56 | Ox(balad) of Bhabhor Bhursing Bhai Natvarbhai,Kachhala Faliyu,Vill-Dhavdiya,Ta-Zalod,Dist-Dahod | 2025-06-18 | FA | [5 empty] | Today, on 18/06/2025, on the information received by telephonic that the Ox(balad) of Bhabhor Bhursing Bhai Natvarbhai died due to electrocution in Kachhla Phalia of Dhavadiya village, the officer/employee of this office arrived at the spot. While inspecting the spot, it was found that the pin was fired due to a technical fault on pole no. 53/170/11 of the 11 KV Garadu JGY line passing near the house of Bhabhor Sureshbhai Natvarbhai in Kachhla faliya of Dhavadiya village, due to which the wire b | [6 empty] | Awaited | NA | NA | At location 11 KV Pin Insulator replaced with polymeric pin insulator on pole |  | Godhra | Dahod | Zalod
57 | Ox(Balad) of Vasaiya Maheshbhai Gavajibhai,Nisal Faliyu,Vill-Melaniya,Ta-Zalod,Dist-Dahod | 2025-06-19 | FA | [5 empty] | Today, on 19/06/2025, Vasaiya Maheshbhai Gavajibhai's Ox(balad) met with an electric accident in Nishal Phalia of Melaniya village. After receiving telephonic information, we went to inspect the place. There is an LT electricity pole on the side of the street on which LT ABC 2 wires are jointed to LT ABC. Due to the rainy weather in the evening, the pole became wet with water. Upon further inspection of the place, it was seen that the joint of the LT cable on the pole came into contact with the | [6 empty] | Awaited | NA | NA | At location LT ABC cable is replaced |  | Godhra | Dahod | Zalod
58 | Cow of Khant Hirabhai Kalubhai,Pateliya Faliyu,Vill-Panam Palla,Ta-Lunawada,Dist-Mahisagar | 2025-06-19 | FA | [5 empty] | On 19.06.2025,As Per Eyewitness Statement And On Site Visit It Was Known That ,At Approximately 08:30 Am ,A Cow Belonging To Hirabhai Kalubhai Khant Was Electrocuted While Gazing For Grass Nearby Panam Palla,Pateliya Faliyu Transformer Centre.The Incident Occured When The Animal Came Into Contact With An Earthing Wire,In Which Neutral Current Was Flowing,Due To Internal Equipment Short Of Consumer Pateliya Ramilaben Ramanbhai Having Cons No 07774001786.Acutal Cause Of Accident Will Be Confirmed | [6 empty] | Awaited | NA | NA | Transformer centre GI wire covered with earthing pipe . |  | Godhra | Lunawada | Lunawada-1
59 | Goat of Parmar Gunvantbhai Gamirbhai,Sim vistar,Vill-Sonipur,Ta-Galteshwar,Dist-Kheda | 2025-06-19 | FA | [5 empty] | Accident Occured Due to Snapping of conductor of 2w open LT line heavy rain and wind the conductor came direct contact with goat which got electroculated and died on spot | [6 empty] | Awaited | NA | NA | LT line maintenance carried out |  | Nadiad | Nadiad | Galteshwar
60 | Buffalo,Bharwad Faliyu,Vill-Indral,Ta-Halol,Dist-Panchmahal | 2025-06-19 | FA | [5 empty] | Buffalo grazing near tc where water accumulated contact with earthing wire and may got electrocuted | [6 empty] | Awaited | NA | NA | New earthing at the Transformer center with PVC insulation pipe done |  | Godhra | Halol | Halol R
61 | Bullock,Kalam Vashahat,Vill-Kundiucha,Ta-Bodeli,Dist-C'udepur | 2025-06-19 | FA | [5 empty] | Grazing near by x'mer center and contact with earthing wire and may got electrocuted | [6 empty] | Awaited | NA | NA | Transformer centre GI wire covered with earthing pipe . |  | Baroda O & M | Bodeli | Bodeli
62 | Buffalo of Shri Damor Parasbhai Tersingbhai,Gamtal Naer PHC,Vill-Kathala,Ta-Dahod,Dist-Dahod | 2025-06-19 | FA | [5 empty] | Buffaloes were grazing in the fields and were passing nearby the flour mill of Shri Kaushik A Nayak (Cons No-51601013574). The Service of said consumer was passing across the road where the consume had privately erected an iron pole on which they had tied the service wire of the electricity connection, which had cracked due to unknown reasons, leading the leakage of current on the iron pole. The victim (Buffalo) would have got into proximity of the iron pole while passing nearby and got electr | [6 empty] | Awaited | NA | NA | New LT pole have been erected across the road to support the new service cable provided to the consumer to prevent future occurrence of such accidents. |  | Godhra | Dahod | Dahod R
63 | Dabhi Lilaben Nileshbhai,Meldi farm,Vill-Haldarwas,Ta-Mehamadabad,Dist-Kheda | 2025-06-19 | FA | [5 empty] | as per messege received from buffalo owner smt dabhi lilaben nileshbhai on dtd 19.06.2025 due to heay rain buffalo was scared and started running around in the farm as per eye witness statement the buffalo suddenly stuck on the transformer center so electrocuted and died on the spot but awaited for postmortem for exact cause of death at the time of site visit by sdo. | [6 empty] | Awaited | NA | NA | Transformer centre maintenance carried out and GI wire covered with earthing pipe . |  | Nadiad | Mehmdabad | Haldarwas
64 | Vasava Naranbhai Pasabhai,Mental Hospital Road,Vill-Vadodara,Ta-Vadodara,Dist-Vadodara | 2025-06-20 | FHO | [5 empty] | Accident occured due to leakage current came from LT network of Vallabhnagar TC, Sayajibaug Feeder of Tower Sdn. The leakage current passed from LT network to Streetlight messenger wire and this wire touched to RSJ new erected pole on which the Victim was working. | [6 empty] | Awaited | NA | NA | LT AB Cable and 1 PH street light Cable saparated and LT Spacer provided and at new erected pole LT Shckle provided with angle by street light department. | N.A. | Baroda City | Vishwamiri E | Karelibaug
65 | Shri Sanjaybhai Ratnabhai Kharadi,Nr Anganvadi,Vill-Ghodali,Ta-Mehamadabad,Dist-Kheda | 2025-06-20 | NFHD | [5 empty] | As per eye witness statement 11 kv ghodali village from 66 kv nenpur ss one bird pigeon trapped on pin pole top fitting on 11 kv ghodali feeder victim tried to remove this trapped bird for saving it life at that time victim called to jinjar ss to trip 11 kv sojali jgy fdr 11 kv sojali jgy fdr also passing parallel to the 11 kv ghodali feeder victim got electrocuted for primary treatment he has admitted ved hospital khatraj and then he has admitted in shelby hospital naroda for further treatment | [6 empty] | Awaited | NA | NA | Aware line staff to use safety gadgets in safety meeting |  | Nadiad | Mehmdabad | Haldarwas
66 | Sukhiben Kalabhai Parmar,Kalaji Na Muvada,Vill-Danadara,Ta-Kapadwanj,Dist-Kheda | 2025-06-21 | FA | [5 empty] | Due To heavy rain,phase wire shorted with stay of transformer stucture and due to this power flows through earthing of transformer and due to this buffalo get electric shock and died on spot | [6 empty] | Awaited | NA | NA | Phase Wire Shortening With Stay Wire Removed |  | Nadiad | Mehmdabad | Kapadwanj E
67 | Owner Zala Jesangbhai Raijibhai,Vill-Haldarwas,Ta-Mehamadabad,Dist-Kheda | 2025-06-21 | FA | [5 empty] | the she buffalo of jesangbhai raijibhai zala was fasten on small tree it accidentally came in contact with broken lt wire of 11 kv rohisa ag fdr big tree was fallen on lt line due to rain and wind pressure and lt open line broken she buffalo died onspot then site visit done by officer lt line temporarily disconnected from the pole | [6 empty] | Awaited | NA | NA | Transformer centre maintenance carried out and GI wire covered with earthing pipe . |  | Nadiad | Mehmdabad | Haldarwas
68 | Buffalo of Shri Khodabhai Bhimabhai Bharwad,Gokalpura,Vill-Manjusar,Ta-Savli,Dist-Vadodara | 2025-06-21 | FA | [5 empty] | on 21-6-25 at 07:00 pm a buffalo belonging to Shri Khodabhai Bhimabhai Bharwad was grazing at dusk and came into contact with a broken LT wire of 11 kv manjusar AG feeder due to rainy condition and moisture on the ground likely exacerbated in situation, casuing electrocuted and died | [6 empty] | Awaited | NA | NA | Broken LT line restringng carried out with proper LT maintenance work. |  | Baroda O & M | Baroda O & M | Manjusar
69 | Bullock of Shri Dadudiyabhai Keshariyabhai,D P Faliyu,Vill-Motikadhai,Ta-Kawant,Dist-C'udepur | 2025-06-21 | FA | [5 empty] | Shri Dadudiyabhai keshiyabhai Rathwa (owner) was coming from his farm with two two bullocks.TC was standing besides the road.When he was paasing through this TC structure one left side Bullock touched th PSC pole and felt leakage current ,1 Bullock fell down on the ground and died on spot. | [6 empty] | Awaited | NA | NA | Transformer centre maintenance carried out and GI wire covered with earthing pipe . |  | Baroda O & M | Bodeli | Kwant
70 | She boffalo of Shri Dalsukhbhai Balubhai Rathava,Vill-Vijol,Ta-C'udepur,Dist-C'udepur | 2025-06-21 | FA | [5 empty] | Shri Dalsukhbhai Balubhai Rathava was taking his buffaloes for grazing. Suddenly one of the buffalo distracted and entered into the farm of Sabur bhai Mangu bhai rathava.There is a transformer in the same farm,at the time grazing she(buffalo) might passed near by transformer. The female buffalo might have come in contact with the earthing wire and might got electrocuted due to leakage current and might have died on the spot. MGVCL team checked leakage current on the TC, PSC pole but didnt find any leakage current. The exact reason for the leakage current is suspected.Thus, exact reason for death of buffalo can be ascertained from post mortem report. | [6 empty] | Awaited | NA | NA | Transformer centre maintenance carried out and GI wire covered with earthing pipe . |  | Baroda O & M | Bodeli | Tejgadh
71 | Afshana Salimbhai Shaikh,Amin auto road,Vill-Anand,Ta-Anand,Dist-Anand | 2025-06-22 | FHO | [5 empty] | according to eye witness shaikh zahedaben satarbhai (grandmother of victim) on dated 22.06.25 during day period private streetlight twincore broken and touch to iron shade.iron shed erected under iron shed.at evening victim touches to iron rod and electrocuted. | [6 empty] | Awaited | NA | NA | Street light private wire remove | no pm done by party , no compensation application submit atsdn office. Also not llyable compensation | Anand | Anand City | Shastri
72 | 01 Nos Buffalo,Chitarwada road,Vill-Kasbara,Ta-Tarapur,Dist-Anand | 2025-06-24 | FA | [5 empty] | Due to broken stay wire of 11 kv ab switch may came into induction zone of jumpers of ab switch.at that time buffalo passing nearby pole and came into contact and got electrocuted.at the time of incident rain was raining with wind pressure.. | [6 empty] | Awaited | NA | NA | Broken Stay Wire Removed |  | Anand | Petlad | Tarapur
73 | She Cow,Shivalay Tirth,Vill-Ankhol,Ta-Vadodara,Dist-Vadodara | 2025-06-26 | FA | [5 empty] | Cow roaming around transformer center, reverse current flowing through private preimises wiring to neutral earthing of the transformer, cow came in contact with earthing wire and died on the spot | [6 empty] | Awaited | NA | NA | Consumer was asked for fresh new wiring.Consumer Submitted new Test Report on Dtd. 29-06-2025. |  | Baroda O & M | Jambuva | Khatamba
74 | Cow,Vill-Vadodara,Ta/Dist-Vadodara | 2025-06-28 | FA | [5 empty] | During investigation it was found that cow passing near lt pole of bhadra kacheri tc, at the same time the heavy raining with wind and lightning stroke, the lt jumper of the bhadra kacheri tc touch with an angle of iron pole and the leakage current passing through the iron pole, the cow was contact with surround area of leakage current and electrocuted and it was died on the spot. | [6 empty] | Awaited | NA | NA | Rectification Done of LT Jumper and LT pole maintenance activity was carried out | owner not found | Baroda City | Vishwamitri E | Mandvi
75 | Jalamsinh Dhanabhai Chauhan,Jibhaypura vistar,Vill-Ahima,Ta-Umreth,Dist-Anand | 2025-06-28 | FHO | [5 empty] | Victim was doing tree cutting on temporay shed situated outside of house and during tree cutting work victim may be in contact with 2w abc line and got electric shock and died. | [6 empty] | Awaited | NA | NA | Maintainance of AB cable carried outand damaged ab cable is repaired | waiting for pm pp and concent of victim family | Anand | Anand | Umreth R
76 | Gayatriben Hiteshkumar Raval,Raval faliyu,Vill-Sundara,Ta-Petlad,Dist-Anand | 2025-06-29 | FHO | [5 empty] | As per eye witness statement and p.a.r.as per site visit victim was washing cloths in chokdi in front of her house.at that time rain was raining with wind pressure where accident occured,adjacent house has iron tin shed structure in front of his house where 1-ph conn is present.the service libe of the same house was with g.i.wire pasibg over this tin shed structure ,while rain was raining with wind pressure a near by neem tree branch was accidentally broken and fallen on this live service line w | [6 empty] | Awaited | NA | NA | Service wire of consumer is replaced by new service wire |  | Anand | Petlad | Tarapur
77 | Buffalo of Narvatbhai Amrabhai Rathva,Vill-Mahadevia,Ta-Ghogamba,Dist-Panchmahal | 2025-06-29 | FA | [5 empty] | As per buffalo owner's statement,buffalo was passing near the ab switch center and started scratching with stay wire and due to scratching force stay wire disconnected from anchor rod due to corrosive effect and stay wire came in touch with 11kv jumper of 11kv paroli feeder and buffalo got electrocuted. | [6 empty] | Awaited | NA | NA | New guy Set installed and addition Guy Set for support installed . |  | Godhra | Halol | Ghoghamba
78 | Buffalo of Shri Kailashben Balvansinh Solanki,Jiliya Faliyu,Vill-Sureli,Ta-Kalol,Dist-Panchmahal | 2025-06-30 | FA | [5 empty] | On dts. 30.06.2025 around 17.00 hrs, a buffalo of shree kailashben balwantsinh solanki was returning to her home after grazing and passing near through the transformer sturcture located at jilliya faliya, accidentally she got electrolucted and fell down on land and died on spot. Cause of death and details investigation is in process. Fir copy, postmortem report and police panchnama reports are stiill awiating from officials. | [6 empty] | Awaited | NA | NA | New earthing at the Transformer center with PVC insulation pipe done |  | Godhra | Halol | Vejalpur
79 | 01 Cow owned by Punjabhai kalubhai bariya,dudhela navi vasahat,Vill-Koydam,Ta-Virpur,Dist-Mahisagar | 2025-06-30 | FA | [5 empty] | On 30.06.2025 at 12:30 PM a cow owned by Punjabhai kalubhai bariya some how got near transformer center at the time due to heavy rain in previous days land near transformer center got erosioned and earthing wire got opened. Cow came in contact with the earthing wires and got electrocuted and died on the spot. | [6 empty] | Awaited | NA | NA | Transformer earthing reactivation done. GI wire covered with earthing pipe . |  | Godhra | Lunawada | Virpur

## MG SoP 03
SOP 3-00B - REGISTER FOR COMPILING THE COMPLAINTS - CLASSIFIFCATION WISE
Quarter of the year : Q-I (Apr-May-June-2025-26)
Name of Office : MGVCL Corporate Office
Classification | Nature of Complaints | Pending complaints of previous qtr. | Complaints received during the qtr. | Total Complaints | No. of Complaints redressed during the quarter. |  |  | Balance Complaints to be redressed
[5 empty] | Within stipulated time. | Beyond stipulated time. | Total
| 1 | 2 | 3 | 4=2+3 | 5 | 6 | 7=5+6 | 8=4-7
A | Interruption in power supply | 0 | 173659 | 173659 | 173615 | 44 | 173659 | 0
I | Loose connections at meter, MCB or service line or from pole | 0 | 79317 | 79317 | 79303 | 14 | 79317 | 0
II | Interruption due to line breakdown | 0 | 48209 | 48209 | 48201 | 8 | 48209 | 0
III | No power complaint on account of blowing of HT/ DropOut (DO)/ LT fuse | 0 | 26405 | 26405 | 26401 | 4 | 26405 | 0
IV | Interruption due to failure of transformer or distribution transformer MCB | 0 | 6051 | 6051 | 6051 | 0 | 6051 | 0
V | Load shedding/ schedule outages | 0 | 13677 | 13677 | 13659 | 18 | 13677 | 0
B | Quality of power supply | 0 | 8415 | 8415 | 8415 | 0 | 8415 | 0
I | Ordinary case, which requires no augmentation, | 0 | 5079 | 5079 | 5079 | 0 | 5079 | 0
II | Where augmentation is required. | 0 | 1878 | 1878 | 1878 | 0 | 1878 | 0
III | Harmonics related issue | 0 | 26 | 26 | 26 | 0 | 26 | 0
IV | Neutral voltage related issue | 0 | 428 | 428 | 428 | 0 | 428 | 0
V | Voltage variations related issue | 0 | 1004 | 1004 | 1004 | 0 | 1004 | 0
C | Meters | 0 | 32595 | 32595 | 32548 | 47 | 32595 | 0
I | Stopped/Defective Meters. | 0 | 13380 | 13380 | 13373 | 7 | 13380 | 0
II | Meter accuracy test (Fast/ Slow | 0 | 1239 | 1239 | 1237 | 2 | 1239 | 0
III | Burnt Meter | 0 | 575 | 575 | 575 | 0 | 575 | 0
IV | Stolen Meter | 0 | 0 | 0 | 0 | 0 | 0 | 0
V | Billing on average basis for more than two hills | 0 | 3967 | 3967 | 3955 | 12 | 3967 | 0
VI | Meter boxes/ metering system | 0 | 13434 | 13434 | 13408 | 26 | 13434 | 0
D | Overhead lines | 0 | 6453 | 6453 | 6447 | 6 | 6453 | 0
I | Loose Wires | 0 | 5016 | 5016 | 5010 | 6 | 5016 | 0
II | Inadequate ground clearance | 0 | 1437 | 1437 | 1437 | 0 | 1437 | 0
E | Bills | 0 | 12042 | 12042 | 12042 | 0 | 12042 | 0
I | For current bills where no additional information is required | 0 | 7791 | 7791 | 7791 | 0 | 7791 | 0
II | Where additional information relating to correctness of reading etc. is required, | 0 | 3346 | 3346 | 3346 | 0 | 3346 | 0
III | Final bill for vacation of premises/ change of occupancy | 0 | 738 | 738 | 738 | 0 | 738 | 0
IV | Change of Tariff | 0 | 167 | 167 | 167 | 0 | 167 | 0
F | Service connections | 0 | 19092 | 19092 | 19092 | 0 | 19092 | 0
I | Where extension of LT line up to 150 Metre is required | 0 | 4867 | 4867 | 4867 | 0 | 4867 | 0
II | Where extension of LT line of more than 150 Metre and/or augmentation of distribution transformer is required | 0 | 1576 | 1576 | 1576 | 0 | 1576 | 0
III | Where erection of new distribution transformer is required | 0 | 1630 | 1630 | 1630 | 0 | 1630 | 0
IV | Where erection of new HT line and distribution transformer is required and/ or existing HT line network is required to be augmented. | 0 | 2197 | 2197 | 2197 | 0 | 2197 | 0
V | Where EHT level line and/ or Sub-station is required to be erected and/ or augmented | 0 | 2 | 2 | 2 | 0 | 2 | 0
VI | Modification in connected load | 0 | 2802 | 2802 | 2802 | 0 | 2802 | 0
VII | Name change/reconnection/ change of category | 0 | 5926 | 5926 | 5926 | 0 | 5926 | 0
VIII | In case connection is denied after payment against demand note | 0 | 40 | 40 | 40 | 0 | 40 | 0
IX | Transfer of connection | 0 | 52 | 52 | 52 | 0 | 52 | 0
G | Request for reconnection/ consumer wanting disconnection | 0 | 2032 | 2032 | 2032 | 0 | 2032 | 0
H | Refund of amount due in regard to temporary connection | 0 | 876 | 876 | 876 | 0 | 876 | 0
I | Street Light complaint | 0 | 855 | 855 | 855 | 0 | 855 | 0
J | Others | 0 | 20043 | 20043 | 20043 | 0 | 20043 | 0
TOTAL |  | 0 | 276062 | 276062 | 275965 | 97 | 276062 | 0
The format is to be sent quarterly The quarterly reporting of the year means reporting for the period 1st Quarter as Apr-Jun, 2nd Quarter as Jul-Sep, 3rd Quarter as Oct – Dec and 4th Quarter as Jan - Mar of the financial Year. For any other complaints not mentioned in the classification, the sequence for J can be used.

## MG SoP 04
Name of Distribution Licensee: M.G.V.C.L.
Quarter of the year : Q-I (Apr-May-June-2025-26)
Year: 2025-26
Performa SoP 004 : Publicity carried out while displaying the contact details of consumer complaints centers.
Particulars should also cover the details of publication of “Manual of Practice for Handling Complaint/ Consumer Charter/ Complaint Charter”, consumer awareness program conducted, advertisement done through various media like TV, newspaper, radio, pamphlets & booklet distributions, Displays etc. The development of website and any medium through which public education is carried out can be included.
Sr. No. (1) | Actions or steps carried out by distribution licensee towards public awareness in the quarter (2) | Likely number of consumers influenced (3) | Details about Media (4)
the Media
1 | RTI Officers Name is displayed at customer care centre on each office | 3668004 | -
2 | Necessary information regarding time schedule for new connection and solving complaints is display on the board. | 3668004 | -
3 | Contact nos. of various officers of the company for emergency contact is also displayed at customer care centre. | 3668004 | Website/ News paper
4 | Safety Meeting with Line Staff at various S/dn,Divisions on Every Monday (Line staff influenced) | 23632 | Meeting/ line staff infulenced
The format is to be sent quarterly. The column 2 shall depict any steps taken by licensee in direction of consumer awareness and educating the consumer through conducting of seminars, meetings, distribution of pamphlets, through guidelines placed on website, formulating team that visit rural area educating consumers on billing, safety measures and procedures for grievance redressal, etc. The quarterly reporting of the year means reporting for the period 1st Quarter as Apr – Jun, 2nd Quarter as Jul – Sep, 3rd Quarter as Oct – Dec and 4th Quarter as Jan – Mar of the financial year.

## MG SoP - 05
Name of Distribution Licensee: M G V C L
Financial Year: 2025-26
Quarter : Q-I (Apr-25 TO Jun-25)
Performa SoP 005: Failure of Distribution Transformer
Sr. No. | Name of Circle | Nos. of existing Distribution Transformers at the start of the quarter | Nos. of Distribution Transformers added during the quarter | Total number of Distribution Transformers on end of quarter | Total number of Distribution transformer failed during quarter | % failure rate of Distribution transformer
|  | A | B | C=A+B | D | H = (D)*100/C
1 | Baroda O&M | 62642 | 464 | 63106 | 775 | 1.2281
2 | Baroda City | 11338 | 203 | 11541 | 29 | 0.25128
3 | Anand | 28761 | 154 | 28915 | 346 | 1.1966
4 | Nadiad | 37559 | 271 | 37830 | 341 | 0.9014
5 | Godhra | 67017 | 359 | 67376 | 928 | 1.3773
| MGVCL | 207317 | 1451 | 208768 | 2419 | 1.1587

## SoP007
Name of Distribution Licensee: M G V C L
Quarter : Q-I (April-May-June-2025)
Year: 2025-26
Performa SoP 007: Sample Test result for Neutral Voltage
Compliance Sample Test Report for Neutral Voltage
-1 | -2 | -3 | -4 | -5 | -6
Sr. No | Category of consumers | Sample Size | Standard specified in regulation | Deviation of results from the sample test (Numbers) | % age compliance
|  | (Numbers) |  |  | (6) = (5)*100/(3)
| LT consumers | 1441 | 2% | 0 | 0
1 | Domestic | 1023 | 2% | 0 | 0
2 | Commercial | 242 | 2% | 0 | 0
3 | Industrial | 23 | 2% | 0 | 0
4 | Agricultural | 143 | 2% | 0 | 0
5 | Public water works | 10 | 2% | 0 | 0
| HT consumers |  | 2%
6 | HT industrial | 5 | 2% | 0 | 0

## SoP008
Name of Distribution Licensee: M G V C L
Quarter : Q-I (April-May-June-2025)
Year: 2025-26
Performa SoP 008: Sample Test result for Voltage variations
Compliance Sample Test Report for voltage variations
-1 | -2 | -3 | -4 | -5
Voltage Level | Sample Size (numbers) | Limit or prescribed standard | Deviation of results from the sample test (Numbers) | % age compliance
(5) = (4)*100/(2)
Low Voltage | 56 | +6% to -6% | 0 | 0
High Voltage | 24 | +6% to -9% | 0 | 0
Extra High Voltage | 1 | +10% to -12.50% | 0 | 0

## SoP009
Name of Distribution Licensee: M G V C L
Quarter : Q-I (April-May-June-2025)
Year: 2025-26
Performa SoP 009: Sample Test result for Harmonics
Compliance Sample Test Report for Harmonics
-1 | -2 | -3 | -4 | -5 | -6
Sr. No | Category of consumers | Sample size (Numbers) | Limit or standard prescribed | Deviation of results from the sample test (Numbers) | %age compliance
(6) = (5)*100/(3)
1 | LT consumers | 33 | 3.5% | 0 | 0
2 | HT consumers | 4 | 3% | 0 | 0
3 | EHT consumers | 1 | 3% | 0 | 0
Note: The licensee shall also submit along with the above harmonic data, the records of customer wise drawls of harmonic currents measured at various strategic points.
The formats SoP 008, SoP 009 and SoP 010 have to be sent annually.
For the purpose of annual submissions, the year end has to be considered as the end of December month of a particular year.

## 010
Q-1 (Apr-June-25)
Year: 2025-26
SoP 010 – A System Average Interruption Frequency Index (SAIFI)
Sr. No | Month | Number of Sustained Interruptions during the Reporting Period = Ai | Number of Interrupted Customers for Sustained Interruption events during the Reporting Period = Ni | Total number of Customers Served for the Areas = Nt | Total Number of Interrupted Customers for Sustained Interruption events during the Reporting Period = Σ (Ai x Ni) | SAIFI = Σ (Ai x Ni) /Nt
1 | 2 | 3 | 4 | 5 | 6 = Σ (3 x 4) | 7 = 6 / 5
1 | 2025-04-01 | 24720 | 3224468 | 3666109 | 29641703 | 8.09
2 | 2025-05-01 | 55146 | 3356998 | 3662903 | 78757400 | 21.5
3 | 2025-06-01 | 56364 | 3353330 | 3668004 | 79757735 | 21.74
|  | 136230 | 9934796 | 10997016 | 188156838 | 17.1098

## 011
Q-1 (Apr-June-25)
Year: 2025-26
SoP 011 – System Average Interruption Duration Index (SAIDI)
Sr. No | Month | Number of Sustained Interruptions during the Reporting Period = Ai (Nos) | Total Outage Duration (Hr : Min) | Restoration time for each Interruption Event = Ri (Hr : Min) | Number of Interrupted Customers for Sustained Interruption events during the Reporting Period = Ni (Nos) | Total Customer Interruption Duration = Ri x Ni (Hr : Min) | Total Number of Customers Served for the Areas = Nt (Nos) | Cumulative Customer Interruptions Duration = Σ(Ri x Ni) (Hr : Min) | SAIDI = Σ (Ri x Ni) / Nt (Hr : Min)
1 | 2 | 3 | 4 | 5 = 4 / 3 | 6 | 7 = 5 x 6 | 8 | 9 = Σ (5 x 6) | 10 = 9 /8
1 | 2025-04-01 | 24720 | 13413:16 | 0:33 | 3224468 | 2102-04-24 01:24 | 3666109 | 1511256:32 | 0:25
2 | 2025-05-01 | 55146 | 37808:41 | 0:41 | 3356998 | 2161-09-08 04:38 | 3662903 | 2299562:29 | 0:38
3 | 2025-06-01 | 56364 | 32693:51 | 0:35 | 3353330 | 2123-02-23 13:10 | 3668004 | 1739385:22 | 0:28
|  | 136230 | 83915:48 | 0.075694 | 9934796 | 6023515:12 | 10997016 | 5550204:23 | 0:30

## 012
Q-1 (Apr-June-25)
Year: 2025-26
SoP 012 – : Momentary Average Interruption Frequency Index (MAIFI)
Sr. No | Month | Total Number of Momentary interruptions = Imi | Total Number of Consumers affected due to Momentary Interruption Events during the Reporting Period = Nmi | Number of Customer Momentary Interruptions = IMi * Nmi | Total Number of Customers Served for the Areas = Nt | Cumulative Momentary Customer Interruptions = Σ (Imi x Nmi) | MAIFI = Σ (IMi x Nmi)/ Nt
1 | 2 | 3 | 4 | 5=3*4 | 6 | 7 = Σ (3 x 4) | 8=7/6
1 | 2025-04-01 | 45827 | 2970688 | 136137718976 | 3666109 | 60996188 | 16.64
2 | 2025-05-01 | 67368 | 3162547 | 213054466296 | 3662903 | 101641078 | 27.75
3 | 2025-06-01 | 66064 | 3125258 | 206467044512 | 3668004 | 102007090 | 27.81
|  | 179259 | 9258493 | 555659229784 | 10997022 | 264644356 | 24.0651

## 013
Q-1 (Apr-June-25)
Year: 2025-26
SoP 013 – : Customer Average Interruption Duration Index (CAIDI)
Sr. No | Month | Total Number of Sustained Interruptions during the Reporting Period = Σ Ai | Total Restoration time for Interruption Events = Σ Ri (Hr : Min) | Total Number of Interrupted Customers for Sustained Interruption events during the Reporting Period = Σni | CAIDI=Σ (Ri x Ni) / Σ (Ai x Ni) = SAIDI/ SAIFI
1 | 2 | 3 | 4 | 5 | 6 = (4 x 5) / (3 x 5)
1 | 2025-04-01 | 24720 | 0:33 | 3224468 | 3.09
2 | 2025-05-01 | 55146 | 0:41 | 3356998 | 1.77
3 | 2025-06-01 | 56364 | 0:35 | 3353330 | 1.29
|  | 136230 | 1:49 | 9934796 | 2.05

## SoP - 15
Name of Distribution Licensee: M G V C L
Financial Year: 2025-26
Quarter : Q-I (Apr-25 TO Jun-25)
Performa SoP 015: Faulty Meters Replacement
Consumer Category | No. of faulty meters at the start of the quarter | No. of faulty meters added during the quarter | Total no. of defective / faulty Meter | No. of faulty Meters repaired and replaced | No of faulty meters pending at the end of the quarter | Remark
| 1 | 2 | (3)=(2)+(1) | 4 | (5)=(3)-(4)
Single Phase | 9340 | 22450 | 31790 | 19128 | 12662
Three Phase | 2588 | 7515 | 10103 | 4842 | 5261

## SoP 16
Name of Distribution Licensee: M G V C L
Quarter : Q-I (April-May-June-2025)
Year: 2025-26
Performa SoP 016: Compensation details
COMPENSATION DETAILS
Sr. No. | Service Area | Compensation payable to | Claimed |  | Payable
|  | consumer for the period of default in case of violation of standard | No. of cases | Amount (Rs.) | No. of cases in which compensation is payable | Amount payable (Rs.) | Amount paid (Rs.)
1 | Registration of complaint and intimation of Unique complaint Number to the Complainant | Rs. 50/- for each default | 0 | 0 | 0 | 0 | 0
2 | Issuance of Demand Note for New Connection, Load Enhancement, Shifting of connection at other premises, Conversion of Service, Temporary Supply, Shifting of Service Connection in exiting premises, Deviation of line and Shifting of equipments | Rs. 50 for each day of default. | 0 | 0 | 0 | 0 | 0
3 | New Connection, Load Enhancement, Shifting of connection at other premises and Conversion of Service where no Network erection and/or augmentation is required. | Rs. 50 for each day of default. | 0 | 0 | 0 | 0 | 0
4 | New Connection, Load Enhancement, Shifting of connection at other premises and Conversion of Service where Network erection and/or augmentation is required. | Rs. 50 for each day of default. | 0 | 0 | 0 | 0 | 0
5 | Release of temporary supply | Rs. 50 for each day of default. | 0 | 0 | 0 | 0 | 0
6 | Shifting of meter/services in the existing premises | Rs. 50 for each day of default. | 0 | 0 | 0 | 0 | 0
7 | Shifting of LT/HT lines |  | 0 | 0 | 0 | 0 | 0
8 | Shifting of Transformer structures |  | 0 | 0 | 0 | 0 | 0
9 | Settlement of amount for refunding of excess amount after completion of work. |  | 0 | 0 | 0 | 0 | 0
10 | Transfer of Service Connection with respect to change of name or change of ownership | Rs. 50 for each day of default. | 0 | 0 | 0 | 0 | 0
11 | Application from consumer requesting Change in Tariff Class/Category. | Rs. 50 for each day of default. | 0 | 0 | 0 | 0 | 0
12 | Complaint Related to Billing | Rs. 50 for each day of default. | 0 | 0 | 0 | 0 | 0
13 | Replacement of Meter | Rs. 25/- for each day of default subject to maximum of Rs. 1500/- for LT connections and Rs. 250/- for each day of default subject to maximum of Rs. 2500/- for HT connections. | 0 | 0 | 0 | 0 | 0
14 | Reconnection of Supply | Rs. 25/- for each six hours (or part thereof) of delay in restoration of supply subject to maximum Rs. 500/- for LT connection and Rs. 50/- for each six hours (or part thereof) of delay in restoration of supply subject to maximum Rs. 1000/- for HT connection. | 0 | 0 | 0 | 0 | 0
15 | More than 2 interruptions in a day to the consumer for the reasons not attributable to the nature of fault as mentioned in Clause 8.4 of these Regulations. | Rs. 25/- for each interruption subject to maximum Rs. 500/- for LT connection and Rs. 50/- for each interruption subject to maximum Rs. 1000/- for HT connection. | 0 | 0 | 0 | 0 | 0
16 | Failure to restore power supply in case of blowing of fuse of LT side distribution transformer, at consumer premises, trouble of MCB of distribution transformer, loose connection at pole, MCB or meter, etc. | Rs. 50/- per hour per Consumer for the first two hours of default. Thereafter Rs. 100/- per hour per Consumer subject to maximum of Rs. 500/- per day for LT consumer and maximum of Rs. 2000/- per day for HT consumer. | 0 | 0 | 0 | 0 | 0
17 | Failure to restore power supply in case of blowing of HT side fuse of distribution transformer |  | 0 | 0 | 0 | 0 | 0
18 | Failure to restore power supply in case of HT and LT line fault |  | 0 | 0 | 0 | 0 | 0
19 | Failure to restore power supply in case of Distribution transformer failure |  | 0 | 0 | 0 | 0 | 0
20 | Failure to restore power supply in case of failure of underground service or underground HT/LT cable |  | 0 | 0 | 0 | 0 | 0
21 | Scheduled Power Outage | Rs. 50/- per hour per Consumer for the first two hours of default. Thereafter Rs. 100/- per hour per Consumer | 0 | 0 | 0 | 0 | 0
22 | Site Visit and Intimation to the Consumer about likely time to resolve the complaint related to voltage fluctuation. | Rs. 200/- for each instance for each complaint. | 0 | 0 | 0 | 0 | 0
23 | Complaint of Neutral Voltage | Rs. 250/- for each complaint | 0 | 0 | 0 | 0 | 0
24 | Complaint regarding Voltage variations at the point of commencement of supply. | Rs. 25/- for each day of default subject to maximum of Rs. 500/- | 0 | 0 | 0 | 0 | 0

## SoP 17
Performa SoP 017: Individual Complaint where Compensation has been paid (To be submitted Quarterly)
Sr. No. | Complaint No. | Date of filing Complaint/ Automatic Compensation | Consumer No. and Name and Address of the Consumer | Nature of Complaint | Reference Standard of Performance | Amount of compensation (Rs.) | Whether Compensation paid automatically or Consumer has to approach CGRF to get compensation | Whether CGRF has upheld demand of Consumer of Compensation and if Yes, date of order of CGRF and date of compensation paid
| 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0

## SOP 18
1. Unauthorised use of Electricity (1st Quarter as Apr 25 - Jun 25)
No. of cases Booked | No. of cases where UUE is established by the Licensee | No. of cases where appeal filed by the consumer before the Apellate Authority | No. of cases decided by the Appellate Authority in favour of the the Licensee | No. of cases decided by the Appellate Authority in favour of the the Consumer
226 | 226 | 0 | 0 | 0
192 | 192 | 0 | 0 | 0
133 | 133 | 0 | 0 | 0
174 | 174 | 0 | 0 | 0
126 | 126 | 0 | 0 | 0
851 | 851 | 0 | 0 | 0
Note:- | The format is to be sent quarterly.
The format shall include individual consumer wise details.
The quarterly reporting of the year means reporting for the period 1st Quarter as Apr – Jun, 2nd Quarter as Jul – Sep, 3 rd Quarter as Oct – Dec and 4th Quarter as Jan – Mar of the financial year.

## SOP 19
2. Theft of Electricity (1st Quarter as Apr 25 - Jun 25)
No. of cases Booked | No. of complaints filed by the Licensee in Police Station | No. of cases in which the judgement delivered by the Special Court | No. of cases decided by the Special Court in favour of Licensee | No. of cases decided by the Special Court in favour of Consumer
659 | 659 | 0 | 0 | 0
135 | 135 | 0 | 0 | 0
382 | 382 | 0 | 0 | 0
501 | 501 | 0 | 0 | 0
2151 | 2151 | 0 | 0 | 0
3828 | 3828 | 0 | 0 | 0
Note:- | The format is to be sent quarterly.
The format shall include individual consumer wise details.
The quarterly reporting of the year means reporting for the period 1st Quarter as Apr – Jun, 2nd Quarter as Jul – Sep, 3 rd Quarter as Oct – Dec and 4th Quarter as Jan – Mar of the financial year.