## INDEX
Uttar Gujarat Vij Company Ltd ,Mehsana
Performas for FY 2025-26
Performa No. | Particulars | Remarks/Report
SoP 001 | Fatal & Non Fatal Accident Report | Qtrly FY 2025-26
SoP 002 | Action taken report for safety measures complied for the accidents occurred | Half Yearly FY 2025-26
SoP 003 | Register for compiling the complaints classification wise | Qtrly FY 2025-26
SoP 004 | Actions or steps carried out by UGVCL towards public awareness in the year | Qtrly FY 2025-26
SoP 005 | Failure of Distribution Transformer. | Qtrly FY 2025-26
SoP 007 | Sample Test result for Neutral Voltage | Half Yearly FY 2025-26
SoP 008 | Sample result for Voltage Variations | Half Yearly FY 2025-26
SoP 009 | Sample Test result for Harmonics | Half Yearly FY 2025-26
SoP 010 - A | System Average Interruption Frequency Index (SAIFI) | Qtrly FY 2025-26
SoP 011 | System Average Interruption Duration Index (SAIDI) | Qtrly FY 2025-26
SoP 012 | Momentary Average Interruption Frequency Index (MAIFI) | Qtrly FY 2025-26
SoP 013 | Customer Average Interruption Duration Index (CAIDI) | Qtrly FY 2025-26
SoP 014 | System Losses at EHT / 11 KV and below | Will be submitted later
SoP 015 | Meter Faults | Qtrly FY 2025-26
SoP 016 | Compensation Details | Qtrly FY 2025-26
SoP 017 | Individual Complaint where Compensation has been paid | Qtrly FY 2025-26
SoP 018 | Unauthorised Use of electricity | Qtrly FY 2025-26
SoP 019 | Theft of electricity | Qtrly FY 2025-26

## SoP001
Uttar Gujarat Vij Company Limited
Performa - SoP 001 : Fatal and Non-fatal Accident report
YEAR 2025-26 (Jan.-26 to March-26)
Sr. No. | Name of Circle | No.of accidents during the quarter |  |  |  |  | Cumulative since the first quarter of the current FY
|  | Departmental |  | Outside |  |  | Departmental |  | Outside
|  | FH | NFH | FH | FA | NFH | FH | NFH | FH | FA | NFH
1 | Sabarmati | 0 | 2 | 5 | 2 | 1 | 1 | 13 | 48 | 48 | 10
2 | Mehsana | 0 | 3 | 4 | 2 | 1 | 1 | 11 | 26 | 26 | 4
3 | Palanpur | 0 | 1 | 5 | 2 | 2 | 1 | 2 | 29 | 27 | 8
4 | Himatnagar | 1 | 1 | 7 | 3 | 2 | 3 | 6 | 25 | 43 | 8
| TOTAL | 1 | 7 | 21 | 9 | 6 | 6 | 32 | 128 | 144 | 30

## SoP002
SOP 002 Action taken report for safety measures complied for the accidents occurred half yearly 2025-26 ( October-25 to March-26)
Sr. No. | Circle, Division, Subdivision | Location of Accident and Rural or Urban | Name of Victim/Owner & Designation | Date of Occurance | Type of Accident FHD/NFHD/FHO/NFHO/FAO | Cause of Accident | Findings of CEI/EI/ AEI | Remedies suggested by CEI / EI/ AEI in various cases | Whether the remedy suggested is complied | Action taken to avoid recurrence of such Accident. | Amount of Compensation and Date of compensation paid (in Rs.)
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12
1 | PLN/Radhanpur/Varahi | Zazam/RURAL | Arvindbhai Mansangbhai Panda | 01.10.2025 | FHO | Accident related message on today 2/10/25 Press of Divya Bhaskar, There are 4 Nos Truck went to Zazam BSF Camp, Farm of Bhagvanbhai Sarpanch for Unloading of Ghaschara. All 4 Truck passed the Line Crossed which is not touched the 11 kv Universal JGY feeder. But when truck cleaner remove rassi from upperside, Driver drive truck in reversed mode & victim stood on uperside of Truck got touched the 11 kv line and hence victim got electrocuted and died. | Yet not received | N/A | N/A | Necessary Required Vertical Distance Provided With Restringing Of Conductor
2 | PLN/Deesa-2/Dhanera-1 | Dhakha/RURAL | 1.Patel Kankaben Babubhai Age:45 yrs approx Fatal , 2.Patel Babubhai Harjibhai Age:48 yrs Approx Non-fatal, 3.Patel Harjibhai kajabhai Age:80yrs Approx Non - fatal | 04.10.2025 | FHO & NFHO | The victim got electri shock when they operate cow milking machine and Internal wiring damaged.The Detail Investigation report is under process. Accident occurred due to internal wiring of Consumer. | Yet not received | N/A | N/A | People were educated to install ELCB/RCCB at their premises
3 | PLN/Palanpur-1/GADH | SAMDHI/RURAL | BALVANTJI MOBTAJI PUNIYATAR | 17.10.2025 | FHO | AT VILLAGE:SAMDHI, Area:Nadhanivas, ON DT 17.10.25, During Switching on three phase supply at agriculture connection of consumer no:-70772101299 in bore well electric conn room at aprroximatly 13.20 hrs Victim came in contact with LT Side Fuse and got electric shock. No currant leakage was found where accident happend. | Yet not received | N/A | N/A | People were educated to Prpoer safety norms must be followed by while working near to live equipment .
4 | PLN/Palanpur-2/Danta | Ratanpur/RURAL | Chauhan Nirmalsinh Vaghusinh (EA) | 25-10-2025 | FHD | Victim has received complain directly from consumer of broken Ag Lt Line so he went there at location of broken conductor where he had removed DO of transformer to off electric supply then he may have started rectification work of broken conductor where he met with accident. As per site visit it was found Lt line was broken. DO fuse of transformer centre was removed. As per Eye witness , victim wear helmet and safety belt and climb on the RSJ girder pole but before clamp the hook of safety belt, some how he jumped from the pole, and fell down on land ,approx. 5 feet away from RSJ pole . victim had breathing problem so local consumer shifted him to Lok-seva hospital from where he refer to Danta civil hospital where he declared dead. There are no burn injuries found on the body of victim. As per the PM Report the cause of death due to cardiorespiratory failure due to abdominal injuries sustained and its complication. The Accident is purely Mechanical Accident. | Yet not received | N/A | N/A | Staff Informed To Take Necessary Care While Climbing Up And Down From Pole
5 | PLN/Deesa-2/Lakhani | Jetada/RURAL | Samir Isubbhai Sama | 4.11.25 | FHO | Victim climbed on Truck roof top and came in Contact with 11 KV Ganesh JGY and died. | Yet not received | N/A | N/A | People were educated to Prpoer safety norms must be followed by while working near to live equipment .
6 | PLN/Deesa-2/Rah | Chhanasara/RURAL | Nayak Babukhan Antlakhan | 9.11.25 | FHO | Victim has fitted Iron wire around his farm for protection from outsider Animals.One Zatka machine lying in Ag Connection room.But as per site visited no any leakage current found and no any tripping recorded on 11 KV Chhanasara feeder. So Victim may be given power from his Ag Connection fuse and unfortunately he came in contact with fencing wire which was live and victim died.Victim Son Jahirkhan tried to save after seen his father but he was also got electric shocked. | Yet not received | N/A | N/A | inform consumer's not use unathorise power
7 | PLN/PALANPUR-1/Dantiwada | Antroli/RURAL | 1 nos Buffallo Name Of Owner:Chauhan Asaratsinh Metapsinh | 11.12.25 | FAO | The buffalo of Owner Shri Chauhan Asaratsinh Metapsinh Thakor is get relief from its rope itself and ran away one km and arrived near the farm of Thakor Jorsinh Madhsinh and came into contact with live electric power passing through the private iron fencing and Died. | Electricity Regulation 2003, regulation no. 14 is found to has violated. | People were awared about no any work to be carried out unauthorized working near Discom Network | Yes | inform consumer's not use unathorise power
8 | PLN/Deesa-2/Dhanera-2 | Jadiya/RURAL | Babubhai Devrajbhai Chodhary | 01.01.2026 | FAO | As per Site Visited and found ,Buffalo was tied with metal Pillar Shed.In Shed area deteriorated Single Phase wiring.So due to private Premises damaged wiring fault Buffalo got electric shock and died on the spot. | Yet not received | N/A | N/A | People were educated to install ELCB/RCCB at their premises
9 | PLN/PALANPUR-1/Gadh | Tokariya/RURAL | (1) Fatal-Govindbhai Jethabhai Jaganiya-Age Aprox 52 years (2) NonFatal-Girishbhai Govindbhai Jaganiya-Age Aprox 30 Years | 15.01.26 | FHO & NFHO | As per Eye witness statement of shri Shamalbhai Umabhai Jaganiya,Age-56 years approximately,Native place:Changvada Tal:Palanpur recently residing at Vill:Changvada informed by statement that " There is electric current given on farm fencing and electric bulbs connected with it which was glow all time at the Agricultural conn of Consumer shri Ramabhai Jivabhai Prajapati ,Consumer number 70751000027 During site visit by UGVCL officials electric bulbs are also visible on fencing.Iron wire fencing done by Farmer Ramabhai Jivabhai Prajapati ,of Vill:Tpkariya at their farm and victim get in contact with fencing and got electric shock and died on the spot named shri Govindbhai Jethabhai Jaganiya and other victim named Shri Girishbhai Govindbhai Jaganiya is also met with electric shock & under medical treatment | Yet not received | N/A | N/A | inform consumer's not use unathorise power
10 | PLN/Sidhpur/SIDH RURAL | LALPUR/RURAL | THAKOR BHAVANJI LALAJI | 19.01.26 | FHO | ON DTD:19.01.2026 ,APPROX TIME: 00.50 A.M. SHRI THAKOR BHAVANJI LALAJI VICTIM CLIMB ON THE POLE OF LOC.NO. 103/50/6 OF 11 KV KUNVARIKA JGY FEEDER EMANTING FROM 66 KAHODA SUB STATION,SOHE VICTIM TOUCH THE 11 LV LIVE LINE FOR SUCIED AND GOT ELECTROCUTED AND FATAL ELECTRICAL ACCIDENT OCCURED. FEEDER TRIP AND HE FELL DOWN FROM POLE.HE WAS DISTURB FOR FAMILY REASON. | Yet not received | N/A | N/A | SUICIDE CASE
11 | PALANPUR/Palanpur-2/Vadgam | Memadpur/RURAL | THAKOR SITABEN MOHANJI | 20.01.2026 | NFHO | A insulated tap provided on joint of service wire of cosumer no 70309/00735/6 had come off due to long time. So live service wire joint came contact with GI wire.The GI wire is came contact with with Iron railing ladder of this consumer house. So electric current is passing through iron railing ladder to ground. The victim came contact with this iron railing ladder and got electric Shock .Victim discharged on dated 21-1-26 with stable condition after treatment. | Yet not received | N/A | N/A | People were educated to Prpoer safety norms must be followed by while working near to live equipment .
12 | PLN/PALANPUR-1/Dantiwada | Bhakodar/RURAL | Rabari Sagarbhai Vahjibhai -Age Aprox 32 years | 25.01.26 | FHO | The person Named Sagarbhai is climbed on Transformer structure of Rabari Maganbhai Mashrubhai due to some unknown reason and three phase schedule is continue on Chodungri Ag Feeder.He was coming into contact of 11KV supply and electrocuted and died on the spot and body is burnt.As per site verification due to any family reason or any mental problem the victim this step with intension of sucide.The house and electric connection of victim is 300 meter away from this location. | Yet not received | N/A | N/A | SUICIDE CASE
13 | PLN/Deesa-2/Dhanera-1 | Runi/RURAL | Patel Kesarsinh Jethabhai | 27-01-2026 | FHO | During Stringing work of new 66 KV line for new Runi SS ,GETCO staff have taken LC of 11KV Voda Ag feeder of 66 KV Khimmat SS while actual feeder passing 11 KV Tarak Ag feeder of 66 KV Voda SS.Contractor Person climbed on 11 KV line and came in Contact with live Conductor and got electric shock and died after primary treatment | Yet not received | N/A | N/A | People were educated to Prpoer safety norms must be followed by while working near to live equipment .
14 | PLN/Palanpur-1/Kanodar | Kanodar/RURAL | Shrimali Vijaybhai Vitthalbhai-Elect Astt-Employee No:10890 | 05.02.26 | NFHD | Victim Had Climbed on Necket Pole to do wiring But, Pole tilted and Victim fall Down on Earth with above Pole and Met with Mechanical Accident | Yet not received | N/A | N/A | Staff Informed To Take Necessary Care While Climbing Up And Down From Pole
15 | PLN/Sidhpur/UNJHA TOWN | Unjha/TOWN | Shri Selot Jayeshbhai Rasubhai | 24.02.2026 | NFHO | On Date-24.02.2026, 04:30PM (Approx) , a Fencing installation work was carried out by Rajesh power Contractor at Unjha Nagarpalika RMU under 11KV Umiya Urban Feeder and their worker Shri Selot Jayeshbhai Rasubhai was breaking the RCC Road by Breaker. During that a armoured LT Cable going to Nagarpalika Meter below the RCC Road is cut by the breaker and electric fire occured due to short circuit. Due to that Shri Selot Jayeshbhai Rasubhai was burnt on their right hand and also on their face. So he was admited to civil hospital unjha for treatment. | Yet not received | N/A | N/A | People were educated to Prpoer safety norms must be followed by while working near to live equipment .
16 | PLN/DEESA -1/SHIHORI | NAGOT/RURAL | BUFFALO OF THAKOR AJITSINH SOMAJI | 15-01-2026 | FAO | As per telephonic message recived from line staff at 11.00 am about fatal animal accident occurred at vill.Nagot .Junior engineer shihori personally visit the site and as per eye witness statement,at approximately 6:30 am due to 11 kv magalpura ag fdr conductor broken nearest 4 to 5 mtr buffalo was shocked and died. | Yet not received | N/A | N/A | Routine maintence of HT network is done. | 15000
17 | PLN/Deesa-2/Zerda | Tetoda/RURAL | Chaudhary(Patel) Dineshbhai Kanjibhai | 20.03.2026 | FHO | Victim got shock in his bathroom due to Water heater rod. | Yet not received | N/A | N/A | People were educated to install ELCB/RCCB at their premises
18 | Sabarmati , Sabarmati, Viramgam R | Vadgas Rural | Rughnathbhai Virabhai Rabari | 2025-09-28 | FA O | As per the statement of owner of the cow, on dtd 28.9.25 at around 8 o’clock at night, after milking the cows, he (owner of the cow) was heading his 6 to 7 cows toward the fields. Suddenly, due to Heavy rain and thunderstorm LT line pole collapsed on a cow. The pole struck the cow’s neck, causing it to collapse on the ground.And due to being crushed under the pole, the cow had died. Further investigation is in under progress. | Yet not received |  |  | NEW POLE ERECTED IN PLACE OF DAMAGED POLE | 15000
19 | Sabarmati , Kalol, Kalol-2 | Dangarva Rural | Rabari Ishvarbhai Jorabhai | 2025-09-30 | FA O | On Dtd. 30.9.2025 approx 9:30 pm the She Buffalo and Cow are passing from near to Manojbhai Babubhai Solanki farm and suddenly near the transformer center due to some reason the animals came in contact of stay wire and due to some leakage current the animals got electrocuted and fell down and died. | Yet not received |  |  | MAKE EARTHING OF STRUCTURE AND MAINTANCE OF THE TRANSFORMER CENTER.
20 | Sabarmati , Bavla, Dholka R | Rasikpura Rural | Bharvad Vipulbhai Kababhai | 2025-09-30 | FA O | As per eye witness statement on date 30/9/25 about 9.30am owner of buffalow himself taken his cattle for grazing while passing through farm at that time 11kv rasikpura ag feeder lt line wire broken near accident place and female buffalo touched with live conductor and electoduted and died on the spot. | Yet not received |  |  | CONDUCTOR JOINT DONE AND RESTRINGING WIRES OF LT LINE | 15000
21 | Sabarmati Gandhinagar U Kudasan | Koba | Virendrasinh Popatsinh Chauhan | 2025-10-08 | NFH D | While dismentaling of conductor near Ekarth SERVAM, Koba , it was observed that the victim was working on a pole where the power supply had been switched off, and the jumper on the next section had been disconnected. However, power remained live on the opposite side of the same pole. It was further found that conductors on the two poles located behind the accident site had already been removed. While loosening the pin binding on the pole where the incident occurred, the conductor became slightly black. Consequently, the required clearance between the dead conductor on the section pole and the nearby live conductor was not adequately maintained. Hence, the victim received an electric shock and fell from the pole. | Yet not received |  |  | Warning memo issue to Defaulter
22 | Sabarmati Sabarmati NARODA Ind. | Naroda | Parmar Alpesh Jagdishbhai | 2025-10-13 | FH O | As per brief received from Naroda police station, on date 13/10/2025 victim working in car washing area at sp cars (a Tata motors car service station) while washing a car from nosel connected to the pressure pump due to leakage current the victim got electrocuted then send to hospital and there he declares dead. Reason of leakage current is not known yet the switch board of pressure pump is taken by police and the service station is closed. Power supply of the premise is disconnected | Yet not received |  |  | POWER DISCONNECTED AFTER ACCIDENT & WAS RECONNECTED AFTER NEW TEST REPORT SUBMITTED BY PARTY | N A
23 | Sabarmati Gandhinagar R Chiloda-1 | Chiloda | Thakor Nisad Arvindji | 2025-10-16 | NFH O | Victim was working with the help of Ladder on temple for the work of lightening work ( Series) and ladder touch with 11 KV Line and he fell down and lekage current flow to his body and passes through his feet and he fell down and Non Fatal electrical accident occurred. | Yet not received |  |  | Cotted Conductor Will Be Provide
24 | Sabarmati Gandhinagar R Dehgam R | Kadadra | 1.Rajkumar Bholama (FH) 2.Gyani Pandit (FH) 3. Bholekumar Manishkumar Devendraprasad (NFH) | 2025-10-17 | FH-NFH O | Limbani Bhautik A.plot no.35 con no.26243/10223/8 LTMD 98 Kw connection plot has given on rent to Bavishi Tushar Rameshbhai which was being emptied plot.In that today 17.10.25 time @8:00 am labour Shri Bholekunar Manishkumar Devendraprasad was get down the iron bed unfortunately contact with our 11kV line,injured and down & electric current passed from his forehead and left hand & try to save him Shri Rajkumar Bholama,Gyani Pandit pulled him & they electrocuted and died on spot while Bholekumar Manishkumar Devendraprasad admitted in Prime Hospital Naroda whose health normal. | Yet not received |  |  | Line Is Already At Safest Distance So No Corrective Action Require.
25 | Sabarmati Bavla Dholka T | Dholka | Dharam Jagdish Singh | 2025-10-16 | FH O | On dated 16/10/2025 at around 4:00 PM, the victim Shri Dharam Jagdish Singh was carrying out harvesting work with the help of a Treak Combine Harvester near Paswanath Hospital on Dholka–Bavla Road. An 11 kV line of Ranoda AG feeder passes through the said area. During the work, the victim climbed slightly on the top portion of the harvesting machine and accidentally came into contact with the live 11 kV conductor. As a result, he received an electric shock and died on the spot. It is also noted that no tripping was observed on the 11 kV Ranoda AG feeder during the time of the incident. | Yet not received |  |  | Power Supply Off After The Incident
26 | Sabarmati Bopal Goblaj | Radhu | Mahavirsinh lalubha Sisodiya | 2025-10-27 | FA O | Owner of the buffalo on date 27.10.25 at around 5:00 AM, due to cyclonic rain somehow insulation of service wire ( before meter) gor broken and touches the roof of house, beside house buffalo tied up in a stable behind the house was some how hit by a leackake current. | Yet not received |  |  | Service Wire Replaced | 15000/ 05-12-2025
27 | Sabarmati Bopal Goblaj | Vasna Bujarg | Kalubhai rupsang Sisodiya | 2025-10-29 | FA O | As per the statement of owner of the buffallo, on dtd 29.10.25at around 08:45 AM due to cyclonic rain Tamarind Tree fallen on LT wire and conductor got broken. At time of graze buffaloes passing to the location might have come in contact with live wire and got electrocuted. Further investigation is in under progress. It's PM report also awaits. | Yet not received |  |  | Tree cutting maintance done | 15000/ 26-12-2025
28 | Sabarmati Kalol Nardipur | Dingucha | Harjibhai Tindabhai Dantani | 2025-10-30 | FA O | As per preliminay information and site visit, at the accident place while goats (25 nos approx) owner of Shri Harjibhai Tidabhai Dantani returning from pansar dingucha naliya road opposite Ganpati bapa Mandir Near tc of Ganpati bapa village tc Somehow 5 nos of goat (female)reached near the transformer center and fatal animal (05 goats female) accident occured. At the time of site visit there is no any leakage current found at near transformer centre and pole and guy set. | Yet not received |  |  | FENCING PROVIDED AROUND T.C. | 7500/ 17-01-2026
29 | Sabarmati Bopal Goblaj | Vasna Bujarg | Pathan Sirajkha MuktyarKha | 2025-11-04 | FA O | As per the statement of owner of the cow, on dtd 04.11.25 at around 10:00 AM, One Buffalo while Grazing, The Buffalo Rubbing her body to the pole of Transfomer structure, might have come in contact with leakage current in Transfomer earthing and got electrocuted. Further investigation is in under progress | Yet not received |  |  | New Earthing Of Transformer Done And Broken Service Wire Replaced. | 15000/ 05-12-2025
30 | Sabarmati Bavla Dholka T | Dholka | Jivrajbhai Karshanbhai Chauhan | 2025-11-10 | FH O | On dated 10/11/2025 at around 15:32 hrs, construction and repair work was going on at a partially demolished house located near Akash Bunglow, Mafalipur, Dholka. Approximately two to three labourers were engaged in the work. Shri Jivrajbhai Karshanbhai Chauhan, aged 53 years, was working on the upper portion of the damaged structure, while the remaining labourers were on ground level. An 11 kV BadiyaDev feeder line passes near to the said house. During the construction activity, a long square metallic pipe was being lifted upward, and the pipe accidentally came into contact with the live 11 kV conductor. Due to direct contact of the metallic pipe with the HT line, the victim received electric shock. After receiving the electric shock, the victim fell down from the structure and sustained critical injuries. As per information received from the site, the victim was shifted by 108 Emergency Service to the hospital (final confirmation to be taken from Police authority). Subsequently, on 11/11/2025, he was declared dead. Tripping of power supply was observed on the 11 kV Badiyadev feeder during the time of the incident. | Yet not received |  |  | NA
31 | Sabarmati Bavla Dholka T | Ganipur | Karthik Vishalbhai Vanza | 2025-11-15 | NFH O | Victim at his Fault. The kite was stuck in the DO unit of the transformer structure, and the victim attempted to retrieve the kite by climbing onto the transformer structure. During this attempt, he came in contact with the live 11 kV conductor at the DO location, received an electric shock, fell down and hung on the transformer oil coke by his sweater . He was immediately shifted to Paswanath Hospital, where the medical team has confirmed that the victim is currently absolutely all right. | Yet not received |  |  | AWARENESS GIVEN ABOUT THE SAFETY PRECAUTIONS
32 | Sabarmati Bavla Koth | Gangad | Mevada Rakeshbhai Karmanbhai | 2025-11-22 | FA O | During monsoon season 1 span of 11 kv shiyawada ag feeder was loose due to tc structure and tap pole was tilted which was not approachable for maintenance due to water logging.as on dt 22/11/2025 time approx 14:00 pm a cow was grassing and passing through below the 11 kv line which span has already low ground clearance and came in contact and got electrocuted and died | Yet not received |  |  | STRINGING OF CONDUCTOR AND MAINTENANCE WORK
33 | Sabarmati Sanand R Changodar | Changodar | Harshadbhai Ajitbhai Parmar | 2025-11-27 | FH O | As per preliminary site visit and statment of panch as per the details, Shri Harshadbhai Ajitbhai Parmar, who was working at the site (Inside T &R Company), was performing transformer testing (Magnetic Balance Test) as shown in the attached photograph. For this testing process, a 3-phase power supply was being used. During the activity, he accidentally came in direct contact with two phases of the 3-phase power supply, which resulted in a severe electric shock. Unfortunately, due to this accidental contact, he got electrocuted and died on the spot. | Yet not received |  |  | NA
34 | Sabarmati Bavla Bavla Ind. | Dhedhal | Maheshbhai Babubhai Bharwad | 2025-11-28 | FA O | As per preliminary site visit and statment of panch it came to notice that buffaloes were walking in the field near ramapir mandir road in dhedhal village and one of buffaloes walking near the electric pole stay wire, as buffalo walking touched the stay wire and it got broken as rusted from earth and came in contact with the live conductor,the buffalo got electrocuted and died on the spot. | Yet not received |  |  | STAY WIRE REMOVED FROM SITE | 15000/ 24-02-2026
35 | Sabarmati Kalol Kalol T | Kalol | Maheshbhai Bhagvanbhai Acharya- FH Arvindbhai Natvarbhai Darji | 2025-11-30 | FH-NFH O | The house owner shree Sureshbhai Patva give plumbing work to Victims of accident. They went for plumbing work at space outside the flate building with long iron rod approx 19 ft and tried to do removing from block pipe and during this work meanwhile the one end side of iron rod came in contact of 11 kv line passing near the bilding, approx 9ft away and both victimes electrucuted. Shree Maheshbhai Bhagvanbhai Acharya(fatal human)fell down from building and taken to hospital for further medical treatment but Dr at hospital declared him dead and shree Arvundbhai Natvarbhai Darji(non fatal) he was also sent to hospital for medical treaent. | Yet not received |  |  | NA
36 | Sabarmati Sanand R Sanand-2 | Melasana | Virendra sinh Khuman sinh Chauhan | 2025-12-03 | FH O | On dated 03.12.25 around at 10:30 am, victim was climbed on wall of under-construction room ,came in contact with HT line conductor and got electrucated and died on spot. | Yet not received |  |  | LINE SHIFTING ESTIMATE WAS ALREADY SERVED TO APPLICANT
37 | Sabarmati Bavla Bavla-1 | Durgi | Bharvad Bharatbhai Dolabhai | 2025-12-09 | FA O | On dated 09.12.25 around at 6.00 pm , LT line conductor was broken at village Durgi near Panchayat TC due to some reason and same time buffalo was passing from there and got in touch with live LT line and got electrucated and died on spot. | Yet not received |  |  | LT Line Deteriorated Conductor Replaced With New LT Line Conductor And Necessary Maintenance Work Has Been Carried Out.
38 | Sabarmati Sanand R Mandal | Sher | Harshadbhai Ashokbhai Thakor | 2025-12-10 | NFH O | On Dated: 10.12.2025 and 4.30 PM While victim were going to catch a kite on the roof of the house of Shri Bharatbhai Mahadevbhai Thakor at Sardar Awas Yojana, the house is constructed under the 11 kv Dalold agriculture feeder, Thakor Harshadbhai Ashokbhai got electrocuted and fallen to the ground, for primary treatment he was taken to shiv hospital, Viramgam after report there is no any majority damage found and little burn found on finger of right hand and on leg too. Site PANCHNAMU Details investigation will be carried out. | Yet not received |  |  | Notice Issued To Consumer As Well As Line Will Be Shifted.
39 | Sabarmati Bavla Bavla Ind. | Nani Devti | Manojbhai Jagdishbhai Damor | 2025-12-18 | FH O | Victim climbed onto dumper to remove tarpaulin and while removing tarpaulin,The victim accidentally came in contact with the HT Conductor of 11 kV Khicha JGY Line, suddenly he got electrocuted and died on the spot. | Yet not received |  |  | NOTICE TO GALA LIFE STYLE OWNER GIVEN TO IMPROVE GROUND CLEARANCE AND STOP WORK PILLING WORK TILL PROPER GROUND CLEARANCE ACHIEVED.
40 | Sabarmati Sanand R Sanand-2 | BOL | Bharvad Lalbhai Hajabhai | 2025-12-23 | FA O | on dated 23.12.25 around at 11.00 am ,two nos of buffalo were grazing near farm of Narendra bhai Kanubhai Barad accidentally came in contact with broken conductor of Vasna Ag ,got electrucated and died on spot. | Yet not received |  |  | BROKEN CONDUCTOR REMOVED FROM SITE
41 | Sabarmati Bavla Dhandhuka | Kashindra | (1) Shehnajbanu Faminkhan Pathan - FH (2) Faisal Faminkhan Pathan - NFH (3) Ramannabanu Faridmiya Malek - NFH | 2025-12-29 | FH-NFH O | On dated 29-12-2025, time about 14:18 on the way of Bhadiad Ursh fair, Mrs. Shahenjabanu Faminkhan Rasulkhan Pathan, age 22, was walking on foot along with other members of her family from Kasindra to Bhadiad road to reach Bhadiad fair. There, from Kasindra towards Bhadiad, i.e. at the place where the incident was built, a pavilion with an iron pipe was built by these people for rest and breakfast, the pipe of which was not buried in the ground and the 11 KV Umargarh feeder was passing over it, which comes from the 66 KV substation. On 29-12-2025, at around 14:18, due to the wind, the iron pavilion, which moved upwards from the ground towards the sky, touched the 11 KV power line passing above it, which is 19.2 feet high from the ground (Its as per the norms of electricity act 2003. The incident occurred when the people caught hold of it and got electrocuted. Mrs. Shahenjabanu Faminkhan Rasulkhan Pathan, age 22, died on the spot and Faisal Faminkhan Rasulkhan Pathan, age 9 months and Tamanna Banu Faridmiya Hasumiya Malek, age 17, were injured. Two spots on the 11 KV line are visible standing on the ground and the tripping of the Umargarh feeder in the substation occurred at 02:18. The accident in which Mrs. Shahenjabanu Faminkhan Rasulkhan Pathan died will be further confirmed after receipt of the post- mortem report. | Yet not received |  |  | After Reaching The Incident Place, Thorough Inspection Was Done, Ground Clearance Is Found Ok As Per The Norms Of Electricity Act 2003.
42 | Sabarmati Sabarmati Kathwada | Kathwada | 01. Aditya Alpeshbhai Parmar, Male-16 Year Approx (Fatal) 02. Vijaybhai Pradipbhai Jatav, Male-17 Year Approx (Non-Fatal) 03. Krishna Bharatbhai Soni, Male-17 Year Approx (Non-Fatal) | 2026-01-10 | FH-NFH O | A 'Mandap' with 4 metal rod pillars, was made by victims near UGVCL DO structure (Single Pole). As per eye witness information, on date 09.01.2026 approx mid night, due to some reasons, a quarrel occurred between, victms and a four wheel owner (unknown).So, in rage, four wheel owner has tried to damage the 'Mandap' with his vehicle, And due to vehicle impact, the 'Mandap' pillars were thrusted in tilted position. As the victims tried to force the mandap in original position, the upper mandap metal rod, might have came in direct contact with jumper wire at DO structure nearby & got electrocuted. So, 1 victim was fatally electrocuted & other 2 were injured and sent to civil hospital Singarava for further treatment. Further investigation is in process . | Yet not received |  |  | 1 NEW JUMPER PROVIDED | 100000/ 18-03-2026
43 | Sabarmati Sanand R Viramgam R | Karakthal | Thakor Kanchanben Dashrathbhai | 2026-01-10 | FH O | As per information received from the press note published in the newspaper today, a married woman has died due to electric shock in Karakthal village. While getting information about this today, the incident took place on 10.01.26 at around 15:30 pm. The name of the person is Thakor Kanchanben Dashrathbhai and she is a resident of Karakthal village. Further investigation has revealed that the person had gone to start the water motor installed in her house on 10.01.26 at around 15:30 pm and suddenly got electrocuted. And due to which she was immediately taken to Viramgam Hospital and doctor declared her dead. The incident took place inside her house, in her private premises. No incident has taken place in the UGVCL network. REASON OF LEACKAGE CURRENT IS NOT KNOWN YET THE Electric MOTOR IS TAKEN BY POLICE. | Yet not received |  |  | AWARENESS GIVEN ABOUT THE SAFETY PRECAUTIONS THROUGH THE SAFETY CAMP.
44 | Sabarmati Sanand R Sanand-2 | Melasana | Patel Vishal Ranchhodbhai | 2026-01-14 | FH O | On dated 14.01.2026 around at 14.00 pm ,Vishal Ranchhod Bhai Patel climbed on a tree to catch a kite and came in contact with11KV Pava ag line passing nearby ,got electrucated .Further he was admitted to hospital for treatment and later he was declared dead by doctors on dt.22.01.2026 | Yet not received |  |  | Tree Cutting Done | 100000/ 13-03-2026
45 | Sabarmati Sabarmati Vinzol | Hathijan | Prabhudas Maxibhai Kalasva | 2026-02-26 | NFH D | On dated 26.2.2026 victim Shri PM Kalasava and Shri HG Dangi ALM and Shri MN Shaikh EA were doing work of maintenance on the route of Dakor padyatra. They have done work of maintenance and at Shyam Swastik Bungalow scheme shri MN Shaikh was climbed on the pole to dismantle HT line . while dismantling HT conductor, the conductor slipped from his hand and collid with near by Advertisement board and Shri PM Kalasvabhai who was standing beside this board, injured due to conductor bouncced back on his head and mechanical accident occured . He was shifted to near by hospital and necessary primary medical treatment given to him. | Yet not received |  |  | SHOWCAUSE NOTICE GIVEN TO SUPERVISOR SHRI H G DANGI & VICTIM SHRI P M KALASVA | N A
46 | Sabarmati Bavla Dholka R | Rajpur | Thakor Karanbhai Natubhai | 2026-02-27 | FH O | On dated 27.02.26 approximately 9:45am victim Thakor Karanbhai Natubhai (labour) and other two labours were working in Jigarbhai Rana farm house with MS steel fabrication/welding work at newly under construction shed which is built up under 11KV Bharvadiyapura Ag line. While lifting up steel ladder type support pole may be touched to live conductor and Victim got electrocuted and died. No tripping recorded during accident time in Chandisar SS. | Yet not received |  |  | NOTICE ISSUED TO JIGARBHAI RANA FOR UNAUTHORIZED SHED CONSTRUCTION WORK UNDER 11KV LINE.
47 | Sabarmati Sanand R Sanand-2 | Chharodi | Kamsibhai Jivanvhai Bharwad | 2026-03-07 | FA O | on dated 07.03.2026 approx at 10.00 am there when buffaloes were grazing at plot area behind Meghmani company at village Chharodi, at that time outgoing conductor of 11KV Bakrana Ag was broken and buffalo accidentally came in direct contact with wire ,got electrucuted and died | Yet not received |  |  | BROKEN CONDUCTOR JOINT WORK DONE
48 | Sabarmati Bavla Bavla-1 | Ramnagar | Maheshbhai Muljibhai Paadhariya | 2026-03-09 | FH O | on date 09.03.2026 at approx 10.15 hrs Maheshbhai Muljibhai Paadhariya was tried to start the motor by connecting cable in house. one side of this cable was pluged in switch board and the switch of these switch board was kept on. While said victim was tried to join the other side of this cable in motors socket he touched live cable/motor and got electrocuted and died. | Yet not received |  |  | SWITCH OFF IN SWITCH BOARD DISCONNECTED SAME
49 | Sabarmati Bopal Goblaj | Navagam | Rajubhai Masurbhai Kalasva-E.A. | 2026-03-19 | NFH D | Today on date 19.03.26 around 8.00 pm an evening due to cyclone & heavy wind three line staff shri R.D.Gosvami,L.M. , Shri P.S.Prajapati E.A. and Shri R.M.Kalasva- E.A. working on 11kv Axar jgy fdr. Which is in P.F..while line petrolling they found nilgiri tree branch fallen on line. Hence to cut/remove this branch victim shri R.M.Kalasva E.A.climb on nilgiri tree while climbing on nilgiri tree branch broken & they loose balance & fallen on grond & injured his left hand. | Yet not received |  |  | NA
50 | Sabarmati Bavla Bavla-1 | Rupal | Bhavanbhai Khengarbhai Bharvad | 2026-03-21 | FA O | on dated 21.03.2026 at approx 08.00 hrs she baffalo of Bhavanbhai Khengarbhai Bharvad were passing near to advertise board "the garden cafe and pan parlour.While said baffalo touched this board, got electrocuted and died. | Yet not received |  |  | Said Connection Has Been Disconnected And Consumer Has Been Informed To Submit New Fresh Report.
51 | Sabarmati Gnadhinagar R Gandhinagar | Pethapur | Vaghela Narayansinh Arjunsinh | 2026-03-26 | NFH O | The victim climbed on to the TC of UGVCL,which located in front of police station.he came in contact with the bushing of TC.which was connected to live cable and held it.resulting in severe injuries. | Yet not received |  |  | NA
52 | MSN/VISNAGAR/Visnagar-1 | Randala (Rural) | Govindbhai Hirabhai Chaudhary | 2026-10-06 | FHO | Fatal Human outside Electrical Accident Occurred to Govindbhai Hirabhai Chaudhary on Dated 06.10.25 time Aprroc 7:30 PM victim went to Chaudhary vas from Dairy due light Rain arround 7:30 PM on dated 06.10.25.He was elctric Shocked and fall down oin land near by big Stone,Approx 5feet far from LT Electric Pole.There was no any body part of Victim directly contact with LT Electric pole.After CPR the victim was reffered to Maniba Hospital and Deep ICU Hospital at Mahesana and Staff Declared Dead.At the time of Visit Found that there is no any leakage Current on pole and periphery.There was no any Evidence left by the public at the site to investigate How the Victim was Electocuted?Also the Actual reason of Death will be found after PM Report.PM Report and Police Panchnama are awaiting.Detail investigation under Progress. | Yet Not Received | N/A | N/A | N/A | N/A
53 | MSN/Kadi/BECHRAJI | BECHRAJI (Rural) | Kismatbhai Gaurangji Thakor | 2025-10-28 | FHO | As per the eye witness statement, the victim Late Shri Thakor Kismatbhai Gaurangji was opening the iron door of their toilet and that time might got electrocuted and shouted loudly. Hence his parents rushed outside the home and attempted to remove him from the iron door and during which they also got minor electric shock. Subsequently, they used Wooden stick to saperate the victim from the Iron door and immediately shifted to Zydus Hospital, Sitapur for Primary treatment. However the Doctor declared him dead. The Victim's postmortem was not conducted. Also The victim's father did not inform UGVCL regarding such an incident. As per site situation service wire found cut and it might touched to iron roof and electric current may pass through iron roof to toilet iron door. Further Detail Investigation is under process. Note: There is no visible electric burn marks or live electrical spots found at the site either on Iron door or at Iron roof. Service connection to the premises is provided using a GI wire and Egg insulator. | Yet Not Received | N/A | N/A | N/A | N/A
54 | MSN/Vijapur/Gozariya | Dabhala | Buffalo of Shri Chavada Arjanji Fulaji | 2025-10-28 | FAO | Shri Chavada Arjanji Fulaji’s one buffalo was tied near transformer center pole in his field. The buffalo got loose from the peg and started rubbing against the earthing wire of the transformer center pole. At that time, light rain was falling and the ground was wet. Due to this, buffalo might have been electrocuted and died. | Yet Not Received | N/A | N/A | N/A | 15000
55 | MSN/VISNAGAR/KHERALU 1 | Nalu (Rural) | RAJUBHAI HALUBHAI DESAI | 03-11-2025 | FAO | ON DATED 03.11.2025 APPROX 09:00AM FATAL ANIMAL ELECTRICAL ACCIDENT OCCURED DUE TO RAINY SEASON, INCOMING JUMPER OF TC BURNT AND MIDDLE PIN OF DO FIRED DUE TO THAT JUMPER WAS TOUCHED TO ANGLE OF TC LEAKAGE CUURENT PASSED THROUGH STAY/EARTH WIRE OR DUE TO WATER CURRENT PASSED ON COW AND GOT ELECTROCUTED | Yet Not Received | N/A | N/A | N/A | N/A
56 | MSH/Mehsana/Dhinoj | Panchot (Rural) | Goswami Daxpuri Jagdishpuri | 2025-10-20 | FHO | The accident occured on 20 oct 2025, this information given by taluka police on date 30.10.2025 vide letter no.4838, Victim was outsider. Where accident occurred at that premise used unauthorize electricity by yash vinodbhai patel from exist 1ph. connection for shop no G42, icon arcade complex. The victim was friend of yash vinodbhai patel and at that day he came for help to car washing work while he was washing the car suddenly he got electric current on nozal of car washing pipe due wet he got electrocuted, immediatly shifted to hospital for more treatment, detail investing under process. | Yet Not Received | N/A | N/A | NA | NA
57 | MSH/Mehsana/Mehsana Rural | JETALVASANA (Rural) | ROHITJI CHEHARAJI AGARAJI THAKOR | 2025-11-19 | FHO | As per the statement of the eye-witness Thakor Dasharathji Sendhaji (age 52, resident of Indiranagar, village Bhandu, the victim was engaged in plaster/mason work at the private residence of Shri Anupkumar Dahyalal Patel at village Jetalvasana. On 19/11/2025 at about 16:30 hrs, while descending from the wooden ladder used for plaster work, the victim accidentally fell down. He was immediately shifted to the Primary Health Centre, Jetalvasana for first aid with the help of local people. The medical officer informed that the victim had no pulse and advised transfer to Civil Hospital Mehsana immediately. The victim was then taken by 108 emergency service to Civil Hospital, where he was declared dead by the attending doctors. During the initial site visit and inspection, no visible signs or evidence were found to suggest that the incident occurred due to electric current. However, as per the Postmortem Report received from Civil Hospital, Mehsana, the cause of death has been confirmed as electrocution (electric current). Accordingly, the accident is considered a human fatal accident of an outsider due to electric current, as per the medical findings. | Yet Not Received | N/A | N/A | N/A | 100000
58 | MSH/Patan/Ranuj | Islampura (Rural) | Shri Thakor Bhartsang Kadvaji | 2025-12-01 | FHO | A Fatal Human electrical accident (Outsider) occured to Shri Thakor Bharatsang Kadvaji, Ag. Approx.47 Years at Patel Jitendrabhai Gangaram farm, Consumer No. 28629100915, Survey No. 555 at Village : Islampura on dated 01.12.2025 at 9.10 AM. As per information received 66kv Keshni Sub-Station from Mob. 7016610453 at 9.22 AM to Shri C.B.Patel , EA for information about accident on 11kv Finachal AG feeder at Village Islampura,the site is visited by undersign, it was to known from unknown present person that , Shri Thakor Bharatsang Kadvaji was operating Tractor of Bore-Well Ring and during bore well work when ring being lifted-up by victim passing under the 11 kv Line of Finchal AG feeder between the Loc.no-103/24/A - TC & 103/23(5.8 mtr distance from ground to middle conductor) ,due to Bore-Well Ring touches live conductor and got electrocuted. After that victim was immediately shifted to Dharpur Medical Hospital by 108 emergency vehicle. In the hospital doctor declared, the victim was dead. There is tripping was recorded in 11kv Finchal AG feeder from 66kv Keshni substation on 9.10 AM on date 01.12.2025. Detail investigation is under process and PM report awaited. | Yet Not Received | N/A | N/A | N/A | 100000
59 | MSH/Patan/CHANASMA | Chanasma (Rural) | VELABHAI MASHRUBHAI RABARI | 2025-12-07 | FAO | As above Fatal Animal Accident Information received telephonic to concern village lineman on dated 07.12.2025 and found that camel Male Age 5 Year Approx. was partially lied at transformer fencing of 200 KVA Transformer plinth of Patel Nikunjbhai Khodabhai,LTMD connection & No sparking & black current spot found on body or any surrounding live electrical parts & no any leakage current found on fencing,no any cause of fault found of UGVCL site but it may be come in contact with induction zone of 11KV line may be electrocuted detail reason of accident is under investigation and PM Report awaited… | Electricity Regulation 2003, regulation no. 14 found to have violated. | Earthing must be done | Yes | Maintenance & Earthing Done | 12500
60 | MSH/Patan/HARIJ | GOVNA (Rural) | BUFFALO OF DESAI AMBARAMBHAI KHENGARBHAI DESAI | 2025-12-10 | FAO | ON DTD 10-12-2025, 11:00 AM, DESAI AMBARAMBHAI KHENGARBHAI GRAZING THE BUFFALO IN THE FARM, SUDDENLY HE HEARED THE LOUD VOICE OF BUFFALO, AS HE HEAR THE VOICE OF BUFFALO HE RUN NEAR THE BUFFALO AND SHOW THAT THE BUFFALO WAS DIED AND LIED ON 1WIRE OF LT LINE OF AG CONNECION. BUFFALO DIED DUE TO COMING IN THE CONTACT OF SNAPPED LT CONDUCTOR | Electricity Regulation 2003, regulation no. 14 and 72 are found to have violated. | Maintanance must be done | Yes | Maintenance Done | 15000
61 | MSN/Vijapur/Vijapur | Vijapur (Rural) | Garasiya Sukhram Maganram | 2026-01-28 | FHO | The victim was pressing cement mixture in vertical column beam with 18.5 feet iron rod standing on wall of height 9 feet at that time iron rod tilted and he might be came in induction zone the 11 KV Krushi ag feeder passing in nearby farm which is at the tilt distance of 13 feet from top of wall & Victim might be got electrocuted & fall down from wall and referred to CHC, Vijapur for Primary treatment and declared dead. | Yet Not Received | N/A | N/A | N/A | N/A
62 | MSN/VISNAGAR/SATLASANA | BHALUSANA (Rural) | Vaghabhai Kesharbhai Gamar | 2026-02-22 | NFHD | On dated 22/2/2026 , Time Approx 12:15 PM, victim Shri Vaghabhai Kesharbhai Gamar was attending line fault of Talegadh JGY FDR,he found insulator failure of AB switch of Bhalusana Village switch.other E.A.has isolated switch from Umrecha village switch . victim has climbed on double pole structure and rejumpering done,he has bypassed switch, and was refinishing work and was checking jumpers.during rechecking of jumper victim got electrocuted and falled down on earth.after accident our team has investgated incident and found on location no.1/57/32/9/90-91 LT line of Sudasana ag fdr top one conductor was in touch with one conductor of 11 kv Talegadh JGY FDR, at 13.00 pm Sudasana ag FDR was started in 3-ph and probably victim has touched jumper on same time and he got shock falled down.primarily he was admitted at satlasana PHC center and then Vadnagar civil hospital. after primary treatment for more treatment we admitted him at Aayush Hospital Mehsana. as per doctor opinion victim has injuries in brain and he is unconscious. Cause : (unexpected return power occurred due to physical contact between the LT conductor of Sudasana Agriculture Feeder and the HT conductor of the Talegadh JGY Feeder at a distant pole location (1/57/32/9/90-91). When the Sudasana Agriculture Feeder was energized at about 13:00 hours, the AB switch jumpers at Bhalusana inadvertently became live. The victim received an electric shock and fell from the Double Pole structure.) | Yet Not Received | N/A | N/A | UNDER INVESTIGATION | N/A
63 | MSN/VIJAPUR/MANSA | BAPUPURA (Rural) | DINESHKUMAR KANUBHAI RAVAL | 2026-02-28 | NFHD | The victim was received the power of complain in r/o Chaudhari Mansinhbhai Hathabhai Consumer No. 21603006133. and victim was attended the complain to restore the power of said consumer at that time victim was climbed on 8 meter psc pole with iron stand for giving new jumper and climb on top lag of the pole but somehow victim was fell down due to sleep of leg and victim was fell down from top step of the pole and got injured due to that mechanical injures done. victim shifted to private hospital for primary treatment and hospitalised. the details are under investigation. | Yet Not Received | N/A | N/A | UNDER INVESTIGATION
64 | MSN/VIJAPUR/MANSA | MANSA (Rural) | DINESHKUMAR PRAHLADBHAI PATEL | 2026-03-19 | FHO | On dated 19.03.2026 extremely heavy wind was started in mansa sub division jurisdiction at around 18.30 hrs onwards and as per information received by victim's relative that Victim was reached out at his farm to see the standing wheat crop and at the same time Victim seen some spark on the standing wheat farm and immediately ran near the sparking area and try to stop the wheat burning incident at that time 11 KV parbatpura JGY location no 13 (Shackle pole ) conductor broken and broken conductor already fell down on victim's farm and somehow victim came in contact with broken conductor and got electrocuted and for primary treatment further shifted in Mansa civil hospital in Private vehicle and present on duty doctor in Mansa civil declared him dead.The details are under investigation. | Yet Not Received | N/A | N/A | N/A | N/A
65 | MSN/Visnagar/Kheralu-1 | NALU (HIRAPURA) (Rural) | OWNER OF COW THAKOR RAMESHJI ANARJI | 2026-03-19 | FAO | On Date 19/03/2026, It was heavy wind (cyclone), Around 09.30 P.M. LT line conductor of 25 KVA JGY Transformer center, due to heavy wind, conductor got tangled together, hence conductor snapped and broken conductor got contected to cow, which was tied near line, and 1no of cow got electrocuted and died on spot | Yet Not Received | N/A | N/A | NA | NA
66 | MSN/Mehsana/Mehsana Industrial | MEHSANA (Urban) | Robinkumar Bhramanand | 2026-03-23 | NFHO | Robinkumar Bhramanand climbed on to Shri Rang Avadhut Society transformer Center & caught 11 KV jumper between transformer's HT Bushing and 11 KV D.O. fuse of Shri Rang Avadhut Society Transformer Center & He got electrocuted. Primary it looks like a suiside purpose. | Yet Not Received | N/A | N/A | NA | NA
67 | MSN/Patan/Sami | Nayka (Rural) | buffalo of Shri 1.GAMI NASHABHAI KAMABHAI and 2.GAMI RASHIKBHAI GANESHBHAI | 2026-03-24 | FAO | During Site Visit,It is found that due to Heavy wind occurred on date 24.3.2026 approx 05:00 pm, at that time buffalo walking around 11kv shamsherpura ag feeder pole line passing through near nayka-shmsherpura road near ground area , pole location number 259/31 HT Line wire accidently break and fall on ground that time buffalo walking below a line so this wire fall on the Buffalo and accidently both buffalo dies due to electric current coming into contact with this live conductor. | Yet Not Received | N/A | N/A | N/A | N/A
68 | MSN/VISNAGAR/Visnagar-1 | Rampura (Rural) | Kantibhai Govindbhai Chuadhary | 2026-03-25 | FHO | On dated 25.03.2026 at approx 14:20 PM, Telephonic message received to Rampura village Line staff shri B D Rathod(ALM) about death of Kantibhai Bhikhabhai Vaghari. Then immediate undersign visited the place and found that on dated 25.03.26 at 12:30 PM, Vagahri Kantibhai Bhikhabhai was helpless found on Northern East side of Rampura to Rajgadh road in Land of Rajubhai Naranbhai near HP Gas godown. This place was 70 meter away from 11 kv Rampura Ag pin pole Loc 81/26/5 and 22 meter away from water irrigated Land. No any tripping was recorded on rampura Ag feeder at 66 kv Valam ss on the day of incident. Furthermore, upon inspection of 11 kv Rampura Ag Loc 81/26/4 & 81/26/5 pole, no any dot or leakage current was detected on the pole. There were no any possibility of electrocution also no any HT/LT line nearer to victim Place hence treated as Suspected Fatal Outsider. | Yet Not Received | N/A | N/A | N/A | N/A
69 | MSN/VIJAPUR/MANSA | DHAMEDA (Rural) | (1) SHAILESHJI GANDAJI THAKOR (Fatal) (2) ROHITJI THAKORJI THAKOR (Non Fatal) | 2026-03-30 | FHO | The Victims are working under the 11 KV Dhameda AG feeder line (between location no 68 and 69) for fitting iron roof on newly constructed iron roof shade temple in the farm of Thakor Vikramji Karshanji while victims are trying to fitting cutting iron roof piece on the iron roof shade at that time somehow iron roof piece came in contact with the one live conductor of the 11 KV Dhameda AG feeder (Emanating from 66 KV Mansa ss) and both the victim's got electrocuted and out of both victim's one is shifted at Private hospital in which present doctor declared him dead and other one is shifted at Gandhinagar civil hospital to Ahmedabad civil hospital the details are under investigation. | Yet Not Received | N/A | N/A | N/A | N/A
70 | MSN/Patan/Jangral | Siyol (Rural) | Bhikhabhai Shankrabhai Makwana(MT)- Emp No.12819 | 2026-03-30 | NFHD | Program of CTPT secondary wiring is arrange for solar captive power plant, to carry out work the victim has climbed on GI ladder which is supported on base angle, but somehow while climbing on GI ladder it got damaged from center in one leg and ladder got unbalanced and victim fallen on ground and got injured in ankle of right leg, then he was transffered to private hospital and further primary treatment is given accordingly, currently victim is under stable condition and detail investigation is under process. | Yet Not Received | N/A | N/A | UNDER INVESTIGATION | N/A
71 | HIMATNAGAR , IDAR , KHEDBRAHMA | GADU(VASAHAT) RURAL | RABARI LALJIBHAI RAMJIBHAI | 2025-10-01 | FA , OUTSIDER | The Accident occurred at village: - Gadu (Vasahat) dated 01.10.25 at approx. 15.20 near gadu vasahat village transformer center, Rabari Laljibhai Ramjibhai was returning to home after grazing his cows, among them one cow passed near to the transformer center fencing which is on the road and died instantly on the spot.By seeing that Rabari Laljibhai Ramjibhai drove away his other cows.We confirmed that there is a leakage current present at TC fencing right now and further resolution is under process. | Yet not received | N/A | N/A | Remove the leackage current (Distribution network , Attributed to COMPANY ) | 15000/10.11.2025
72 | HIMATNAGAR , HIMATNAGAR , HMT R | PIPLODI RURAL | Shree Krishna Yadav | 2025-10-01 | FH , OUTSIDER | On dated 01.10.2025 victim was painting in petrolpump with approximately 24 feet long ladder , while victim and other 2 labour trying to transfer ladder from one side to another side in petrolpump premises . Meanwhile ladder was touched to 11 kv Bhoomi jgy feeder and all 3 labour got electric shocked and one of them Shree Krishna Yadav age 35 was expired on the spot than all 3 labour admitted to civil hospital for primary treatment and one of them shree Krishna Yadav was declared death . | Yet not received | N/A | N/A | BASIC HUMAN MISTAKE,, Distribution network , Attributed to Victim | PENDING DUE TO INSUFFICIENT DOC
73 | HIMATNAGAR , IDAR , JADAR | SINGHA RURAL | BHARVAD JAYRAMBHAI KALUBHAI | 2025-10-04 | FA , OUTSIDER | On Date:- 4.10.2025 the bufellow are passing from behind area of 66 kv singha ss . One buffelow that is passing from under Ag tc of 11 kv canal ag is suddenly shocked and fell down.On investigating there are 2 LT conductors are touched in LT of this TC and so leakage current is found on tc GI Earthing wire with respect to earth. So due to this current , the bufellow came contact with tc earthing wire and bufellow got electrocuted and died on the spot.Detailed Investigation Report and Post Mortem Report under progress. | Yet not received | N/A | N/A | LINE RE-STRINGING OF LINE & RE STRAIGHTTNING OF GUY DONE & TREE CUTTING : Distribution network , Attributed to COMPANY | 15000/16.10.2025
74 | HIMATNAGAR , BHILODA , SHAMLAJI | GALISEMRO RURAL | DAMOR KALIDASBHAI NAVJIBHAI | 2025-10-04 | FA , OUTSIDER | FA ACCIDENT OCCURRED TO COW OF DAMOR KALIDASBHAI NAVJIBHAI AT VILLAGE GALISEMRO, TA. SHAMLAJI, DIST ARAVALI ON DTD. 4.10.2025 AT 12.30 PM, A 3P4W LT LINE WIRE EXTENDING FRO, THE FARM OF DAMOR KALIDASBHAI NAVJIBHAI TO THE TRANSFORMER OF GALISEMTRO AG FEEDER IN AMBAVADI AREA CAUSED A MAJOR SHORT CIRCUIT DUE TO VAGOL BETWEEN THE FOURTH AND FIFTH POL DUE TO THIS ONE PHASE WIRE OF AN LT LINE BROKEN AND FELL ON A COW TIED TO THE FARM AND THE COW ELECTROCUTED AND DIED. DETAIL INVATIGATION IS AWAITED. | Yet not received | N/A | N/A | Routine maintence of LT network is done. Distribution network , Attributed to company
75 | HIMATNAGAR , BHILODA , SHAMLAJI | LUSADIYA RURAL | ASARI ASHISHBHAI KAMJIBHAI | 2025-10-06 | FH , OUTSIDER | A FATAL AQCCIDENT OF OUTSIDER Mr. ASARI ASHISHBHAI KAMAJIBHAI AT, LUSADIYA VILLAGE , TA -SHAMLAJI, DIST- ARAVALLI WAS OCCURRED ON DATED 06.10.2025 TIME 14:04PM. AS PER EYE WITNESS STATEMENT AND PANCHANAMA REPORT VICTIM WAS CLIMBED ON LT POLE LOCATED IN THE OF MALAVIYA RUPSINGBHAI TO ATTEND AG MOTOR COMPLAINT WOTHOUT GIVING INFORMATION TO UGVCL STAFF. SUDDENLY HE FELL DOWN FROM THE POLE AND VILLAGERS WORKING IN THE FARM HAD ADMITTED VICTIM TO THE HOSPITAL. WHERE DOCTOR DECELERED HIM DEAD. .PM REPORT AWAITED AND | Yet not received | N/A | N/A | BASIC HUMAN MISTAKE, Distribution network , Attributed to Victim | NOT LIABLE
76 | HIMATNAGAR , MODASA , MODASA-R2 | Amlai RURAL | Parmar Girishkumar Kodarbhai (ALM) | 2025-10-24 | FH , DEPT | On dated 24/10/2025 , Time Approx 11:45 Am, victim late sh Parmar Girishkumar Kodarbhai was climed on Ag tapping pole for jumpering work at location number HT pole no. 128/4/8 of Napa ag feeder work, he got electric shok and fall down from pole to ground. Due to this the victim was badly injured and immediately shifted him to Aims hospital Modasa in UGVCL hired vehicle. After primary treatment on duty medical officer has declared him dead. Victim and co worker had started work without any line clear permit from substation. The line was made isolated by AB switch from location no.46, but proper communication and confirmation not ensured before starting the work. Even no confirmation of isolation and avoid local earthing process are the route cause of said accident. Detail investigation report is awaited. | Yet not received | N/A | N/A | Line staff were educated to inspect the pole before commensement of work : Distribution network , Attributed to company | NOT LIABLE
77 | HIMATNAGAR , TALOD , TALOD-1 | Umedni Muvadi RURAL | Desai Melabhai Maljibhai | 2025-11-03 | FA , OUTSIDER | Date:- 03/11/2025 3 ph 4 wire Lt Line of 11kv Aniyod ag passing through Luni River, out of them one live wire of LT line had broken & fallen on ground due to heavy wind, at the same time she bufello was Grazing there, while she bufello came near such broken conductor, she got electrocuted & died, Investigation Report and Post Mortem Report under progress. | Yet not received | N/A | N/A | CONDUCTOR RE JOINT & RESTRINGING DONE , Distribution network , Attributed to company | 15000/28.01.2026
78 | HIMATNAGAR , HIMATNAGAR , MEHTAPURA | GADHA RURAL | PARMAR VASHUDEV SHIVAJI | 2025-11-24 | FA , OUTSIDER | After receiving information about a fatal accident of an animal at Gadha village under the Mehtapura Sub Division Office , the line staff of the Sub Division Office , immediately reached at the spot . At that time, a buffalo was found dead under the transformer center of the Prempur AG Feeder . First , a leakage current was found while checking the neutral earthing of the said AG transformer center. Upon further investigation , an aluminum conductor was slipped & got stuck on an iron part , on a PSC pole of LT Line coming from the said AG transformer , due to that the AG transformer neutral earthing was also getting leakage current. After that, repairing the said power fault, no current was found while checking the neutral earthing of the AG transformer again. This entire incident is caused by leakage current at the neutral earthing in the AG transformer. | Yet not received | N/A | N/A | Remove the leackage current , Distribution network , Attributed to company | 15000/03.01.2026
79 | HIMATNAGAR , TALOD , DHANSURA | BHESAVADA RURAL | JAIMINBHAI RAMANLAL BHARVAD PRUTVIRAJ NARANJI BHARVAD | 2025-11-25 | FH , OUTSIDER | DATE-25-11-2025 TIME APPROX 04:10AM EARLY MORNING VICTIM 1)JAIMINBHAI RAMANLAL BHARVAD 2) PRUTVIRAJ NARANJI BHARVAD WERE TRIED TO THEFT OF CONDUCTOR ON EXISTING 11 KV MELDIMATA AG FDR WITH FEEDER IN ON POSION &CAME INTO CONTACT WITH THE LIVE WIRE,THEY GOT ELECTRIC SHOK.DUE TO THIS THE VICTIM S WAS BADLY BURN IN FULL BODY AND THEY ARE DEAD ON THE SPOT. AND UGVCL NOT RESPONSIBLE FOR THESE ACCIDENT POLICE INVESTIGATION REPORT IS AWAITED. | Yet not received | N/A | N/A | THEFT OF CONDUCTOR CASE , Distribution network , Attributed to Victim | NOT LIABLE
80 | HIMATNAGAR , MODASA , MEGHRAJ-2 | Jalampur RURAL | Khant Jethiben Dhirabhai | 2025-11-28 | NFH , OUTSIDER | victim was carrying stack of tree branches on her head which was approx 10 ft long. When she got tired she came near the tree to put that stack of branches down in support with the tree. Near the tree 11 kv line was passing whose span was long and saggy because of some objection in past for pole errection. so when victim tried to put down the stack of tree branches down vetically it came in contact with live 11 kv line. as the branches were fresh ( not dry), victim got shcoked and fell on ground. she was injured and admitted for primary medical treatment at ISRI CHC then further shifted for treatment at himatnagar civil hospital. whose health is now stable. | Yet not received | N/A | N/A | HT CONDUCTOR RESTRINGING DONE Distribution network , Attributed to company | NA
81 | HIMATNAGAR , HIMATNAGAR , MEHTAPURA | ILOL RURAL | BHARVAD DEVABHAI RANABHAI | 2025-05-29 | FH , OUTSIDER & fao | As Message Received About Fatal Accident Immediately UGVCL Staff Visited The Site And Found That Victim And Its Sheep Was Found Dead Near Barbed Wire Fencing Of Private Premise A One Marble And Granite Factory At That Time No Any Leakage Current Found On Private Fencing Of Said Premises While Inquiring The Leakage Current Reason All The Electrical Appliances Of Said Factory Were Turned On And Also Checked That No Physical Electrical Connection Found To Barbed Wire Fencing Around Marble Factory No Live Electrical Power Detected On Barbed Wire Fencing As Well As No Leakage Current Present At Neutral Earthing Of Transformer Center And Meter Installation Of UGVCL No TT And SF Occurred Of 11 KV Savgadh JGY Feeder Between 02 00 Pm To 04 00 Pm Hrs Reason For Death Of Victim And Animal Is Still Under Investigation Above Incident Occurred In Private Premises UGVCL Is Not Responsible For That | Yet not received | N/A | N/A | THERE IS NO ANY NEGLEGENCE FOUND IN NETWORK , Private Premises , Attributed to VICTIM | NA
82 | HIMATNAGAR , IDAR , KHEDBRAHMA | RODHARA RURAL | RABARI SAVAJI KASNAJI | 2025-10-30 | FA , OUTSIDER | The Accident occurred at village: - Rodhara dated 30.10.25 at approx. 12.00 near Rodhara village near farm of Patel Mitulkumar Popatbhai, Rabari Savaji Kasnaji was grazing his buffaloes, among them five buffaloes passed near/touched to the electricity pole which is having moisture due to rainy atmosphere since morning.Buffaloes may be electrocuted due to one of the 11KV HT jumper had touched to the upper part of stay wire hence the leakage current may be passed through the pole upto the ground thus 5 Buffaloes died instantly on the spot. By seeing that Rabari Savaji Kasnaji drove away his other buffaloes. | Yet not received | N/A | N/A | LEKAGE CURRENT PROBLEM RESOLVED BY DOING MAINT. ,Distribution network , Attributed to company | 48000/14.12.2025
83 | HIMATNAGAR , MODASA , TINTOI | Bhatkota RURAL | Bhaveshbhai Punabhai Rabari | 2025-10-31 | FA , OUTSIDER | On Date 31/10/2025 at 100 KVA AG TC near Qlarish lab. In Bhatkota simada a Cow while Grassing at 02:00 PM came near Transformer center got electric shock and died, Primarily found that earthing wire of transformer was open near ground and due to this leakage current passes through earthing wire where cow came in contact got electric shock and died on the spot. Detailed reason of leakage current under investigation . | Yet not received | N/A | N/A | LEKAGE CURRENT PROBLEM RESOLVED BY DOING NECESSARY MAINTANANCE, Distribution network , Attributed to company | 15000/29.01.2026
84 | HIMATNAGAR , IDAR , KHEDBRAHMA | Unchi Dhanal RURAL | (1)Bharatbhai Hirabhai Parmar,Age-24 Year. (2)Kiritbhai Kantibhai Parmar,Age-25 Year (3)Abhisekhbhai Girdharbhai Parmar, 32 Year. | 2025-12-18 | NFH , OUTSIDER | An electrical non-fatal human accident occurred at Village Unchidhanal on 18.12.2025 at approximately 2:40 PM. Contractor labourers were carrying out provinding LT spacer work on AG line at the farm of Shri Patel Vinodbhai Faljibhai. After completing the Lt spacer work at location, while raising the leader erected on the ground, the ground was wet and while applying more force, this leader came into contact with the 11 kV line on it., the long ladder came into contact with 11 KV line of Dantiya AG feeder while shifting the ladder by lifting with labour’s hand. As a result, electric current passed through the ladder and three labourers holding the ladder received electric shock. | Yet not received | N/A | N/A | MISTAKE OF VICTIMS , Distribution network , Attributed to VICTIM | NA
85 | HIMATNAGAR , BHILODA , BHILODA-2 | RINTODA RURAL | VANZARA GANPATBHAI NARSINHBHAI, 60 YEAR | 2025-12-20 | FH , OUTSIDER | AS PER EYE WITNESS STATEMENT , THE VICTIM WAS RESTORING THE BLOWEN OUT DO FUSE OF HIS XMER WITH BAMBOO STICK WITH NACKED HAND AND FOOT. VICTIM GOT ELECTRIC SHOCK AND FALL DOWN ON GROUND. HE WAS SENT TO REFERAL HOSPITAL FOR FURTHUER TREATMENT BUT DR DECLARED HIM DEAD. AT THE TIME OF SITE VISIT THERE IS NO ANY LEAKAGE CURRENT FOUND AND NO ANY FAULT FOUND IN UGVCL SIDE | Yet not received | N/A | N/A | People were educated to Prpoer safety norms must be followed by while working near to live equipment . ,Distribution network , Attributed to VICTIM | PENDING DUE TO INSUFFICIENT DOC
86 | HIMATNAGAR , IDAR , JADAR | VASNA RURAL | Bhavikbhai Rmeshbhai Limbachiya , App LM, Jadar sdn | 2025-12-26 | NFH , DEPT | The non fatal human departmental accident occured at village Vasna Ta Idar on dtd 26.12.2025 At aprox 2.35 PM . For consumer complaintof 3 ph ag power not getting , named chimanbhai ranchodbhai patel at vill Lalpur on vasna Road. For solving the complaint shri J D Nayee EA and Sh B R Limachiya App LM gone on site. Sh J D Nayee EA has checked the AG TC by removing DO Fuse and then after making the DO Fuse and after sh J D Nayee EA and Sh B R Limbachiya both are checking the power suplly on 3 phase ag meter TTB . While checking the power supply on 3 ph ag meter TTB Suddenly with blast fire take place and meter terminal block burnt. and this burning flame come on sh B R Limbachiya"s hand and face and due to this fire flame this burning take place and meter terminal block burnt. There is no electrical leakage but it is due to fire flame. .after that he was taken to CHC Hospital Davad for primary treatment and after that victim shifted to Hope hospital Himmatnagar for more treatment.at present victim health is good and stable and conscious. | Yet not received | N/A | N/A | Line staff were educated to inspect the pole before commensement of work , DISTRIBUTION NETWORK , Attributed to company | NA
87 | HIMATNAGAR , HIMATNAGAR , MEHTAPURA | LALPUR RURAL | Tirgar Govindbhai becharbhai | 2026-01-05 | FH , OUTSIDER | In the morning,the victim was started the electric motor ito fill water meantime the pipe of the electric motor leaked and water was pouring out from the motor. Than after victim, was holding the body of the motor with one hand and tried to fit the leaked pipe with the other hand into the motor. suddenly victim shouted and got electrocuted. Then his son rushed and turn off power supply of the electric motor. After that, the victim's son tried his best to provide first aid and took him to the hospital but victims died on the way.this entire incident took place in the private house of the victim, Uttar Gujarat Electricity Company Limited is not responsible for this fatal electrical accident. | Yet not received | N/A | N/A | ADVISE FOR INSTALLTION OF RCCB OR ELCB IN MAIN .Private premises , Attributed to VICTIM | NA
88 | HIMATNAGAR , HIMATNAGAR , SALAL | Piludra RURAL | Ranjitji Laxmanji Makwana | 2026-01-21 | FA , OUTSIDER | As per Primary investigation, a buffalo found dead on Moyad JGY feeder , LT 2wire line. The stay was found broken & far away about 5"-6" from the dead buffalo. During site visit no leakage current found on the said location. Also LT pole checked by climbing on the pole, but found nothing abnormal or any leakage current. Actual report or reason will be disclosed after PM of the buffalo. The occurence happened at approx. 4pm as witness informed. | Yet not received | N/A | N/A | no any rectification needed, Distribution network , Attributed to company
89 | HIMATNAGAR , HIMATNAGAR , HMT R | Kapoda RURAL | Rabari Nibaram Savaram | 2026-01-23 | FA , OUTSIDER | As per Primary investigation Crowd of Cows and Bull Grazing Near Kapoda village Waterworks Sump and Suddenly Cow came in contact with staywire of Dual Power Double pole structure of 11 kv Isarvada Jgy feeder Cows horn Struck and broke the Staywire Attached to the Double pole Structure of Isarvada Jgy feeder So Lower Part of Staywire (Below Guy insulator ) came in contact with Jumper of AB Switch and current Flows through Staywire so due to electrocution 2 Cows and 1 bull dead at the Site The Occurence happened at approx 12:10 PM as witness informed ,No any Tripping of 11 KV Isarvada Jgy feeder Recorded in Substation when Accident occurred . PM report is awaited | Yet not received | N/A | N/A | New Stay Provided, Maintenance Done, Distribution network , Attributed to company
90 | HIMATNAGAR , TALOD , TALOD-1 | Ujjediya RURAL | Vinodsinh Kanusinh Thakor | 2026-01-30 | NFH , DEPT | Today, dated 30.01.2026, at 18.30 hrs under Talod 1 S/dn. Shri V K Thakor Ele . Assistant with Sh R P patel,ALM gone for jumper work at Gentry in ujjediya SS. Shri R P patel has taken Line clear at 18.05 hr and Earthing done at Gentry and 2nd pole location. Shri v k Thakor weared safety belt and helmet and while climbing on girder for jumper work at around 2.5 meter suddenly his leg slipped on girder and due to unbalance fallen from height so injured and immediately shifted him to shivam arthopedic hospital, himatnagar in office vehicle as per Dr report fractured observed in left leg. And he is in stable position.. | Yet not received | N/A | N/A | Show cause notice served to EA & ALM Distribution network , Attributed to VICTIM | NA
91 | HIMATNAGAR , MODASA , MEGHRAJ-1 | Meghraj RURAL | Mir Bhaveshbhai Maldebhai | 2026-02-03 | FH , OUTSIDER | As per site visit regarding the fatal electrical accident of Mir Bhaveshbhai Maldebhai near Meghraj Range Forest Office. On February 3, 2026, at approximately 09:45 AM, a fatal electrical accident occurred at Vanga Kotar, located opposite the Range Forest Office on the Meghraj-Modasa road, involving a local resident named Mir Bhaveshbhai Maldebhai. The deceased, accompanied by his cousin, was foraging for fodder for his livestock(goats& sheeps) using a custom-made tool consisting of a 19-feet long iron pipe(vansi) with a sickle(datardu) welded to the top. While attempting to cut grass at a height, the victim inadvertently brought the long metallic pipe(vansi) into contact with the overhead 11 kV Bedaj Feeder line, which originates from the 66 kV Meghraj Substation. This contact resulted in an immediate and fatal electric shock, causing death at the site. Initial site observations indicate that the accident was caused by the victim’s use of a highly conductive 19-feet metal tool in close proximity to the high-tension lines, and there appears to be no technical lapse or negligence on the part of UGVCL infrastructure or maintenance. | Yet not received | N/A | N/A | People were educated to Prpoer safety norms must be followed by while working near to live equipment . ,Distribution network , attributed to victim
92 | HIMATNAGAR , MODASA , MALPUR | Kothiya RURAL | 1.Khant Ratibhai Dhirabhai Age: Apprx. 60 years , Resi.of Dalpatpura Aniyor 2.Bharvad Montubhai Malabhai,Age: Apprx. 23 years ,Resi of Kothiya bharvadvas | 2026-02-13 | NFH , OUTSIDER | During the site visit, it was reported that two persons were walking on the footpath in the farm of Bharvad Bhalabhai Kureshibhai Bharvad. While passing near the HT pole of the 11 kV Kothiya Ag Feeder, the HT conductor was found broken from the TC disc hardware (TC connection of Bharvad Bhalabhai Kureshibhai) and was hanging in front of the TC structure pole. The conductor was not connected to the ground. Suddenly, the hanging conductor came in contact with Khant Ratibhai Dhirabhai, who is a partner (Bhagidar) of Bharvad Bhalabhai Kureshibhai, and he got an electric shock. Another person, Bharvad Montubhai Malabhai, who was walking just behind him, tried to help and touched him, and he also got an electric shock. After the incident, nearby people gathered and immediately took both persons to Aniyor Hospital and later shifted them to Modasa Sarvajanik Hospital for further treatment. As per the latest information, both persons are now in stable condition in the hospital. During detailed investigation, it was found that the 11 kV Kothiya Ag Feeder conductor broke from the 11 kV disc shackle hardware due to some reason. Since the broken conductor did not touch the ground, no tripping was recorded in the substation records. | Yet not received | N/A | N/A | BROKEN CONDUCTOR JOINT WORK COMPLETED ,Distribution network , attributed to company | NA
93 | HIMATNAGAR , MODASA , MODASA-R | Nava Vadavasa RURAL | Chauhan Tinabhai Bakabhai | 2026-02-27 | FH , OUTSIDER | During the site visit, it was found that victim and other person installed temporary mandap for potato at his farm, while installing angle,angle touch to 11 kv Miragadh AG over head electric line and victim got electic shock and fell down. Person who was working nearby victim farm called ambulance and admit him at Anjali hospital ranasan. Dr of Anjali hospital declared victim dead. After that admit to Medhasan hospital for PM. | Yet not received | N/A | N/A | People were educated to Prpoer safety norms must be followed by while working near to live equipment . , Distribution network , attributed to victim
94 | HIMATNAGAR , HIMATNAGAR , HMT T | HIMATNAGAR URBAN | Mir Iliyasbhai Allarakhabhai | 2026-02-10 | FH , OUTSIDER | On 11/02/2026 at 17:15 hrs, Letter No. 426/2026 dated 11/02/2026 regarding the occurrence of an electrical fatal accident was received at Himmatnagar Town sdn from B Division police station & the site visited, it was found that the victim was pulling a banner frame of iron pipe approximately 12 feet in length. He was standing on the terrace of the library.After pulling the banner frame with a rope, the iron frame came into contact with the live 11 KV conductor. As a result, the victim got an electric shock and died on the spot.The horizontal distance between the 11 KV line conductor and the building is approximately 8 feet, and the ground clearance of the line is approximately 23 feet.The accident appears to have occurred due to the negligence of the victim. UGVCL is not responsible for the said accident.No TT recorded on fdr ..pulling the banner frame with a rope, the iron frame came into contact with the live 11 KV conductor | Yet not received | N/A | N/A | People were educated to Prpoer safety norms must be followed by while working near to live equipment . , Distribution network , attributed to victim
95 | HIMATNAGAR , IDAR , KHEDBRAHMA | AGIA (CHADA) RURAL | Mr. Ajitbhai Dhulabhai Parghi | 2026-02-21 | FH , OUTSIDER | On 21.02.2026 at approximately 3:00 PM, Mr. Ajitbhai Dhulabhai Parghi, aged 22 years, resident of Village Chada, attempted to start his personal fan at his residence using a private wire connection. As the floor was wet at the time, he accidentally came into direct contact with the live wire and received an electric shock. Upon hearing his loud cries, nearby villagers rushed to the spot and immediately arranged to shift him to Khedbrahma Hospital for treatment through the 108 ambulance service. Get From Local Police Station on date 25.02.2026* 26.02.2026 *Time: 11:30 AM During transit, the victim unfortunately succumbed to the electric shock and was declared dead. It is noted that no main switch or MCB was provided at the residence. The accident occurred due to the use of a private wire connection. There is no fault attributable to UGVCL in this incident as accident occurred in Pvt premise. | Yet not received | N/A | N/A | ADVISE FOR INSTALLTION OF RCCB OR ELCB IN MAIN ,private premises , attributed to victim | NA
96 | HIMATNAGAR , IDAR , KHEROJ | Demati (Gujarmala) RURAL | Gamar Vanrajbhai Narsabhai | 2026-02-22 | FH , OUTSIDER | on dtd 22/02/2026 time 09:00 a fatal human electrical accident occured to Gamar Vanrajbhai Narsabhai at village Demati ()Gujarmala) when victim and others are going on tempo was fully over heighted filled date palm leaves at that time victim touched iron rod which was touched to 11KV line Demati eminating from 66KV Golwada sub station. Related documents will be sent later | Yet not received | N/A | N/A | NECESSARY REQUIRED VERTICAL DISTANCE PROVIDED AND COATED CONDUCTOR PROVIDED AGAINST NORMAL CONDUCTOR ,Distribution network , attributed to victim
97 | HIMATNAGAR , BHILODA , BHILODA-2 | Moti Bebar RURAL | Kanaiyalal Keshabhai Pranami, EA | 2026-03-11 | FH , DEPT | A service cable replacement complaint is received at sub division vide complaint no. 8170 Dtd. 6.03.2026 which is assign to victim by local CCC as he is village helper of that village. But AG motor of that consumer is under repairing so, victim went at site on dated 11/03/2026 at approx. 9:00 AM after confirming with consumer. Victim has called nearby village helper M K Pranami, EA at site to assist the complaint. Victim has first cut the power from DO and Asked M K Pranami to stay at TC structure location. Then he climbed on third pole of LT line from TC with wearing safety helmet for attending replacement of cable complaint, but while climbing on pole his plier fell down. So he hold stay wire with one hand and said consumer to throw plier up. at that time due to excessive pressure on stay, stay wire left out from eye bolt and due to unbalancing employee fell down on ground, his safety helmet also fell down and his head strike on damaged pole lying on ground, So head injury occurs and then victim immediately referred at Mira Hospital Bhiloda, and Dr. Suggested to refer Hope Hospital Himatnagar. After head surgery at hope hospital victim declared dead on Dtd. 12.03.2026 at 20.20 hrs. Detail investigation report is awaited. | Yet not received | N/A | N/A | Staff Informed To Take Necessary Care While Climbing Up And Down From Pole, Distribution network , attributed to victim | NOT LIABLE
98 | HIMATNAGAR , BHILODA , CHORIWAD | CHORIWAD RURAL | CHENVA RAMJIBHAI BHIKHABHAI | 2026-03-03 | FA , OUTSIDER | ON DATED:03/03/2026 TIME: 01.30 PM ,ONE CONDUCTOR OF 11KV CHORIWAD AG HT LINE WAS BROKEN DUE TO HEAVY WIND AND FALLEN ON IRON SHED AND BUFFALO WAS TIED UNDER THIS SHED AND BUFFALO CAME CONTACT WITH IRON SHED AND IRON PIPE.CURRENT PASSES THROUGH IRON SHED AND PIPE AND BUFFALO GOT ELECTROCUTED AND THEN AFTER BUFFALO WAS TREATED BY VATERNARY DOCTOR AND WAS DIED ON 05/03/2026 TIME: 08.30 AM .DETAIL INVESTIGATION IS FURTHER. | Yet not received | N/A | N/A | Necessary instruction given to Contractor , Distribution network , attributed to company
99 | HIMATNAGAR , IDAR , VADALI | Navachamu RURAL | Thakarda Hiraben Mansingbhai | 2026-03-10 | NFH , OUTSIDER | On the Kesarganj JGY feeder, a road crossing LT dead line was passing over the road. During movement of a high-height tempo vehicle through the road crossing, the vehicle came into contact with the LT line. Due to this contact, the LT conductor was pulled with force which resulted in breakage of the pole. Consequently, the pole collapsed and during the incident victim was passing near pole. Victim has minor injury on her leg due to the fallen pole. The incident occurred due to accidental contact of a high-height vehicle with the existing Dead LT road crossing line. Victim has been shifted to Private hospital at idar by ambulance. FIR will be done against vehicle owner tomorrow | Yet not received | N/A | N/A | Consumer is advised to do not work below HT/LT line ,Distribution network , attributed to company | NA
100 | HIMATNAGAR , HIMATNAGAR , HMT-T | Himatnagar URBAN | NAYAK SAGARBHAI PANKAJBHAI | 2026-02-21 | FH , OUTSIDER | The Information Regarding Accident Received On Dated 25.02.2026 From A Division Police Station. Site Visited On 26.02.2026 And Nivedan Taken Of Victim's Father Shri.Nayak Pankajbhai Ratilal. Victim Wanted To Lift Water By Motor On Dtd:25/07/2025.So Victim Switched On Power Supply After Inserting Male Two Pin In Socket With Second End Male Two Pin Connected To Wire In His Left Hand. So Victim Got Electrocuted And Became Unconscious. After He Got Treatment At Various Hospital. But On Dated 21/02/2026 He Declared Dead At GMERS Civil Hospital Himmatnagar. The Accident Occurred In Victim's Private Premises. UGVCL Is Not Responsible For The Said Accident. ACCIDENT OCCURRED ON 25.07.2025 NFH OUTSIDER IN PROVATE PREMISES. BUT CONVERTED INTO FATAL HUMAN OUTSIDER ON 21.02.2026. | Yet not received | N/A | N/A | ADVISE FOR INSTALLTION OF RCCB OR ELCB IN MAIN ,private premises , attributed to victim | NA

## SoP003B
Uttar Gujarat Vij Company Limited
Year 2025-26 (Jan.-26 to March-26)
Performa SoP 003 B:
APPENDIX - B
REGISTER FOR COMPILING THE COMPLAINTS CLASSIFICATION WISE
Classification | Pending complaints of previous Year | Complaints received during the Year | Total complaints | No.of complaints redressed during the month |  |  | Balance complaints to be redressed (4) - (9) | Classification of complaints
|  |  |  | Within stipulated time | Beyond stipulated time | Total
1 | 2 | 3 | 4 = 2 + 3 | 5 | 6 | 7 = 5 + 6 | 8 = 7 - 4 | 9
A(I) | 0 | 29689 | 29689 | 26334 | 3355 | 29689 | 0 | Loose connections at meter, MCB or service line or from pole
A(II) | 0 | 9061 | 9061 | 8086 | 975 | 9061 | 0 | Interruption due to line breakdown
A(III) | 0 | 4387 | 4387 | 3988 | 399 | 4387 | 0 | No power complaint on account of blowing of HT/ DropOut (DO)/ LT fuse
A(IV) | 0 | 1976 | 1976 | 1474 | 502 | 1976 | 0 | Interruption due to failure of transformer or distribution transformer MCB
A(V) | 0 | 1099 | 1099 | 1023 | 76 | 1099 | 0 | Load shedding/ schedule outages
B(I) | 0 | 1295 | 1295 | 1193 | 102 | 1295 | 0 | Ordinary case, which requires no augmentation
B(II) | 0 | 291 | 291 | 216 | 75 | 291 | 0 | Where augmentation is required
B(III) | 0 | 810 | 810 | 759 | 51 | 810 | 0 | Harmonics related issue
B(IV) | 0 | 685 | 685 | 493 | 192 | 685 | 0 | Neutral voltage related issue
B(V) | 0 | 868 | 868 | 651 | 217 | 868 | 0 | Voltage variations related issue
C(I) | 0 | 2487 | 2487 | 2012 | 475 | 2487 | 0 | Stopped/Defective Meters.
C(II) | 0 | 391 | 391 | 306 | 85 | 391 | 0 | Meter accuracy test (Fast/ Slow)
C(III) | 0 | 653 | 653 | 413 | 240 | 653 | 0 | Burnt Meter
C(IV) | 0 | 13 | 13 | 13 | 0 | 13 | 0 | Stolen Meter
C(V) | 0 | 1852 | 1852 | 1686 | 166 | 1852 | 0 | Billing on average basis for more than two bills
C(VI) | 0 | 966 | 966 | 660 | 306 | 966 | 0 | Meter boxes/ metering system
D(I) | 0 | 2045 | 2045 | 1737 | 308 | 2045 | 0 | Loose Wires
D(II) | 0 | 194 | 194 | 158 | 36 | 194 | 0 | Inadequate ground clearance
E(I) | 0 | 2354 | 2354 | 2201 | 153 | 2354 | 0 | For current bills where no additional information is required
E(II) | 0 | 801 | 801 | 697 | 104 | 801 | 0 | Where additional information relating to correctness of reading etc. is required
E(III) | 0 | 99 | 99 | 88 | 11 | 99 | 0 | Final bill for vacation of premises/ change of occupancy
E(IV) | 0 | 216 | 216 | 155 | 61 | 216 | 0 | Change of Tariff
F(I) | 0 | 442 | 442 | 393 | 49 | 442 | 0 | Where extension of LT line up to 150 Metre is required
F(II) | 0 | 225 | 225 | 184 | 41 | 225 | 0 | Where extension of LT line of more than 150 Metre and/or augmentation of distribution transformer is required
F(III) | 0 | 900 | 900 | 819 | 81 | 900 | 0 | Where erection of new distribution transformer is required
F(IV) | 0 | 423 | 423 | 399 | 24 | 423 | 0 | Where erection of new HT line and distribution transformer is required and/ or existing HT line network is required to be augmented
F(V) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Where EHT level line and/ or Sub-station is required to be erected and/ or augmented
F(VI) | 0 | 1418 | 1418 | 1179 | 239 | 1418 | 0 | Modification in connected load
F(VII) | 0 | 1943 | 1943 | 1646 | 297 | 1943 | 0 | Name change/reconnection/ change of category
F(VIII) | 0 | 50 | 50 | 36 | 14 | 50 | 0 | In case connection is denied after payment against demand note
F(IX) | 0 | 255 | 255 | 173 | 82 | 255 | 0 | Transfer of connection
G | 0 | 1594 | 1594 | 1221 | 373 | 1594 | 0 | Request for reconnection/ consumer wanting disconnection
H | 0 | 565 | 565 | 537 | 28 | 565 | 0 | Refund of amount due in regard to temporary connection
I | 0 | 217 | 217 | 155 | 62 | 217 | 0 | Street Light complaint
J | 0 | 6162 | 6162 | 5790 | 372 | 6162 | 0 | Others
Total | 0 | 76426 | 76426 | 66875 | 9551 | 76426 | 0
| 0 | 97364 | 97364 | 94778 | 2586 | 97364 | 0

## SoP004
Uttar Gujarat Vij Company Limited
Year 2025-26 (Jan.-26 to March-26)
Performa SoP 004
Sr. No. | Actions or steps carried out by UGVCL towards public awareness in the quarter | Likely number of consumers influenced | Details about the media
1 | Display board of SOP at circle, Division & S/Dn | 186478 | Notice Board
2 | Display board of Name of information officers under RTI Act 2005 at Circle,Division,Sub- division offices. | 145425 | Notice Board
3 | Consumer care centers at various places | 106092 | Verbal & Notice Board at CCC
4 | Advertisement through Daily News papers | 201361 | Daily News papers
5 | Pamphlets distributed among public | 232915 | Pamphlets
6 | Advertisement through slide in TV / Banners | 94763 | T V Channels
7 | On Web site of Uttar Gujarat Vij Company Limited | 249709 | Internet
8 | Through Regular Energy Bills | 2834216 | Energy Bill
9 | Others | 0 | CD

## SoP005
Uttar Gujarat Vij Company Limited
Year 2025-26 (Jan.-26 to March-26)
Performa SoP 005 : Failure of Distribution Transformer.
Sr. No. | No. of existing Distribution transformer at the start of the Quarter | No.of Distribution transformers added during the Quarter | Total number of Distribution transformers | Total number of Distribution transformer failed during the Quarter | % failure rate of Distribution transformer
| A | B | C=A+B | D | E = (D) * 100/C
1 | 458125 | 4856 | 462981 | 4314 | 0.93179
Total | 458125 | 4856 | 462981 | 4314 | 0.93179

## SoP007
Uttar Gujarat Vij Company Limited
Year 2025-26 (Oct.-25 to March-26)
Performa SoP 007: Compliance of Sample Test result for Neutral Voltage
Sr. No | Category of consumers | Sample Size (Numbers) | Standard specified in regulations | Non-Deviation of results from the sample test (Numbers) | % age compliance
(6) = (5)*100/(3)
1 | 2 | 3 | 4 | 5 | 6
LT consumers
1 | Domestic | 124278 | 2% | 1672 | 1.3454
2 | Commercial | 12525 | 2% | 165 | 1.3174
3 | Industrial | 3775 | 2% | 31 | 0.82119
4 | Agricultural | 26336 | 2% | 994 | 3.7743
5 | Public water works | 2143 | 2% | 31 | 1.4466
HT consumers
6 | HT Industrial | 1606 | 2% | 6 | 0.3736

## SoP008
Uttar Gujarat Vij Company Limited
Year 2025-26 (Oct.-25 to March-26)
Performa SoP 008: Compliance of Sample Test Report for voltage variations
1 | 2 | 3 | 4 | 5
Voltage Level | Sample Size (numbers) | Limit or prescribed standard | Non-Deviation of results from the sample test (Numbers)
% age compliance
(5) = (4)*100/(2)
Low Voltage | 10221 | +6% to -6% | 227 | 2.2209
High Voltage | 1328 | +6% to -9% | 14 | 1.0542
Extra High Voltage | 14 | +10% to -12.5% | 0 | 0

## SoP009
Uttar Gujarat Vij Company Limited
Year 2025-26 (Oct.-25 to March-26)
Performa SoP 009: Compliance of Sample Test result for Harmonics
1 | 2 | 3 | 4 | 5 | 6
Sr. No | Category of consumers | Sample size (Numbers) | Limit or prescribed standard | Non- Deviation of results from the sample test (Numbers) | %age compliance
(6) = (5)*100/(3)
1 | LT consumers | 11555 | 3.5% | 30 | 0.25963
2 | HT consumers | 367 | 3% | 9 | 2.4523
3 | EHT consumers | 5 | 3% | 0 | 0

## SoP010 to 13 AG
Uttar Gujarat Vij Company Limited
Year 2025-26 (Jan.-26 to March-26)
SoP 010 - A : System Average Interruption Frequency Index (SAIFI) for AG. Dominant Category
Sr. No | Month | Number of Sustained Interruptions during the Reporting Period = Ai | Number of Interrupted Customers for Sustained Interruption events during the Reporting Period = Ni | Total number of Customers Served for the Areas = Nt | Total Number of Interrupted Customers for Sustained Interruption events during the Reporting Period = Σ (Ai x Ni) | SAIFI = Σ (Ai x Ni) / Nt
1 | 2 | 3 | 4 | 5 | 6 = Σ (3 x 4) | 7 = 6 / 5
1 | 2026-01-01 | 25341 | 633523 | 730643 | 6546830 | 8.9604
2 | 2026-02-01 | 16543 | 553038 | 732772 | 4268841 | 5.8256
3 | 2026-03-01 | 35571 | 626804 | 734133 | 8815712 | 12.0083
Total |  | 77455 | 1813365 | 2197548 | 19631383 | 8.9333
SoP 011 : System Average Interruption Duration Index (SAIDI) for AG. Dominant category
Sr. No | Month | Number of Sustained Interruptions during the Reporting Period = Ai | Total Outage Duration | Restoration time for each Interruption Event = Ri | Number of Interrupted Customers for Sustained Interruption events during the Reporting Period = Ni | Total Customer Interruption Duration = Ri x Ni | Total Number of Customers Served for the Areas = Nt | Cumulative Customer Interruptions Duration = Σ (Ri x Ni) | SAIDI = Σ (Ri x Ni) / Nt
|  | Nos | Hr : Min | Hr : Min | Nos | Hr : Min | Nos | Hr : Min | Hr : Min
1 | 2 | 3 | 4 | 5 = 4 / 3 | 6 | 7 = 5 * 6 | 8 | 9 = Σ (5 x 6) | 10 = 9 / 8
1 | 2026-01-01 | 25341 | 1902-07-27 05:33 | 0:53 | 633523 | 23480.7083 | 730643 | 237570.0167 | 0.32515
2 | 2026-02-01 | 16543 | 1901-07-05 01:29 | 0:48 | 553038 | 18455.6174 | 732772 | 2250-02-06 01:14 | 0.17451
3 | 2026-03-01 | 35571 | 1903-12-18 08:53 | 0:59 | 626804 | 25522.0264 | 734133 | 333994.2934 | 0.45495
Total |  | 77455 | 1908-01-17 15:55 | 0:55 | 1813365 | 67458.3521 | 2197548 | 699437.3612 | 0.31828
SoP 012 : Momentary Average Interruption Frequency Index (MAIFI) for AG. Dominant category
Sr. No | Month | Total Number of Momentary interruptions = Imi | Total Number of Consumers affected due to Momentary Interruption Events during the Reporting Period = Nmi | Number of Customer Momentary Interruptions = IMi * Nmi | Total Number of Customers Served for the Areas = Nt | Cumulative Momentary Customer Interruptions = Σ (Imi x Nmi) | MAIFI = Σ (IMi x Nmi)/ Nt
1 | 2 | 3 | 4 | 5 = 3 * 4 | 6 | 7 = Σ (3 x 4) | 8=7/6
1 | 2026-01-01 | 28724 | 638811 | 18349207164 | 730643 | 7570171 | 10.361
2 | 2026-02-01 | 18475 | 467821 | 8642992975 | 732772 | 4858664 | 6.6305
3 | 2026-03-01 | 27929 | 532772 | 14879789188 | 734133 | 7431717 | 10.1231
Total |  | 75128 | 1639404 | 123165143712 | 2197548 | 19860552 | 9.0376
SoP 013 – : Customer Average Interruption Duration Index (CAIDI) for AG. Dominant category
Sr. No | Month | Total Number of Sustained Interruptions during the Reporting Period = Σ Ai | Total Restoration time for Interruption Events = Σ Ri | Total Number of Interrupted Customers for Sustained Interruption events during the Reporting Period = Σni | CAIDI=Σ (Ri x Ni) / Σ (Ai x Ni) = SAIDI/ SAIFI
1 | 2 | 3 | 4 | 5 | 6 = (4 x 5) / (3 x 5)
1 | 2026-01-01 | 25341 | 1902-07-27 05:33 | 633523 | 0.036288
2 | 2026-02-01 | 16543 | 1901-07-05 01:29 | 553038 | 0.029955
3 | 2026-03-01 | 35571 | 1903-12-18 08:53 | 626804 | 0.037886
Total |  | 77455 | 1908-01-17 15:55 | 1813365 | 0.035629
Formulas:
Hr : Min = [Hr : Min]/[Nos]
Hr : Min = SUM(D15:[Hr : Min, row above])

## SoP010 to 13 JGY
Uttar Gujarat Vij Company Limited
Year 2025-26 (Jan.-26 to March-26)
SoP 010 - A : System Average Interruption Frequency Index (SAIFI) for JGY Dominant Category
Sr. No | Month | Number of Sustained Interruptions during the Reporting Period = Ai | Number of Interrupted Customers for Sustained Interruption events during the Reporting Period = Ni | Total number of Customers Served for the Areas = Nt | Total Number of Interrupted Customers for Sustained Interruption events during the Reporting Period = Σ (Ai x Ni) | SAIFI = Σ (Ai x Ni) / Nt
1 | 2 | 3 | 4 | 5 | 6 = Σ (3 x 4) | 7 = 6 / 5
1 | 2026-01-01 | 5642 | 1814082 | 2145276 | 11776876 | 5.4897
2 | 2026-02-01 | 2950 | 1409689 | 2149390 | 5742646 | 2.6718
3 | 2026-03-01 | 7124 | 1745187 | 2151118 | 14043608 | 6.5285
Total |  | 15716 | 4968958 | 6445784 | 31563130 | 4.8967
SoP 011 : System Average Interruption Duration Index (SAIDI) for JGY Dominant category
Sr. No | Month | Number of Sustained Interruptions during the Reporting Period = Ai | Total Outage Duration | Restoration time for each Interruption Event = Ri | Number of Interrupted Customers for Sustained Interruption events during the Reporting Period = Ni | Total Customer Interruption Duration = Ri x Ni | Total Number of Customers Served for the Areas = Nt | Cumulative Customer Interruptions Duration = Σ (Ri x Ni) | SAIDI = Σ (Ri x Ni) / Nt
|  | Nos | Hr : Min | Hr : Min | Nos | Hr : Min | Nos | Hr : Min | Hr : Min
1 | 2 | 3 | 4 | 5 = 4 / 3 | 6 | 7 = 5 * 6 | 8 | 9 = Σ (5 x 6) | 10 = 9 / 8
1 | 2026-01-01 | 5642 | 1900-06-03 19:50 | 0:40 | 1814082 | 3739:50 | 2145276 | 284328.8772 | 0.13254
2 | 2026-02-01 | 2950 | 1900-04-09 17:33 | 0:49 | 1409689 | 2417:33 | 2149390 | 2384-01-10 10:49 | 0.082251
3 | 2026-03-01 | 7124 | 1900-06-21 11:38 | 0:35 | 1745187 | 4163:38 | 2151118 | 304706.8758 | 0.14165
Total |  | 15716 | 1901-03-05 01:02 | 0:39 | 4968958 | 10321:02 | 6445784 | 765824.2036 | 0.11881
SoP 012 : Momentary Average Interruption Frequency Index (MAIFI) for JGY Dominant category
Sr. No | Month | Total Number of Momentary interruptions = Imi | Total Number of Consumers affected due to Momentary Interruption Events during the Reporting Period = Nmi | Number of Customer Momentary Interruptions = IMi * Nmi | Total Number of Customers Served for the Areas = Nt | Cumulative Momentary Customer Interruptions = Σ (Imi x Nmi) | MAIFI = Σ (IMi x Nmi)/ Nt
1 | 2 | 3 | 4 | 5 = 3 * 4 | 6 | 7 = Σ (3 x 4) | 8=7/6
1 | 2026-01-01 | 7406 | 1889929 | 13996814174 | 2145276 | 17539670 | 8.176
2 | 2026-02-01 | 3382 | 1351024 | 4569163168 | 2149390 | 7512440 | 3.4951
3 | 2026-03-01 | 6003 | 1519707 | 9122801121 | 2151118 | 13056536 | 6.0697
Total |  | 16791 | 4760660 | 79936242060 | 6445784 | 38108646 | 5.9122
SoP 013 – : Customer Average Interruption Duration Index (CAIDI) for JGY Dominant category
Sr. No | Month | Total Number of Sustained Interruptions during the Reporting Period = Σ Ai | Total Restoration time for Interruption Events = Σ Ri | Total Number of Interrupted Customers for Sustained Interruption events during the Reporting Period = Σni | CAIDI=Σ (Ri x Ni) / Σ (Ai x Ni) = SAIDI/ SAIFI
1 | 2 | 3 | 4 | 5 | 6 = (4 x 5) / (3 x 5)
1 | 2026-01-01 | 5642 | 1900-06-03 19:50 | 1814082 | 0.024143
2 | 2026-02-01 | 2950 | 1900-04-09 17:33 | 1409689 | 0.030785
3 | 2026-03-01 | 7124 | 1900-06-21 11:38 | 1745187 | 0.021697
Total |  | 15716 | 1901-03-05 01:02 | 4968958 | 0.024263
Formulas:
Hr : Min = [Hr : Min]/[Nos]
Hr : Min = SUM(D15:[Hr : Min, row above])

## SoP010 to13 other than AG & JGY
Uttar Gujarat Vij Company Limited
Year 2025-26 (Jan.-26 to March-26)
SoP 010 - A : System Average Interruption Frequency Index (SAIFI) for other than Ag & JGY Dominant Category
Sr. No | Month | Number of Sustained Interruptions during the Reporting Period = Ai | Number of Interrupted Customers for Sustained Interruption events during the Reporting Period = Ni | Total number of Customers Served for the Areas = Nt | Total Number of Interrupted Customers for Sustained Interruption events during the Reporting Period = Σ (Ai x Ni) | SAIFI = Σ (Ai x Ni) / Nt
1 | 2 | 3 | 4 | 5 | 6 = Σ (3 x 4) | 7 = 6 / 5
1 | 2026-01-01 | 2178 | 782164 | 1527262 | 3486193 | 2.2826
2 | 2026-02-01 | 1191 | 478158 | 1535607 | 1174192 | 0.76464
3 | 2026-03-01 | 2181 | 592257 | 1545063 | 2259261 | 1.4622
Total |  | 5550 | 1852579 | 4607932 | 6919646 | 1.5017
SoP 011 : System Average Interruption Duration Index (SAIDI) for other than Ag & JGY Dominant category
Sr. No | Month | Number of Sustained Interruptions during the Reporting Period = Ai | Total Outage Duration | Restoration time for each Interruption Event = Ri | Number of Interrupted Customers for Sustained Interruption events during the Reporting Period = Ni | Total Customer Interruption Duration = Ri x Ni | Total Number of Customers Served for the Areas = Nt | Cumulative Customer Interruptions Duration = Σ (Ri x Ni) | SAIDI = Σ (Ri x Ni) / Nt
|  | Nos | Hr : Min | Hr : Min | Nos | Hr : Min | Nos | Hr : Min | Hr : Min
1 | 2 | 3 | 4 | 5 = 4 / 3 | 6 | 7 = 5 * 6 | 8 | 9 = Σ (5 x 6) | 10 = 9 / 8
1 | 2026-01-01 | 2178 | 1900-05-03 05:14 | 1:22 | 782164 | 2981:14 | 1527262 | 2149-09-09 06:41 | 0.059714
2 | 2026-02-01 | 1191 | 1900-08-01 00:13 | 4:19 | 478158 | 5136:13 | 1535607 | 1985-07-22 13:01 | 0.020351
3 | 2026-03-01 | 2181 | 1900-03-16 00:39 | 0:50 | 592257 | 1824:39 | 1545063 | 2048-03-31 18:34 | 0.035046
Total |  | 5550 | 1901-02-17 06:06 | 1:47 | 1852579 | 9942:06 | 4607932 | 2383-07-04 14:16 | 0.038325
SoP 012 : Momentary Average Interruption Frequency Index (MAIFI) for other than Ag & JGY Dominant category
Sr. No | Month | Total Number of Momentary interruptions = Imi | Total Number of Consumers affected due to Momentary Interruption Events during the Reporting Period = Nmi | Number of Customer Momentary Interruptions = IMi * Nmi | Total Number of Customers Served for the Areas = Nt | Cumulative Momentary Customer Interruptions = Σ (Imi x Nmi) | MAIFI = Σ (IMi x Nmi)/ Nt
1 | 2 | 3 | 4 | 5 = 3 * 4 | 6 | 7 = Σ (3 x 4) | 8=7/6
1 | 2026-01-01 | 2132 | 768460 | 1638356720 | 1527262 | 4790484 | 3.1366
2 | 2026-02-01 | 898 | 456657 | 410077986 | 1535607 | 1266392 | 0.82468
3 | 2026-03-01 | 1329 | 459157 | 610219653 | 1545063 | 1731939 | 1.121
Total |  | 4359 | 1684274 | 7341750366 | 4607932 | 7788815 | 1.6903
SoP 013 – : Customer Average Interruption Duration Index (CAIDI) for other than AG & JGY Dominant category
Sr. No | Month | Total Number of Sustained Interruptions during the Reporting Period = Σ Ai | Total Restoration time for Interruption Events = Σ Ri | Total Number of Interrupted Customers for Sustained Interruption events during the Reporting Period = Σni | CAIDI=Σ (Ri x Ni) / Σ (Ai x Ni) = SAIDI/ SAIFI
1 | 2 | 3 | 4 | 5 | 6 = (4 x 5) / (3 x 5)
1 | 2026-01-01 | 2178 | 1900-05-03 05:14 | 782164 | 0.02616
2 | 2026-02-01 | 1191 | 1900-08-01 00:13 | 478158 | 0.026615
3 | 2026-03-01 | 2181 | 1900-03-16 00:39 | 592257 | 0.023967
Total |  | 5550 | 1901-02-17 06:06 | 1852579 | 0.025521
Formulas:
Hr : Min = [Hr : Min]/[Nos]
Hr : Min = SUM(D15:[Hr : Min, row above])

## SoP010 to 13 Overall
Uttar Gujarat Vij Company Limited
Year 2025-26 (Jan.-26 to March-26)
SoP 010 - A : System Average Interruption Frequency Index (SAIFI) for Overall Dominant Category
Sr. No | Month | Number of Sustained Interruptions during the Reporting Period = Ai | Number of Interrupted Customers for Sustained Interruption events during the Reporting Period = Ni | Total number of Customers Served for the Areas = Nt | Total Number of Interrupted Customers for Sustained Interruption events during the Reporting Period = Σ (Ai x Ni) | SAIFI = Σ (Ai x Ni) / Nt
1 | 2 | 3 | 4 | 5 | 6 = Σ (3 x 4) | 7 = 6 / 5
1 | 2026-01-01 | 33161 | 3229769 | 4403181 | 21809899 | 4.9532
2 | 2026-02-01 | 20684 | 2440885 | 4417769 | 11185679 | 2.532
3 | 2026-03-01 | 44876 | 2964248 | 4430314 | 25118581 | 5.6697
Total |  | 98721 | 8634902 | 13251264 | 58114159 | 4.3856
SoP 011 : System Average Interruption Duration Index (SAIDI) for Overall Dominant category
Sr. No | Month | Number of Sustained Interruptions during the Reporting Period = Ai | Total Outage Duration | Restoration time for each Interruption Event = Ri | Number of Interrupted Customers for Sustained Interruption events during the Reporting Period = Ni | Total Customer Interruption Duration = Ri x Ni | Total Number of Customers Served for the Areas = Nt | Cumulative Customer Interruptions Duration = Σ (Ri x Ni) | SAIDI = Σ (Ri x Ni) / Nt
|  | Nos | Hr : Min | Hr : Min | Nos | Hr : Min | Nos | Hr : Min | Hr : Min
1 | 2 | 3 | 4 | 5 = 4 / 3 | 6 | 7 = 5 * 6 | 8 | 9 = Σ (5 x 6) | 10 = 9 / 8
1 | 2026-01-01 | 33161 | 1903-05-03 06:37 | 0:53 | 3229769 | 1219.2758 | 4403181 | 613098.1722 | 0.13924
2 | 2026-02-01 | 20684 | 1902-05-15 19:15 | 1:00 | 2440885 | 20803:15 | 4417769 | 335912.0442 | 0.076037
3 | 2026-03-01 | 44876 | 1904-08-23 21:10 | 0:54 | 2964248 | 1697.882 | 4430314 | 692849.943 | 0.15639
Total |  | 98721 | 1910-05-10 23:02 | 0:55 | 8634902 | 3783.9601 | 13251264 | 1641860.1594 | 0.1239
SoP 012 : Momentary Average Interruption Frequency Index (MAIFI) for Overall Dominant category
Sr. No | Month | Total Number of Momentary interruptions = Imi | Total Number of Consumers affected due to Momentary Interruption Events during the Reporting Period = Nmi | Number of Customer Momentary Interruptions = IMi * Nmi | Total Number of Customers Served for the Areas = Nt | Cumulative Momentary Customer Interruptions = Σ (Imi x Nmi) | MAIFI = Σ (IMi x Nmi)/ Nt
1 | 2 | 3 | 4 | 5 = 3 * 4 | 6 | 7 = Σ (3 x 4) | 8=7/6
1 | 2026-01-01 | 38262 | 3297200 | 126157466400 | 4403181 | 29900325 | 6.7906
2 | 2026-02-01 | 22755 | 2275502 | 51779048010 | 4417769 | 13637496 | 3.087
3 | 2026-03-01 | 35261 | 2511636 | 88562796996 | 4430314 | 22220192 | 5.0155
Total |  | 96278 | 8084338 | 778343893964 | 13251264 | 65758013 | 4.9624
SoP 013 – : Customer Average Interruption Duration Index (CAIDI) for Overall category
Sr. No | Month | Total Number of Sustained Interruptions during the Reporting Period = Σ Ai | Total Restoration time for Interruption Events = Σ Ri | Total Number of Interrupted Customers for Sustained Interruption events during the Reporting Period = Σni | CAIDI=Σ (Ri x Ni) / Σ (Ai x Ni) = SAIDI/ SAIFI
1 | 2 | 3 | 4 | 5 | 6 = (4 x 5) / (3 x 5)
1 | 2026-01-01 | 33161 | 1903-05-03 06:37 | 3229769 | 0.028111
2 | 2026-02-01 | 20684 | 1902-05-15 19:15 | 2440885 | 0.030031
3 | 2026-03-01 | 44876 | 1904-08-23 21:10 | 2964248 | 0.027583
Total |  | 98721 | 1910-05-10 23:02 | 8634902 | 0.028252
Formulas:
Hr : Min = [Hr : Min]/[Nos]
Hr : Min = SUM(D15:[Hr : Min, row above])

## SoP015
Uttar Gujarat Vij Company Limited
Year 2025-26 (Jan.-26 to March-26)
Performa SoP 015 : Meter faults
Consumer Category | No. of faulty meters at the start of the Quarter | No. of faulty meters added during the Quarter | Total No. of defective / faulty meter | No. of faulty Meters repaired and replaced | No. of faulty meters pending at the end of the Quarter
| 1 | 2 | 3=2+1 | 4 | 5=3-4
Single Phase | 8989 | 20482 | 29471 | 20656 | 8815
Three Phase | 4342 | 8120 | 12462 | 8214 | 4248
HT | 0 | 0 | 0 | 0 | 0
Total | 13331 | 28602 | 41933 | 28870 | 13063

## SoP016
Uttar Gujarat Vij Company Limited
Year 2025-26 (Jan.-26 to March-26)
Performa SoP 016 : Compensation details
COMPENSATION DETAILS
Sr. No. | Service Area | Compensation payable to consumer for the period of default in case of violation of standard | Claimed |  | Payable
|  |  | No. of cases | Amount (Rs.) | No. of cases in which compensation is payable | Amount payable (Rs.) | Amount paid (Rs.)
1 | Registration of complaint and intimation of Unique complaint Number to the Complainant | Rs. 50/- for each default | Nil |  | Nil
2 | Issuance of Demand Note for New Connection, Load Enhancement, Shifting of connection at other premises, Conversion of Service, Temporary Supply, Shifting of Service Connection in exiting premises, Deviation of line and Shifting of equipments | Rs. 50 for each day of default.
3 | New Connection, Load Enhancement, Shifting of connection at other premises and Conversion of Service where no Network erection and/or augmentation is required. | Rs. 50 for each day of default.
4 | New Connection, Load Enhancement, Shifting of connection at other premises and Conversion of Service where Network erection and/or augmentation is required. | Rs. 50 for each day of default.
5 | Release of temporary supply | Rs. 50 for each day of default.
6 | Shifting of meter/services in the existing premises | Rs. 50 for each day of default.
7 | Shifting of LT/HT lines
8 | Shifting of Transformer structures
9 | Settlement of amount for refunding of excess amount after completion of work.
10 | Transfer of Service Connection with respect to change of name or change of ownership | Rs. 50 for each day of default.
11 | Application from consumer requesting Change in Tariff Class/Category. | Rs. 50 for each day of default.
12 | Complaint Related to Billing | Rs. 50 for each day of default.
13 | Replacement of Meter | Rs. 25/- for each day of default subject to maximum of Rs. 1500/- for LT connections and Rs. 250/- for each day of default subject to maximum of Rs. 2500/- for HT connections.
14 | Reconnection of Supply | Rs. 25/- for each six hours (or part thereof) of delay in restoration of supply subject to maximum Rs. 500/- for LT connection and Rs. 50/- for each six hours (or part thereof) of delay in restoration of supply subject to maximum Rs. 1000/- for HT connection.
15 | More than 2 interruptions in a day to the consumer for the reasons not attributable to the nature of fault as mentioned in Clause 8.4 of these Regulations. | Rs. 25/- for each interruption subject to maximum Rs. 500/- for LT connection and Rs. 50/- for each interruption subject to maximum Rs.1000/- for HT connection.
16 | Failure to restore power supply in case of blowing of fuse of LT side distribution transformer, at consumer premises, trouble of MCB of distribution transformer, loose connection at pole, MCB or meter, etc. | Rs. 50/- per hour per Consumer for the first two hours of default. Thereafter Rs. 100/- per hour per Consumer subject to maximum of Rs. 500/- per day for LT consumer and maximum of Rs. 2000/- per day for HT consumer.
17 | Failure to restore power supply in case of blowing of HT side fuse of distribution transformer
18 | Failure to restore power supply in case of HT and LT line fault
19 | Failure to restore power supply in case of Distribution transformer failure
20 | Failure to restore power supply in case of failure of underground service or underground HT/LT cable
21 | Scheduled Power Outage | Rs. 50/- per hour per Consumer for the first two hours of default. Thereafter Rs. 100/- per hour per Consumer
22 | Site Visit and Intimation to the Consumer about likely time to resolve the complaint related to voltage fluctuation. | Rs. 200/- for each instance for each complaint.
23 | Complaint of Neutral Voltage | Rs. 250/- for each complaint
24 | Complaint regarding Voltage variations at the point of commencement of supply. | Rs. 25/- for each day of default subject to maximum of Rs. 500/-

## SoP017
Uttar Gujarat Vij Company Limited
Year 2025-26 (Jan.-26 to March-26)
Performa SoP 017: Individual Complaint where Compensation has been paid
Sr. No. | Complaint No. | Date of filing Complaint/ Automatic Compensation | Consumer No. and Name and Address of the Consumer | Nature of Complaint | Reference Standard of Performance | Amount of compensation (Rs.) | Whether Compensation paid automatically or Consumer has to approach CGRF to get compensation | Whether CGRF has upheld demand of Consumer of Compensation and if Yes, date of order of CGRF and date of compensation paid
Nil

## SoP018
Uttar Gujarat Vij Company Limited
Year 2025-26 (Jan.-26 to March-26)
Performa SoP 018: Unauthorised Use of electricity
No. of cases booked | No. of cases where UUE is established by the Licensee | No. of cases where appeal filed by the consumer before the Appellate Authority | No. of cases decided by the Appellate Authority in favour of the Licensee | No. of cases decided by the Appellate Authority in favour of the consumer
1341 | 1341 | 0 | 0 | 0

## SoP019
Uttar Gujarat Vij Company Limited
Year 2025-26 (Jan.-26 to March-26)
SoP 019: Theft of electricity
No. of cases booked | No. of complaints filed by the Licensee in Police Station | No. of cases in which judgment delivered by the Special Court | No. of cases decided by the Special Court in favour of Licensee | No. of cases decided by the Special Court in favour of Consumer
2580 | 2580 | 0 | 0 | 0