## INDEX
Sr. No | Performa/ Sheet Name | Particulars | Frequency
1 | Sop 001 | Fatal and Non-fatal accident report | Quarterly
2 | Sop 002 | Action taken report for safety measures complied for the accidents occurred | Half Yearly
3 | Sop 003 | Register For Compiling The Complaints {As per Appendix B of the regulation} | Quarterly
4 | Sop 004 | Publicity carried out | Quarterly
5 | Sop 005 | Failure of Distribution Transformer | Quarterly
6 | Sop 006 | Failure of Power Transformer | Quarterly
1 | Sop 007 | Sample Test result for Neutral Voltage | Yearly
2 | Sop 008 | Sample Test result for Voltage variations | Yearly
3 | Sop 009 | Sample Test result for Harmonics | Yearly
4 | Sop 010 - A | Reliability Indices – SAIFI | Yearly
5 | Sop 011 | Reliability Indices – SAIDI | Yearly
6 | Sop 012 | Reliability Indices – MAIDI | Yearly
7 | Sop 013 | Reliability Indices – CAIDI | Yearly
14 | Sop 014 | System Losses at EHT/11 KV and Below | Half Yearly
15 | Sop 015 | Meter faults | Quarterly
16 | Sop 016 | Compensation details | Quarterly
17 | Sop 017 | Individual Complaint where Compensation has been paid | Quarterly
18 | Sop 018 | Unauthorised Use of electricity | Quarterly
19 | Sop 019 | Theft of electricity | Quarterly

## Banner
STANDARD OF PERFORMANCE COMPLIANCE REPORT YEAR : 2025-26
Reported By Pascim Gujarat Vij Company Limited
Submitted To : GUJARAT ELECTRICITY REGULATORY COMMISSION
Report: April-2025 to March-2026

## 007
Paschim Gujarat Vij Company Limited
Year 2025-26 (April-25 to March-26)
Performa SoP 007: Sample Test result for Neutral Voltage
Compliance Sample Test Report for Neutral Voltage
Sr. No | Sr. No | Category of consumers | Sample Size (Numbers) | Standard specified in regulations | Non-Deviation of results from the sample test (Numbers) | % age compliance
(6) = (5)*100/(3)
1 |  | 2 | 3 | 4 | 5 | 6
| PGVCL | LT consumers
1 |  | Domestic | 1178 | 2% | 1178 | 100
2 |  | Commercial | 547 | 2% | 547 | 100
3 |  | Industrial | 417 | 2% | 417 | 100
4 |  | Agricultural | 560 | 2% | 560 | 100
5 |  | Public water works | 133 | 2% | 133 | 100
HT consumers
6 |  | HT Industrial | 158 | 2% | 158 | 100

## 008
Paschim Gujarat Vij Company Limited
Year 2025-26 (April-25 to March-26)
Performa SoP 008: Sample Test Report for voltage variations
Compliance Sample Test Report for Voltage variations
1 | 2 | 3 | 4 | 5
Voltage Level | Sample Size (numbers) | Limit or prescribed standard | Non-Deviation of results from the sample test (Numbers)
% age compliance
(5) = (4)*100/(2)
Low Voltage | 1630 | +6% to -6% | 1630 | 100
High Voltage | 392 | +6% to -9% | 392 | 100
Extra High Voltage | 36 | +10% to -12.5% | 36 | 100

## 009
Performa SoP 009: Sample Test result for Harmonics
Compliance Sample Test Report for Harmonics (2025-26)
1 | 2 | 3 | 4 | 5 | 6
Name of Area/Circle | Category of consumers | Sample size (Numbers) | Limit or standard prescribed | Deviation of results from the sample test (Numbers) | %age compliance (6) = (5)*100/(3)
BTD | LT consumers
HT consumers
EHT consumers
AMR | LT consumers
HT consumers
EHT consumers
SNR | LT consumers
HT consumers
EHT consumers
PGVCL | LT consumers | #REF! | 3.5 | #REF! | #REF!
| HT consumers | #REF! | 3.5 | #REF! | #REF!
| EHT consumers | #REF! | 3.5 | #REF! | #REF!
TOTAL | LT consumers | 0 | 3.5% | 0 | #DIV/0!
| HT consumers | 382 | 3% | 382 | 100
| EHT consumers | 0 | 3% | 0 | #DIV/0!

## SoP 010-013 Overall
Paschim Gujarat Vij Company Limited
Year 2025-26 (April-25 to March-2026)
SoP 010 - A : System Average Interruption Frequency Index (SAIFI) for Overall Category (To be submitted Quarterly and Annually)
Sr. No | Month | Number of Sustained Interruptions during the Reporting Period = Ai | Number of Interrupted Customers for Sustained Interruption events during the Reporting Period = Ni | Total number of Customers Served for the Areas = Nt | Total Number of Interrupted Customers for Sustained Interruption events during the Reporting Period = Σ (Ai x Ni) (Monthly SAIFI) | SAIFI = Σ (Ai x Ni) / Nt
1 | 2 | 3 | 4 | 5 | 6 = Σ (3 x 4) | 7 = 6 / 5
1 | 2025-04-01 | 113414 | 5334855 | 6324707 | 62932223 | 9.9502
2 | 2025-05-01 | 223563 | 5627901 | 6336420 | 128412304 | 20.2658
3 | 2025-06-01 | 207393 | 5616990 | 6353086 | 115267141 | 18.1435
4 | 1st Qtr | 544370 | 16579746 | 19014213 | 306611668 | 16.1254
5 | 2025-07-01 | 194498 | 5422118 | 6375010 | 106477313 | 16.7023
6 | 2025-08-01 | 219176 | 5426358 | 6383070 | 113746983 | 17.8201
7 | 2025-09-01 | 185991 | 5293529 | 6386243 | 97726166 | 15.3026
8 | 2nd Qtr | 599665 | 16142005 | 19144323 | 317950462 | 16.6081
9 | 2025-10-01 | 180982 | 5139825 | 6427405 | 93048478 | 14.4768
10 | 2025-11-01 | 158911 | 5121458 | 6447171 | 78742733 | 12.2135
11 | 2025-12-01 | 128571 | 5178989 | 6539654 | 67555728 | 10.3302
12 | 3rd Qtr | 468464 | 15440272 | 19414230 | 239346939 | 12.3284
13 | 2026-01-01 | 116989 | 5404662 | 6539736 | 69838347 | 10.6791
14 | 2026-02-01 | 64591 | 4264630 | 6559491 | 35681952 | 5.4397
15 | 2026-03-01 | 95935 | 4831354 | 6566641 | 52135403 | 7.9394
16 | 4th Qtr | 277515 | 14500646 | 19665868 | 157655702 | 8.0167
| Yearly Data | 1890014 | 62662669 | 77238634 | 1021564771 | 13.2261
SoP 011 : System Average Interruption Duration Index (SAIDI) for Overall category (To be submitted Quarterly and Annually)
Sr. No | Month | Number of Sustained Interruptions during the Reporting Period = Ai | Total Outage Duration | Restoration time for each Interruption Event = Ri | Number of Interrupted Customers for Sustained Interruption events during the Reporting Period = Ni | Total Customer Interruption Duration = Ri x Ni | Total Number of Customers Served for the Areas = Nt | Cumulative Customer Interruptions Duration = Σ (Ri x Ni) | SAIDI = Σ (Ri x Ni) / Nt
|  | Nos | Hr : Min | Hr : Min | Nos | Hr : Min | Nos | Hr : Min | Hr : Min
1 | 2 | 3 | 4 | 5 = 4 / 3 | 6 | 7 = 5 * 6 | 8 | 9 = Σ (5 x 6) | 10 = 9 / 8
1 | 2025-04-01 | 113414 | 5788.3079 | 0.051037 | 5334855 | 272274.8817 | 6324707 | 2840769.7363 | 0.44915
2 | 2025-05-01 | 223563 | 14044.5113 | 0.062821 | 5627901 | 353551.8798 | 6336420 | 6154612.3396 | 0.97131 | 26.33
3 | 2025-06-01 | 207393 | 12691.6313 | 0.061196 | 5616990 | 343737.5698 | 6353086 | 3540411.8346 | 0.55727
4 | 1st Qtr | 544370 | 32524.4504 | 0.059747 | 16579746 | 990589.3541 | 19014213 | 12535793.9104 | 0.65929
5 | 2025-07-01 | 194498 | 1928-06-21 09:21 | 1:17 | 5422118 | 289936.8609 | 6375010 | 3926177.3438 | 0.61587
6 | 2025-08-01 | 219176 | 1927-08-16 16:59 | 1:06 | 5426358 | 249825.6715 | 6383070 | 3942742.455 | 0.61769
7 | 2025-09-01 | 185991 | 1925-02-03 15:02 | 1:11 | 5293529 | 260893.291 | 6386243 | 3463193.6004 | 0.54229
8 | 2nd Qtr | 599665 | 1981-03-12 17:22 | 1:11 | 16142005 | 800655.8234 | 19144323 | 11332113.3992 | 0.59193
9 | 2025-10-01 | 180982 | 1920-11-18 05:34 | 1:01 | 5139825 | 216639.0902 | 6427405 | 3167998.2904 | 0.49289
10 | 2025-11-01 | 158911 | 1915-02-19 07:53 | 0:50 | 5121458 | 2387-11-23 18:41 | 6447171 | 2277082.9746 | 0.35319
11 | 2025-12-01 | 128571 | 1911-06-18 13:19 | 0:47 | 5178989 | 2361-10-28 13:20 | 6539654 | 1942334.4025 | 0.29701
12 | 3rd Qtr | 468464 | 1947-06-27 02:45 | 0:53 | 15440272 | 563520.4242 | 19414230 | 7387415.6675 | 0.38052
13 | 2026-01-01 | 116989 | 1911-05-03 22:38 | 0:51 | 5404662 | 2423-11-22 15:03 | 6539736 | 2082939.8896 | 0.31851
14 | 2026-02-01 | 64591 | 1905-08-14 10:02 | 0:46 | 4264630 | 2271-03-12 05:04 | 6559491 | 968752.3375 | 0.14769
15 | 2026-03-01 | 95935 | 1916-05-18 07:16 | 1:30 | 4831354 | 301323.3175 | 6566641 | 2181124.4658 | 0.33215
16 | 4th Qtr | 277515 | 1933-05-04 15:55 | 1:03 | 14500646 | 628250.1555 | 19665868 | 5232816.6929 | 0.26609
0 | Yearly Data | 1890014 | 2151-01-28 22:51 | 1:10 | 62662669 | 2983015.7572 | 77238634 | 36488139.67 | 0.47241
SoP 012 : Momentary Average Interruption Frequency Index (MAIFI) for Overall category (To be submitted Quarterly and Annually)
Sr. No | Month | Total Number of Momentary interruptions = Imi | Total Number of Consumers affected due to Momentary Interruption Events during the Reporting Period = Nmi | Number of Customer Momentary Interruptions = IMi * Nmi | Total Number of Customers Served for the Areas = Nt | Cumulative Momentary Customer Interruptions = Σ (Imi x Nmi) | MAIFI = Σ (IMi x Nmi)/ Nt
1 | 2 | 3 | 4 | 5 = 3 * 4 | 6 | 7 = Σ (3 x 4) | 8=7/6
1 | 2025-04-01 | 121587.5 | 5210907 | 633581154862.5 | 6324707 | 65859844.5 | 10.4131
2 | 2025-05-01 | 166588 | 5333248 | 888455117824 | 6336420 | 93528881 | 14.7605
3 | 2025-06-01 | 150845 | 5213384 | 786412909480 | 6353086 | 83758747 | 13.1839
4 | 1st Qtr | 439020.5 | 15757539 | 6.9179e+12 | 19014213 | 243147472.5 | 12.7877
5 | 2025-07-01 | 125332 | 5007294 | 627574171608 | 6375010 | 67438021 | 10.5785
6 | 2025-08-01 | 166013 | 5142839 | 853778130907 | 6383070 | 86981343 | 13.6269
7 | 2025-09-01 | 147368 | 5063521 | 746200962728 | 6386243 | 77818233 | 12.1853
8 | 2nd Qtr | 438713 | 15213654 | 6674427787302 | 19144323 | 232237597 | 12.1309
9 | 2025-10-01 | 158623 | 5019056 | 796137719888 | 6427405 | 82327960 | 12.8089
10 | 2025-11-01 | 163009 | 4978031 | 811463855279 | 6447171 | 79977046 | 12.405
11 | 2025-12-01 | 139518 | 5065557 | 706736381526 | 6539654 | 69663362 | 10.6525
12 | 3rd Qtr | 461150 | 15062644 | 6946138280600 | 19414230 | 231968368 | 11.9484
13 | 2026-01-01 | 116516 | 5161110 | 601351892760 | 6539736 | 62981440 | 9.6306
14 | 2026-02-01 | 65951 | 3787307 | 249776683957 | 6559491 | 33512112 | 5.109
15 | 2026-03-01 | 83613 | 4106365 | 343345496745 | 6566641 | 42675516 | 6.4988
16 | 4th Qtr | 266080 | 13054782 | 3473616394560 | 19665868 | 139169068 | 7.0767
0 | Yearly Data | 1604963.5 | 59088619 | 9.4835e+13 | 77238634 | 846522505.5 | 10.9598
SoP 013 – : Customer Average Interruption Duration Index (CAIDI) for Overall category (To be submitted Quarterly and Annually)
Sr. No | Month | Total Number of Sustained Interruptions during the Reporting Period = Σ Ai | Total Restoration time for Interruption Events = Σ Ri | Total Number of Interrupted Customers for Sustained Interruption events during the Reporting Period = Σni | CAIDI=Σ (Ri x Ni) / Σ (Ai x Ni) = SAIDI/ SAIFI
1 | 2 | 3 | 4 | 5 | 6 = (4 x 5) / (3 x 5)
1 | 2025-04-01 | 62932223 | 457718.7041 | 5334855 | 0.0072732
2 | 2025-05-01 | 128412304 | 1743514.9023 | 5627901 | 0.013577
3 | 2025-06-01 | 115267141 | 556623.6904 | 5616990 | 0.004829
4 | 1st Qtr | 306611668 | 2757857.2967 | 16579746 | 0.0089946
5 | 2025-07-01 | 106477313 | 941712.7383 | 5627901 | 0.0088443
6 | 2025-08-01 | 113746983 | 847660.3419 | 5616990 | 0.0074522
7 | 2025-09-01 | 97726166 | 763731.9185 | 16579746 | 0.007815
8 | 2nd Qtr | 317950462 | 2553104.9987 | 27824637 | 0.0080299
9 | 2025-10-01 | 93048478 | 749305.4308 | 5426358 | 0.0080528
10 | 2025-11-01 | 78742733 | 559901.9328 | 5293529 | 0.0071105
11 | 2025-12-01 | 67555728 | 371818.2539 | 16142005 | 0.0055039
12 | 3rd Qtr | 239346939 | 1681025.6176 | 26861892 | 0.0070234
13 | 2026-01-01 | 69838347 | 395440.7199 | 5121458 | 0.0056622
14 | 2026-02-01 | 35681952 | 153807.2561 | 5178989 | 0.0043105
15 | 2026-03-01 | 52135403 | 379175.304 | 15440272 | 0.0072729
16 | 4th Qtr | 157655702 | 928423.28 | 25740719 | 0.0058889
0 | Yearly Data | 1021564771 | 7920411.1931 | 97006994 | 0.0077532
Formulas:
Hr : Min = [Hr : Min]/[Nos]
Hr : Min = SUM(I28:[Hr : Min, row above])
Nos = ([Hr : Min]*[Hr : Min])/([Nos]*[Hr : Min])

## SoP 010-013 AG
Paschim Gujarat Vij Company Limited
Year 2025-26 (April-25 to March-2026)
SoP 010 - A : System Average Interruption Frequency Index (SAIFI) for AG. Dominant Category (To be submitted Quarterly and Annually)
Sr. No | Month | Number of Sustained Interruptions during the Reporting Period = Ai | Number of Interrupted Customers for Sustained Interruption events during the Reporting Period = Ni | Total number of Customers Served for the Areas = Nt | Total Number of Interrupted Customers for Sustained Interruption events during the Reporting Period = Σ (Ai x Ni) (Monthly SAIFI) | SAIFI = Σ (Ai x Ni) / Nt
1 | 2 | 3 | 4 | 5 | 6 = Σ (3 x 4) | 7 = 6 / 5
1 | 2025-04-01 | 90721 | 1369611 | 1435954 | 33451379 | 23.2956
2 | 2025-05-01 | 174907 | 1371549 | 1436692 | 64538716 | 44.9217
3 | 2025-06-01 | 162788 | 1377338 | 1438440 | 58662677 | 40.7822
4 | 1st Qtr | 428416 | 4118498 | 4311086 | 156652772 | 36.3372
5 | 2025-07-01 | 153978 | 1365450 | 1441769 | 55690395 | 38.6264
6 | 2025-08-01 | 178593 | 1366540 | 1442890 | 63723457 | 44.1638
7 | 2025-09-01 | 150029 | 1358056 | 1446918 | 53443253 | 36.9359
8 | 2nd Qtr | 482600 | 4090046 | 4331577 | 172857105 | 39.9063
9 | 2025-10-01 | 147895 | 1356456 | 1448036 | 51161475 | 35.3316
10 | 2025-11-01 | 132115 | 1371099 | 1450767 | 46029506 | 31.7277
11 | 2025-12-01 | 105717 | 1386346 | 1487071 | 38197279 | 25.6863
12 | 3rd Qtr | 385727 | 4113901 | 4385874 | 135388260 | 30.8692
13 | 2026-01-01 | 91706 | 1364040 | 1488547 | 33148708 | 22.2692
14 | 2026-02-01 | 51747 | 1198574 | 1495310 | 18388442 | 12.2974
15 | 2026-03-01 | 76301 | 1248335 | 1496757 | 26404920 | 17.6414
16 | 4th Qtr | 219754 | 3810949 | 4480614 | 77942070 | 17.3954
0 | Yearly Data | 1516497 | 16133394 | 17509151 | 542840207 | 31.0032
SoP 011 : System Average Interruption Duration Index (SAIDI) for AG. Dominant category (To be submitted Quarterly and Annually)
Sr. No | Month | Number of Sustained Interruptions during the Reporting Period = Ai | Total Outage Duration | Restoration time for each Interruption Event = Ri | Number of Interrupted Customers for Sustained Interruption events during the Reporting Period = Ni | Total Customer Interruption Duration = Ri x Ni | Total Number of Customers Served for the Areas = Nt | Cumulative Customer Interruptions Duration = Σ (Ri x Ni) | SAIDI = Σ (Ri x Ni) / Nt
|  | Nos | Hr : Min | Hr : Min | Nos | Hr : Min | Nos | Hr : Min | Hr : Min
1 | 2 | 3 | 4 | 5 = 4 / 3 | 6 | 7 = 5 * 6 | 8 | 9 = Σ (5 x 6) | 10 = 9 / 8
1 | 2025-04-01 | 90721 | 1912-11-15 06:11 | 1:15 | 1369611 | 2094-05-25 21:08 | 1435954 | 1392579.0433 | 0.96979
2 | 2025-05-01 | 174907 | 1933-08-11 13:19 | 1:41 | 1371549 | 2163-08-03 13:13 | 1436692 | 4072673.5833 | 1900-01-01 20:02
3 | 2025-06-01 | 162788 | 1929-11-09 02:32 | 1:36 | 1377338 | 2152-08-20 19:21 | 1438440 | 1392579.0433 | 0.96812
4 | 1st Qtr | 428416 | 1976-05-06 22:02 | 1:34 | 4118498 | 268085.733 | 4311086 | 6857831.67 | 1899-12-31 14:11
5 | 2025-07-01 | 153978 | 1925-03-06 23:27 | 1:26 | 1365450 | 2123-04-26 01:17 | 1441769 | 2641588.1004 | 1899-12-31 19:58
6 | 2025-08-01 | 178593 | 1924-09-06 07:26 | 1:13 | 1366540 | 2088-11-18 02:14 | 1442890 | 2740944.4408 | 1899-12-31 21:35
7 | 2025-09-01 | 150029 | 1922-04-29 15:12 | 1:18 | 1358056 | 2102-02-13 10:32 | 1446918 | 2320533.7721 | 1899-12-31 14:29
8 | 2nd Qtr | 482600 | 1972-03-11 22:05 | 1:19 | 4090046 | 224380.5859 | 4331577 | 7703066.3133 | 1899-12-31 18:41
9 | 2025-10-01 | 147895 | 1918-05-21 10:11 | 1:05 | 1356456 | 2068-08-26 08:45 | 1448036 | 2042476.8917 | 1899-12-31 09:51
10 | 2025-11-01 | 132115 | 1913-02-18 20:26 | 0:52 | 1371099 | 2036-05-07 19:53 | 1450767 | 1480536.9271 | 1899-12-31 00:30
11 | 2025-12-01 | 105717 | 1909-09-22 15:17 | 0:48 | 1386346 | 2027-08-02 11:49 | 1487071 | 1169224.0454 | 0.78626
12 | 3rd Qtr | 385727 | 1941-04-02 21:54 | 0:56 | 4113901 | 2332-08-07 16:28 | 4385874 | 4692237.8642 | 1899-12-31 01:41
13 | 2026-01-01 | 91706 | 1908-10-14 20:19 | 0:50 | 1364040 | 2030-10-02 07:22 | 1488547 | 1015905.4379 | 0.68248
14 | 2026-02-01 | 51747 | 1904-09-03 06:10 | 0:48 | 1198574 | 2008-04-28 23:32 | 1495310 | 541486.2221 | 0.36212
15 | 2026-03-01 | 76301 | 1914-06-03 20:03 | 1:39 | 1248335 | 2136-01-03 15:28 | 1496757 | 1400544.2263 | 0.93572
16 | 4th Qtr | 219754 | 1927-11-21 22:32 | 1:07 | 3810949 | 2375-02-04 22:21 | 4480614 | 2957935.8863 | 0.66016
0 | Yearly Data | 1516497 | 2117-09-11 16:34 | 1:16 | 16133394 | 823998.9363 | 17509151 | 22211071.7337 | 1899-12-31 06:27
SoP 012 : Momentary Average Interruption Frequency Index (MAIFI) for AG. Dominant category (To be submitted Quarterly and Annually)
Sr. No | Month | Total Number of Momentary interruptions = Imi | Total Number of Consumers affected due to Momentary Interruption Events during the Reporting Period = Nmi | Number of Customer Momentary Interruptions = IMi * Nmi | Total Number of Customers Served for the Areas = Nt | Cumulative Momentary Customer Interruptions = Σ (Imi x Nmi) | MAIFI = Σ (IMi x Nmi)/ Nt
1 | 2 | 3 | 4 | 5 = 3 * 4 | 6 | 7 = Σ (3 x 4) | 8=7/6
1 | 2025-04-01 | 102640.5 | 1354741 | 139051293610.5 | 1435954 | 38800207.5 | 27.0205
2 | 2025-05-01 | 137993 | 1324009 | 182703973937 | 1436692 | 52006867 | 36.199
3 | 2025-06-01 | 123828 | 1340822 | 166031306616 | 1438440 | 45127389 | 31.3725
4 | 1st Qtr | 364461.5 | 4019572 | 1464979240478 | 4311086 | 135934463.5 | 31.5314
5 | 2025-07-01 | 103123 | 1303627 | 134433927121 | 1441769 | 36684857 | 25.4443
6 | 2025-08-01 | 140180 | 1358259 | 190400746620 | 1442890 | 50692248 | 35.1324
7 | 2025-09-01 | 123870 | 1341331 | 166150670970 | 1446918 | 45436988 | 31.4026
8 | 2nd Qtr | 367173 | 4003217 | 1469873195541 | 4331577 | 132814093 | 30.6618
9 | 2025-10-01 | 133540 | 1336420 | 178465526800 | 1448036 | 46746864 | 32.2829
10 | 2025-11-01 | 141873 | 1347446 | 191166206358 | 1450767 | 50774481 | 34.9984
11 | 2025-12-01 | 122142 | 1376593 | 168139822206 | 1487071 | 45421020 | 30.5439
12 | 3rd Qtr | 397555 | 4060459 | 1614255777745 | 4385874 | 142942365 | 32.5915
13 | 2026-01-01 | 99059 | 1359775 | 134697951725 | 1488547 | 36198110 | 24.3177
14 | 2026-02-01 | 57261 | 1124382 | 64383237702 | 1495310 | 20307451 | 13.5808
15 | 2026-03-01 | 71122 | 1134034 | 80654766148 | 1496757 | 24393789 | 16.2978
16 | 4th Qtr | 227442 | 3618191 | 822928597422 | 4480614 | 80899350 | 18.0554
0 | Yearly Data | 1356631.5 | 15701439 | 2.1301e+13 | 17509151 | 492590271.5 | 28.1333
SoP 013 – : Customer Average Interruption Duration Index (CAIDI) for AG. Dominant category (To be submitted Quarterly and Annually)
Sr. No | Month | Total Number of Sustained Interruptions during the Reporting Period = Σ Ai | Total Restoration time for Interruption Events = Σ Ri | Total Number of Interrupted Customers for Sustained Interruption events during the Reporting Period = Σni | CAIDI=Σ (Ri x Ni) / Σ (Ai x Ni) = SAIDI/ SAIFI
1 | 2 | 3 | 4 | 5 | 6 = (4 x 5) / (3 x 5)
1 | 2025-04-01 | 33451379 | 351407.5111 | 1369611 | 0.010505
2 | 2025-05-01 | 64538716 | 1495744.6907 | 1371549 | 0.023176
3 | 2025-06-01 | 58662677 | 401182.066 | 1377338 | 0.0068388
4 | 1st Qtr | 156652772 | 2248334.2677 | 4118498 | 0.014352
5 | 2025-07-01 | 55690395 | 799174.1707 | 1365450 | 0.01435
6 | 2025-08-01 | 63723457 | 706991.9884 | 1366540 | 0.011095
7 | 2025-09-01 | 53443253 | 621386.3794 | 1358056 | 0.011627
8 | 2nd Qtr | 172857105 | 2127552.5385 | 4090046 | 0.012308
9 | 2025-10-01 | 51161475 | 525288.8008 | 1356456 | 0.010267
10 | 2025-11-01 | 46029506 | 433589.6138 | 1371099 | 0.0094198
11 | 2025-12-01 | 38197279 | 285429.4415 | 1386346 | 0.0074725
12 | 3rd Qtr | 135388260 | 1244307.8562 | 4113901 | 0.0091907
13 | 2026-01-01 | 33148708 | 257247.0006 | 1364040 | 0.0077604
14 | 2026-02-01 | 18388442 | 117353.4363 | 1198574 | 0.0063819
15 | 2026-03-01 | 26404920 | 310803.726 | 1248335 | 0.011771
16 | 4th Qtr | 77942070 | 685404.1629 | 3810949 | 0.0087938
0 | Yearly Data | 542840207 | 6305598.8253 | 16133394 | 0.011616
Formulas:
Hr : Min = [Nos]*[Hr : Min]
Hr : Min = [Hr : Min]/[Nos]
Nos = ([Hr : Min]*[Hr : Min])/([Nos]*[Hr : Min])

## SoP 010-013 JGY
Paschim Gujarat Vij Company Limited
Year 2025-26 (April-25 to March-2026)
SoP 010 - A : System Average Interruption Frequency Index (SAIFI) for JGY Category
Sr. No | Month | Number of Sustained Interruptions during the Reporting Period = Ai | Number of Interrupted Customers for Sustained Interruption events during the Reporting Period = Ni | Total number of Customers Served for the Areas = Nt | Total Number of Interrupted Customers for Sustained Interruption events during the Reporting Period = Σ (Ai x Ni) (Monthly SAIFI) | SAIFI = Σ (Ai x Ni) / Nt
1 | 2 | 3 | 4 | 5 | 6 = Σ (3 x 4) | 7 = 6 / 5
1 | 2025-04-01 | 17054 | 2011457 | 2207153 | 20020108 | 9.0706
2 | 2025-05-01 | 37727 | 2026725 | 2210133 | 45439828 | 20.5598
3 | 2025-06-01 | 33996 | 2039783 | 2219696 | 39960801 | 18.0028
4 | 1st Qtr | 88777 | 6077965 | 6636982 | 105420737 | 15.8838
5 | 2025-07-01 | 31481 | 2046313 | 2224092 | 36793806 | 16.5433
6 | 2025-08-01 | 32229 | 2018010 | 2227523 | 36828211 | 16.5333
7 | 2025-09-01 | 28514 | 1981202 | 2226396 | 32680962 | 14.6789
8 | 2nd Qtr | 92224 | 6045525 | 6678011 | 106302979 | 15.9184
9 | 2025-10-01 | 25691 | 1934751 | 2232847 | 29234976 | 13.0931
10 | 2025-11-01 | 20627 | 1979651 | 2239478 | 23365095 | 10.4333
11 | 2025-12-01 | 17389 | 2009720 | 2272906 | 20264100 | 8.9155
12 | 3rd Qtr | 63707 | 5924122 | 6745231 | 72864171 | 10.8023
13 | 2026-01-01 | 17888 | 1981868 | 2270287 | 21689768 | 9.5538
14 | 2026-02-01 | 9639 | 1651636 | 2277309 | 11718601 | 5.1458
15 | 2026-03-01 | 14812 | 1793476 | 2278573 | 17643932 | 7.7434
16 | 4th Qtr | 42339 | 5426980 | 6826169 | 51052301 | 7.4789
0 | Yearly Data | 287047 | 23474592 | 26886393 | 335640188 | 12.4836
SoP 011 : System Average Interruption Duration Index (SAIDI) for JGY category
Sr. No | Month | Number of Sustained Interruptions during the Reporting Period = Ai | Total Outage Duration | Restoration time for each Interruption Event = Ri | Number of Interrupted Customers for Sustained Interruption events during the Reporting Period = Ni | Total Customer Interruption Duration = Ri x Ni | Total Number of Customers Served for the Areas = Nt | Cumulative Customer Interruptions Duration = Σ (Ri x Ni) | SAIDI = Σ (Ri x Ni) / Nt
|  | Nos | Hr : Min | Hr : Min | Nos | Hr : Min | Nos | Hr : Min | Hr : Min
1 | 2 | 3 | 4 | 5 = 4 / 3 | 6 | 7 = 5 * 6 | 8 | 9 = Σ (5 x 6) | 10 = 9 / 8
1 | 2025-04-01 | 17054 | 1902-02-08 23:35 | 1:05 | 2011457 | 2148-12-18 14:51 | 2207153 | 1034725.4779 | 0.46881
2 | 2025-05-01 | 37727 | 1903-06-06 15:31 | 0:48 | 2026725 | 2084-05-19 21:57 | 2210133 | 1449625.7233 | 0.6559
3 | 2025-06-01 | 33996 | 1903-04-09 22:30 | 0:51 | 2039783 | 2096-06-16 01:25 | 2219696 | 1357500.3825 | 0.61157
4 | 1st Qtr | 88777 | 1908-10-24 13:37 | 0:52 | 6077965 | 220490.6002 | 6636982 | 3841851.5838 | 0.57886
5 | 2025-07-01 | 31481 | 1902-04-05 11:06 | 0:38 | 2046313 | 2047-01-29 07:45 | 2224092 | 940886.6488 | 0.42304
6 | 2025-08-01 | 32229 | 1902-02-25 04:35 | 0:35 | 2018010 | 2034-12-11 17:43 | 2227523 | 891689.7217 | 0.40031
7 | 2025-09-01 | 28514 | 1902-01-02 23:35 | 0:37 | 1981202 | 2039-08-16 09:38 | 2226396 | 838223.0646 | 0.37649
8 | 2nd Qtr | 92224 | 1906-06-04 15:16 | 0:37 | 6045525 | 2321-08-29 11:06 | 6678011 | 2670799.435 | 0.39994
9 | 2025-10-01 | 25691 | 1901-09-27 02:32 | 0:36 | 1934751 | 2031-02-25 04:25 | 2232847 | 764014.9792 | 0.34217
10 | 2025-11-01 | 20627 | 1901-04-24 13:01 | 0:34 | 1979651 | 2026-04-07 11:26 | 2239478 | 520626.1712 | 0.23248
11 | 2025-12-01 | 17389 | 1901-03-05 05:23 | 0:36 | 2009720 | 2036-02-17 20:50 | 2272906 | 516880.8829 | 0.22741
12 | 3rd Qtr | 63707 | 1904-03-25 20:57 | 0:35 | 5924122 | 2293-07-23 12:41 | 6745231 | 1801522.0333 | 0.26708
13 | 2026-01-01 | 17888 | 1901-06-09 16:28 | 0:42 | 1981868 | 2059-10-05 04:28 | 2270287 | 639038.4742 | 0.28148
14 | 2026-02-01 | 9639 | 1900-09-03 14:10 | 0:37 | 1651636 | 2016-02-24 09:01 | 2277309 | 296018.4221 | 0.12999
15 | 2026-03-01 | 14812 | 1901-04-12 12:32 | 0:46 | 1793476 | 2055-04-25 22:32 | 2278573 | 537574.3042 | 0.23593
16 | 4th Qtr | 42339 | 1903-05-26 19:10 | 0:42 | 5426980 | 2331-03-28 12:02 | 6826169 | 1472631.2004 | 0.21573
0 | Yearly Data | 287047 | 1922-11-17 20:59 | 0:42 | 23474592 | 675754.0925 | 26886393 | 9786804.2525 | 0.36401
SoP 012 : Momentary Average Interruption Frequency Index (MAIFI) for JGY category
Sr. No | Month | Total Number of Momentary interruptions = Imi | Total Number of Consumers affected due to Momentary Interruption Events during the Reporting Period = Nmi | Number of Customer Momentary Interruptions = IMi * Nmi | Total Number of Customers Served for the Areas = Nt | Cumulative Momentary Customer Interruptions = Σ (Imi x Nmi) | MAIFI = Σ (IMi x Nmi)/ Nt
1 | 2 | 3 | 4 | 5 = 3 * 4 | 6 | 7 = Σ (3 x 4) | 8=7/6
1 | 2025-04-01 | 14777 | 1995716 | 29490695332 | 2207153 | 19569883 | 8.8666
2 | 2025-05-01 | 23400 | 1995800 | 46701720000 | 2210133 | 30565855 | 13.8299
3 | 2025-06-01 | 21796 | 1942898 | 42347404808 | 2219696 | 28827064 | 12.9869
4 | 1st Qtr | 59973 | 5934414 | 355904610822 | 6636982 | 78962802 | 11.8974
5 | 2025-07-01 | 18014 | 1934752 | 34852622528 | 2224092 | 23031498 | 10.3555
6 | 2025-08-01 | 21144 | 1983057 | 41929757208 | 2227523 | 27537211 | 12.3623
7 | 2025-09-01 | 19211 | 1975309 | 37947661199 | 2226396 | 24823883 | 11.1498
8 | 2nd Qtr | 58369 | 5893118 | 343975404542 | 6678011 | 75392592 | 11.2897
9 | 2025-10-01 | 19811 | 1935899 | 38352095089 | 2232847 | 25361958 | 11.3586
10 | 2025-11-01 | 17169 | 1944332 | 33382236108 | 2239478 | 22200790 | 9.9134
11 | 2025-12-01 | 13851 | 1926266 | 26680710366 | 2272906 | 17671732 | 7.775
12 | 3rd Qtr | 50831 | 5806497 | 295150049007 | 6745231 | 65234480 | 9.6712
13 | 2026-01-01 | 13362 | 1962358 | 26221027596 | 2270287 | 17454163 | 7.6881
14 | 2026-02-01 | 6699 | 1424591 | 9543335109 | 2277309 | 8919483 | 3.9167
15 | 2026-03-01 | 9652 | 1557008 | 15028241216 | 2278573 | 12617287 | 5.5374
16 | 4th Qtr | 29713 | 4943957 | 146899794341 | 6826169 | 38990933 | 5.712
0 | Yearly Data | 198886 | 22577986 | 4490445323596 | 26886393 | 258580807 | 9.6175
SoP 013 – : Customer Average Interruption Duration Index (CAIDI) for JGY category
Sr. No | Month | Total Number of Sustained Interruptions during the Reporting Period = Σ Ai | Total Restoration time for Interruption Events = Σ Ri | Total Number of Interrupted Customers for Sustained Interruption events during the Reporting Period = Σni | CAIDI=Σ (Ri x Ni) / Σ (Ai x Ni) = SAIDI/ SAIFI
1 | 2 | 3 | 4 | 5 | 6 = (4 x 5) / (3 x 5)
1 | 2025-04-01 | 20020108 | 53878.4561 | 2011457 | 0.0026912
2 | 2025-05-01 | 45439828 | 166191.3534 | 2026725 | 0.0036574
3 | 2025-06-01 | 39960801 | 91861.7936 | 2039783 | 0.0022988
4 | 1st Qtr | 105420737 | 311931.6032 | 6077965 | 0.0029589
5 | 2025-07-01 | 36793806 | 93335.3443 | 2046313 | 0.0025367
6 | 2025-08-01 | 36828211 | 94449.5828 | 2018010 | 0.0025646
7 | 2025-09-01 | 32680962 | 92337.8461 | 1981202 | 0.0028254
8 | 2nd Qtr | 106302979 | 280122.7732 | 6045525 | 0.0026351
9 | 2025-10-01 | 29234976 | 104653.1841 | 1934751 | 0.0035797
10 | 2025-11-01 | 23365095 | 57336.3835 | 1979651 | 0.0024539
11 | 2025-12-01 | 20264100 | 51949.7106 | 2009720 | 0.0025636
12 | 3rd Qtr | 72864171 | 213939.2781 | 5924122 | 0.0029361
13 | 2026-01-01 | 21689768 | 51469.7433 | 1981868 | 0.002373
14 | 2026-02-01 | 11718601 | 22799.0829 | 1651636 | 0.0019455
15 | 2026-03-01 | 17643932 | 38907.9404 | 1793476 | 0.0022052
16 | 4th Qtr | 51052301 | 113176.7666 | 5426980 | 0.0022169
0 | Yearly Data | 335640188 | 919170.4211 | 23474592 | 0.0027386
Formulas:
Hr : Min = [Nos]*[Hr : Min]
Hr : Min = [Hr : Min]/[Nos]
Nos = ([Hr : Min]*[Hr : Min])/([Nos]*[Hr : Min])

## SoP 010-013 other than AG & JGY
Paschim Gujarat Vij Company Limited
Year 2025-26 (April-25 to March-2026)
SoP 010 - A : System Average Interruption Frequency Index (SAIFI) for other than Ag & JGY Category
Sr. No | Month | Number of Sustained Interruptions during the Reporting Period = Ai | Number of Interrupted Customers for Sustained Interruption events during the Reporting Period = Ni | Total number of Customers Served for the Areas = Nt | Total Number of Interrupted Customers for Sustained Interruption events during the Reporting Period = Σ (Ai x Ni) (Monthly SAIFI) | SAIFI = Σ (Ai x Ni) / Nt
1 | 2 | 3 | 4 | 5 | 6 = Σ (3 x 4) | 7 = 6 / 5
1 | 2025-04-01 | 5639 | 1953787 | 2681600 | 9460736 | 3.528
2 | 2025-05-01 | 10929 | 2229627 | 2689595 | 18433760 | 6.8537
3 | 2025-06-01 | 10609 | 2199869 | 2694950 | 16643663 | 6.1759
4 | 1st Qtr | 27177 | 6383283 | 8066145 | 44538159 | 5.5216
5 | 2025-07-01 | 9039 | 2010355 | 2709149 | 13993112 | 5.1651
6 | 2025-08-01 | 8354 | 2041808 | 2712657 | 13195315 | 4.8644
7 | 2025-09-01 | 7448 | 1954271 | 2712929 | 11601951 | 4.2765
8 | 2nd Qtr | 24841 | 6006434 | 8134735 | 38790378 | 4.7685
9 | 2025-10-01 | 7396 | 1848618 | 2746522 | 12652027 | 4.6066
10 | 2025-11-01 | 6169 | 1770708 | 2756926 | 9348132 | 3.3908
11 | 2025-12-01 | 5465 | 1782923 | 2779677 | 9094349 | 3.2717
12 | 3rd Qtr | 19030 | 5402249 | 8283125 | 31094508 | 3.754
13 | 2026-01-01 | 7395 | 2058754 | 2780902 | 14999871 | 5.3939
14 | 2026-02-01 | 3205 | 1414420 | 2786872 | 5574909 | 2.0004
15 | 2026-03-01 | 4822 | 1789543 | 2791311 | 8086551 | 2.897
16 | 4th Qtr | 15422 | 5262717 | 8359085 | 28661331 | 3.4288
0 | Yearly Data | 86470 | 23054683 | 32843090 | 143084376 | 4.3566
SoP 011 : System Average Interruption Duration Index (SAIDI) for other than Ag & JGY category
Sr. No | Month | Number of Sustained Interruptions during the Reporting Period = Ai | Total Outage Duration | Restoration time for each Interruption Event = Ri | Number of Interrupted Customers for Sustained Interruption events during the Reporting Period = Ni | Total Customer Interruption Duration = Ri x Ni | Total Number of Customers Served for the Areas = Nt | Cumulative Customer Interruptions Duration = Σ (Ri x Ni) | SAIDI = Σ (Ri x Ni) / Nt
|  | Nos | Hr : Min | Hr : Min | Nos | Hr : Min | Nos | Hr : Min | Hr : Min
1 | 2 | 3 | 4 | 5 = 4 / 3 | 6 | 7 = 5 * 6 | 8 | 9 = Σ (5 x 6) | 10 = 9 / 8
1 | 2025-04-01 | 5639 | 1900-11-09 01:37 | 1:20 | 1953787 | 2197-12-04 04:46 | 2681600 | 413465.215 | 0.15419
2 | 2025-05-01 | 10929 | 1901-05-27 07:26 | 1:08 | 2229627 | 2186-09-16 10:53 | 2689595 | 632313.0329 | 0.2351
3 | 2025-06-01 | 10609 | 1901-08-11 14:07 | 1:20 | 2199869 | 2234-09-21 05:09 | 2694950 | 790332.4087 | 0.29326
4 | 1st Qtr | 27177 | 1903-11-16 23:10 | 1:15 | 6383283 | 332814.0927 | 8066145 | 1836110.6567 | 0.22763
5 | 2025-07-01 | 9039 | 1901-01-09 22:48 | 1:00 | 2010355 | 2128-12-03 15:58 | 2709149 | 343702.5946 | 0.12687
6 | 2025-08-01 | 8354 | 1900-10-13 04:58 | 0:50 | 2041808 | 2092-03-08 12:27 | 2712657 | 310108.2925 | 0.11432
7 | 2025-09-01 | 7448 | 1900-10-03 00:15 | 0:54 | 1954271 | 2098-12-30 09:38 | 2712929 | 304436.7637 | 0.11222
8 | 2nd Qtr | 24841 | 1902-07-28 04:01 | 0:55 | 6006434 | 226495.5864 | 8134735 | 958247.6508 | 0.1178
9 | 2025-10-01 | 7396 | 1900-10-01 16:50 | 0:54 | 1848618 | 2088-08-31 04:15 | 2746522 | 361506.4196 | 0.13162
10 | 2025-11-01 | 6169 | 1900-09-05 22:25 | 0:58 | 1770708 | 2096-05-29 09:52 | 2756926 | 275919.8763 | 0.10008
11 | 2025-12-01 | 5465 | 1900-07-21 16:38 | 0:54 | 1782923 | 2081-12-08 17:03 | 2779677 | 256229.4742 | 0.09218
12 | 3rd Qtr | 19030 | 1901-12-29 07:54 | 0:55 | 5402249 | 207104.2988 | 8283125 | 893655.77 | 0.10789
13 | 2026-01-01 | 7395 | 1901-02-07 09:51 | 1:19 | 2058754 | 2208-04-01 02:16 | 2780902 | 427995.9775 | 0.15391
14 | 2026-02-01 | 3205 | 1900-04-06 13:42 | 0:44 | 1414420 | 2017-11-20 15:18 | 2786872 | 2259-05-04 16:38 | 0.047095
15 | 2026-03-01 | 4822 | 1900-09-01 22:40 | 1:13 | 1789543 | 2149-11-24 01:47 | 2791311 | 243005.9354 | 0.087058
16 | 4th Qtr | 15422 | 1902-01-16 22:13 | 1:10 | 5262717 | 246921.806 | 8359085 | 802249.6063 | 0.095973
0 | Yearly Data | 86470 | 1910-06-30 09:18 | 1:04 | 23054683 | 1013335.7838 | 32843090 | 4490263.6837 | 0.13672
SoP 012 : Momentary Average Interruption Frequency Index (MAIFI) for other than Ag & JGY category
Sr. No | Month | Total Number of Momentary interruptions = Imi | Total Number of Consumers affected due to Momentary Interruption Events during the Reporting Period = Nmi | Number of Customer Momentary Interruptions = IMi * Nmi | Total Number of Customers Served for the Areas = Nt | Cumulative Momentary Customer Interruptions = Σ (Imi x Nmi) | MAIFI = Σ (IMi x Nmi)/ Nt
1 | 2 | 3 | 4 | 5 = 3 * 4 | 6 | 7 = Σ (3 x 4) | 8=7/6
1 | 2025-04-01 | 4170 | 1860450 | 7758076500 | 2681600 | 7489754 | 2.793
2 | 2025-05-01 | 5195 | 2013439 | 10459815605 | 2689595 | 10956159 | 4.0735
3 | 2025-06-01 | 5221 | 1929664 | 10074775744 | 2694950 | 9804294 | 3.638
4 | 1st Qtr | 14586 | 5803553 | 84650624058 | 8066145 | 28250207 | 3.5023
5 | 2025-07-01 | 4195 | 1768915 | 7420598425 | 2709149 | 7721666 | 2.8502
6 | 2025-08-01 | 4689 | 1801523 | 8447341347 | 2712657 | 8751884 | 3.2263
7 | 2025-09-01 | 4287 | 1746881 | 7488878847 | 2712929 | 7557362 | 2.7857
8 | 2nd Qtr | 13171 | 5317319 | 70034408549 | 8134735 | 24030912 | 2.9541
9 | 2025-10-01 | 5272 | 1746737 | 9208797464 | 2746522 | 10219138 | 3.7208
10 | 2025-11-01 | 3967 | 1686253 | 6689365651 | 2756926 | 7001775 | 2.5397
11 | 2025-12-01 | 3525 | 1762698 | 6213510450 | 2779677 | 6570610 | 2.3638
12 | 3rd Qtr | 12764 | 5195688 | 66317761632 | 8283125 | 23791523 | 2.8723
13 | 2026-01-01 | 4095 | 1838977 | 7530610815 | 2780902 | 9329167 | 3.3547
14 | 2026-02-01 | 1991 | 1238334 | 2465522994 | 2786872 | 4285178 | 1.5376
15 | 2026-03-01 | 2839 | 1415323 | 4018101997 | 2791311 | 5664440 | 2.0293
16 | 4th Qtr | 8925 | 4492634 | 40096758450 | 8359085 | 19278785 | 2.3063
0 | Yearly Data | 49446 | 20809194 | 1028931406524 | 32843090 | 95351427 | 2.9032
SoP 013 – : Customer Average Interruption Duration Index (CAIDI) for other than AG & JGY category
Sr. No | Month | Total Number of Sustained Interruptions during the Reporting Period = Σ Ai | Total Restoration time for Interruption Events = Σ Ri | Total Number of Interrupted Customers for Sustained Interruption events during the Reporting Period = Σni | CAIDI=Σ (Ri x Ni) / Σ (Ai x Ni) = SAIDI/ SAIFI
1 | 2 | 3 | 4 | 5 | 6 = (4 x 5) / (3 x 5)
1 | 2025-04-01 | 9460736 | 52432.7369 | 1953787 | 0.0055421
2 | 2025-05-01 | 18433760 | 81578.8582 | 2229627 | 0.0044255
3 | 2025-06-01 | 16643663 | 63579.8308 | 2199869 | 0.0038201
4 | 1st Qtr | 44538159 | 197591.4259 | 6383283 | 0.0044365
5 | 2025-07-01 | 13993112 | 49203.2233 | 2010355 | 0.0035162
6 | 2025-08-01 | 13195315 | 46218.7707 | 2041808 | 0.0035027
7 | 2025-09-01 | 11601951 | 50007.693 | 1954271 | 0.0043103
8 | 2nd Qtr | 38790378 | 145429.687 | 6006434 | 0.0037491
9 | 2025-10-01 | 12652027 | 119363.4459 | 1848618 | 0.0094343
10 | 2025-11-01 | 9348132 | 68975.9355 | 1770708 | 0.0073786
11 | 2025-12-01 | 9094349 | 34439.1018 | 1782923 | 0.0037869
12 | 3rd Qtr | 31094508 | 222778.4833 | 5402249 | 0.0071646
13 | 2026-01-01 | 14999871 | 86723.976 | 2058754 | 0.0057816
14 | 2026-02-01 | 5574909 | 13654.7369 | 1414420 | 0.0024493
15 | 2026-03-01 | 8086551 | 29463.6376 | 1789543 | 0.0036435
16 | 4th Qtr | 28661331 | 129842.3505 | 5262717 | 0.0045302
0 | Yearly Data | 143084376 | 695641.9467 | 23054683 | 0.0048618
Formulas:
Hr : Min = [Nos]*[Hr : Min]
Hr : Min = [Hr : Min]/[Nos]
Nos = ([Hr : Min]*[Hr : Min])/([Nos]*[Hr : Min])

## Sheet1 (hidden)
add | rep |  |  | pen
5532 | 5283 |  |  | 1399
1829 | 1829 | 1829 | 1829 | 0
8542 | 8855 |  |  | 6434
1324 | 1083 | 1324 | 1083 | 744
7369 | 10688 |  |  | 7564
569 | 598 | 569 | 598 | 222
8950 | 16365 |  |  | 12125
530 | 1110 | 530 | 1110 | 709
4115 | 4205 |  |  | 8514
232 | 232 | 232 | 232 | 0
13485 | 8807 |  |  | 12511
887 | 868 | 887 | 868 | 24
13152 | 18190 |  |  | 24335
378 | 348 | 378 | 348 | 85
8197 | 7971 |  |  | 7458
1179 | 1193 | 1179 | 1193 | 24
3737 | 5953 |  |  | 7568
386 | 892 | 386 | 892 | 1104
73079 | 86317 |  |  | 87908
7314 | 8153 | 7314 | 8153 | 2912

## Accident (2) (hidden)
PASCHIM GUJARAT VIJ COMPANY LIMITED REGD. & CORPORATE OFFICE, RAJKOT
ACCIDENT DETAILS | [9 empty] | 2010-03-05
No | CIRCLE | DIVISION | Nos. of accidents(victim) during Month | [7 empty] | Cummulative | [8 empty] | Previous Month |  |  |  | 2006-04-01 |  |  | 2006-05-01 |  |  | 2006-06-01 |  |  | 2006-07-01 |  |  | 2006-08-01 |  |  | 2006-09-01 |  |  | 2006-10-01 |  |  | 2006-11-01 |  |  | 2006-12-01 |  |  | 2007-01-01 |  |  | 2007-02-01 |  |  | 2007-03-01 |  |  | Cumulative since mayil-05
| 1 | 3 | Department |  | Outsider |  |  | Total |  |  | Department |  | Outsider |  |  | Total |  |  |  | FH | FA | NFH |  | Total |  |  | Total |  |  | Total |  |  | Total |  |  | Total |  |  | Total |  |  | Total |  |  | Total |  |  | Total |  |  | Total |  |  | Total |  |  | Total |  |  | Total
| 1 | 3 | FH | NFH | FH | FA | NFH | FH | FA | NFH | FH | NFH | FH | FA | NFH | FH | FA | NFH |  |  |  |  | 18 | FH | FA | NFH | FH | FA | NFH | FH | FA | NFH | FH | FA | NFH | FH | FA | NFH | FH | FA | NFH | FH | FA | NFH | FH | FA | NFH | FH | FA | NFH | FH | FA | NFH | FH | FA | NFH | FH | FA | NFH | FH | FA | NFH
1 | RJC | RAJKOT C-1 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 1 | 2 | 7 | 4 | 2 | 7 | 5 | 14 | 2 | 7 | 4 |  | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 5 | 0 | 0 | 2 | 1 | 0 | 0 | 0 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 1
2 |  | RAJKOT C-2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 7 | 1 | 1 | 8 | 10 | 1 | 1 | 8 |  | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 3 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 1 | 3
3 |  | RAJKOT C-3 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 1 | 5 | 7 | 11 | 5 | 7 | 12 | 24 | 5 | 7 | 11 |  | 0 | 0 | 0 | 1 | 0 | 1 | 0 | 2 | 1 | 2 | 3 | 2 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 2 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 1 | 2 | 2 | 6
1 |  | CIRCLE-TOTAL | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 3 | 8 | 15 | 22 | 8 | 15 | 25 | 48 | 8 | 15 | 23 |  | 0 | 0 | 2 | 1 | 0 | 2 | 1 | 7 | 4 | 2 | 5 | 3 | 0 | 0 | 1 | 1 | 0 | 3 | 0 | 2 | 1 | 0 | 0 | 0 | 0 | 1 | 3 | 3 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 3 | 3 | 10 | 16
1 | RJR | GONDAL | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 1 | 0 | 7 | 8 | 5 | 8 | 8 | 5 | 21 | 8 | 8 | 4 |  | 1 | 0 | 0 | 0 | 0 | 1 | 0 | 3 | 1 | 1 | 3 | 0 | 1 | 1 | 0 | 1 | 0 | 1 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 2 | 0 | 0 | 0 | 0 | 1 | 4 | 1 | 2
2 |  | DHORAJI | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 5 | 11 | 23 | 6 | 12 | 23 | 11 | 46 | 12 | 23 | 11 |  | 2 | 0 | 0 | 0 | 1 | 1 | 3 | 6 | 2 | 1 | 8 | 2 | 2 | 0 | 2 | 1 | 6 | 2 | 1 | 0 | 2 | 0 | 2 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 3 | 2 | 2
3 |  | JASDAN | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 | 6 | 2 | 2 | 6 | 3 | 11 | 2 | 6 | 3 |  | 0 | 1 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 4 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1
4 |  | RAJKOT RURAL | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3 | 6 | 3 | 3 | 6 | 4 | 13 | 3 | 6 | 4 |  | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 3 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2 |  | CIRCLE-TOTAL | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 2 | 7 | 23 | 43 | 16 | 25 | 43 | 23 | 91 | 25 | 43 | 22 |  | 4 | 1 | 2 | 0 | 1 | 2 | 4 | 10 | 3 | 3 | 18 | 3 | 3 | 3 | 3 | 3 | 7 | 4 | 1 | 0 | 4 | 1 | 3 | 0 | 1 | 0 | 0 | 1 | 0 | 1 | 4 | 0 | 0 | 0 | 0 | 1 | 8 | 3 | 6 | 17
3 | MRB | MORBI | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 8 | 8 | 4 | 8 | 8 | 6 | 22 | 9 | 10 | 6 |  | 0 | 2 | 0 | 0 | 0 | 1 | 1 | 1 | 0 | 4 | 3 | 1 | 0 | 1 | 0 | 1 | 1 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 2 | 0 | 3
4 |  | HALVAD | 0 | 1 | 3 | 4 | 1 | 3 | 4 | 2 | 0 | 2 | 5 | 12 | 1 | 5 | 12 | 3 | 20 | 1 | 6 | 1 |  | 1 | 1 | 0 | 1 | 0 | 0 | 1 | 3 | 0 | 0 | 5 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 | 1 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 0 | 2 | 2 | 3
4 |  | CIRCLE-TOTAL | 0 | 1 | 3 | 4 | 1 | 3 | 4 | 2 | 0 | 4 | 13 | 20 | 5 | 13 | 20 | 9 | 42 | 10 | 16 | 7 |  | 1 | 3 | 0 | 1 | 0 | 1 | 2 | 4 | 0 | 4 | 8 | 1 | 0 | 2 | 0 | 1 | 1 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 1 | 2 | 1 | 0 | 1 | 0 | 0 | 2 | 1 | 1 | 1 | 4 | 2 | 6 | 12
1 | PBR | PBR CITY | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 2 | 6 | 12 | 1 | 6 | 12 | 3 | 21 | 5 | 12 | 3 |  | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 2 | 0 | 0 | 6 | 2 | 2 | 3 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 2 | 0 | 0
2 |  | PBR RURAL | 0 | 0 | 3 | 0 | 3 | 3 | 0 | 3 | 0 | 2 | 8 | 15 | 5 | 8 | 15 | 7 | 30 | 5 | 15 | 4 |  | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 4 | 1 | 0 | 5 | 0 | 1 | 3 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 1 | 2 | 0 | 1 | 1 | 0 | 1 | 0 | 1 | 0 | 0 | 0 | 3 | 0 | 3 | 6 | 3 | 5
3 |  | KESHOD-1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 6 | 0 | 2 | 6 | 0 | 8 | 2 | 6 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 4 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0
4 |  | KESHOD-2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 17 | 3 | 8 | 17 | 3 | 28 | 8 | 17 | 3 |  | 0 | 0 | 0 | 1 | 0 | 0 | 3 | 3 | 0 | 1 | 11 | 3 | 0 | 2 | 0 | 3 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0
4 |  | CIRCLE-TOTAL | 0 | 0 | 4 | 0 | 3 | 4 | 0 | 3 | 0 | 4 | 24 | 50 | 9 | 24 | 50 | 13 | 87 | 20 | 50 | 10 |  | 0 | 0 | 0 | 2 | 0 | 1 | 4 | 10 | 1 | 2 | 26 | 5 | 3 | 9 | 0 | 4 | 1 | 1 | 0 | 1 | 1 | 1 | 2 | 0 | 1 | 1 | 0 | 2 | 0 | 1 | 1 | 0 | 0 | 4 | 0 | 3 | 9 | 4 | 5 | 18
1 | JMN | JMN CITY-1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 5 | 5 | 2 | 5 | 5 | 3 | 13 | 4 | 5 | 3 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 0 | 1 | 1 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 3 | 2 | 1
2 |  | JMN CITY-2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 12 | 6 | 2 | 12 | 6 | 20 | 2 | 12 | 6 |  | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 | 1 | 0 | 4 | 1 | 0 | 1 | 2 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 3 | 0 | 0 | 2 | 1 | 0 | 0 | 0 | 1 | 5 | 2
3 |  | JAMNAGAR | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 2 | 14 | 6 | 2 | 14 | 7 | 23 | 2 | 14 | 6 |  | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 4 | 1 | 1 | 3 | 0 | 0 | 4 | 4 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 2
4 |  | KHAMBHALIA | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 2 | 10 | 18 | 10 | 10 | 18 | 12 | 40 | 10 | 17 | 12 |  | 1 | 0 | 0 | 1 | 0 | 0 | 2 | 4 | 4 | 1 | 7 | 2 | 1 | 4 | 1 | 0 | 2 | 2 | 1 | 0 | 3 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 4 | 1 | 3
|  | JAMJODHPUR | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0
5 |  | CIRCLE-TOTAL | 0 | 1 | 3 | 1 | 0 | 3 | 1 | 1 | 0 | 4 | 21 | 49 | 24 | 21 | 49 | 28 | 98 | 18 | 48 | 27 |  | 1 | 0 | 0 | 1 | 2 | 0 | 3 | 11 | 7 | 3 | 15 | 3 | 2 | 10 | 7 | 0 | 2 | 3 | 3 | 2 | 4 | 2 | 0 | 0 | 0 | 1 | 1 | 1 | 3 | 1 | 2 | 2 | 1 | 1 | 1 | 1 | 9 | 9 | 8 | 26
1 | BHJ | BHUJ | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 6 | 5 | 4 | 7 | 5 | 4 | 13 | 22 | 4 | 4 | 13 |  | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 2 | 2 | 1 | 2 | 0 | 0 | 0 | 2 | 2 | 0 | 1 | 0 | 0 | 4 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 2 | 0 | 6
2 |  | MANDVI | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 2 | 2 | 13 | 5 | 2 | 13 | 7 | 22 | 2 | 13 | 6 |  | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 7 | 1 | 0 | 1 | 1 | 0 | 4 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 4
3 |  | ANJAR | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 5 | 3 | 4 | 5 | 3 | 4 | 12 | 4 | 3 | 4 |  | 0 | 0 | 1 | 1 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 3 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 3 | 1 | 0
4 |  | GANDHIDHAM | 0 | 0 | 3 | 0 | 0 | 3 | 0 | 0 | 0 | 1 | 15 | 2 | 2 | 15 | 2 | 3 | 20 | 12 | 2 | 3 |  | 1 | 0 | 0 | 1 | 0 | 1 | 2 | 1 | 0 | 4 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 2 | 0 | 0 | 3 | 0 | 0 | 7 | 0 | 1
6 |  | CIRCLE-TOTAL | 0 | 0 | 5 | 0 | 1 | 5 | 0 | 1 | 0 | 9 | 27 | 22 | 18 | 27 | 22 | 27 | 76 | 22 | 22 | 26 |  | 1 | 0 | 3 | 2 | 0 | 2 | 4 | 11 | 3 | 5 | 4 | 5 | 0 | 4 | 2 | 2 | 1 | 1 | 2 | 0 | 6 | 0 | 0 | 0 | 0 | 1 | 3 | 4 | 1 | 1 | 2 | 0 | 0 | 5 | 0 | 1 | 13 | 2 | 11 | 26
1 | JND | JUNAGADH CITY | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 3 | 2 | 1 | 3 | 3 | 7 | 1 | 3 | 3 |  | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 2
2 |  | JUNAGADH DN-1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 5 | 5 | 4 | 12 | 5 | 4 | 17 | 26 | 5 | 4 | 16 |  | 0 | 0 | 3 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 3 | 4 | 1 | 0 | 2 | 1 | 0 | 2 | 1 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 1 | 0 | 4
3 |  | JUNAGADH DN-2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 9 | 3 | 1 | 9 | 3 | 13 | 1 | 9 | 3 |  | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 7 | 1 | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
4 |  | VERAVAL | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 8 | 27 | 5 | 8 | 27 | 7 | 42 | 8 | 27 | 7 |  | 0 | 0 | 0 | 0 | 0 | 2 | 2 | 6 | 0 | 1 | 7 | 0 | 0 | 8 | 5 | 0 | 0 | 0 | 1 | 3 | 0 | 0 | 1 | 0 | 1 | 2 | 0 | 1 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 5 | 6 | 0
7 |  | CIRCLE-TOTAL | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 8 | 15 | 43 | 22 | 15 | 43 | 30 | 88 | 15 | 43 | 29 |  | 0 | 1 | 3 | 0 | 0 | 4 | 3 | 8 | 1 | 3 | 18 | 5 | 1 | 10 | 7 | 1 | 0 | 3 | 3 | 3 | 1 | 0 | 1 | 3 | 1 | 2 | 0 | 1 | 0 | 1 | 2 | 0 | 1 | 0 | 0 | 1 | 7 | 6 | 7 | 20
1 | BVN | BVN CITY-1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 2 | 0 | 0 | 2 | 0 | 3 | 5 | 2 | 0 | 3 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 2
2 |  | BVN CITY-2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2 | 1 | 1 | 2 | 2 | 5 | 1 | 2 | 2 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1
3 |  | Bhavnagar | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 12 | 15 | 2 | 13 | 15 | 2 | 30 | 13 | 15 | 2 |  | 0 | 0 | 0 | 1 | 1 | 0 | 1 | 5 | 2 | 2 | 4 | 0 | 2 | 4 | 0 | 2 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 5 | 1 | 0
4 |  | MAHUVA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 2 | 6 | 2 | 2 | 6 | 5 | 13 | 2 | 6 | 5 |  | 0 | 1 | 2 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 2 | 1 | 1 | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 2
5 |  | PALITANA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 6 | 10 | 0 | 6 | 10 | 2 | 18 | 6 | 10 | 2 |  | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 4 | 0 | 1 | 2 | 0 | 0 | 1 | 0 | 0 | 3 | 1 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 1
8 |  | CIRCLE-TOTAL | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 9 | 23 | 33 | 5 | 24 | 33 | 14 | 71 | 24 | 33 | 14 |  | 1 | 1 | 2 | 1 | 1 | 0 | 2 | 10 | 3 | 4 | 10 | 1 | 4 | 6 | 0 | 2 | 4 | 2 | 1 | 1 | 1 | 2 | 0 | 0 | 1 | 0 | 1 | 5 | 0 | 2 | 1 | 0 | 2 | 0 | 0 | 0 | 10 | 1 | 6 | 17
1 | BTD | BOTAD | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 3 | 0 | 3 | 3 | 0 | 6 | 3 | 3 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 | 0 | 0 | 1 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0
2 |  | GADHDA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3 | 3 | 1 | 3 | 3 | 7 | 1 | 3 | 3 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 2 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0
9 |  | CIRCLE-TOTAL | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 6 | 3 | 4 | 6 | 3 | 13 | 4 | 6 | 3 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 1 | 4 | 0 | 0 | 2 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 2
1 | AMR | AMRELI -1 | 0 | 1 | 1 | 0 | 2 | 1 | 0 | 3 | 0 | 4 | 5 | 8 | 11 | 5 | 8 | 15 | 28 | 4 | 8 | 12 |  | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 2 | 0 | 1 | 3 | 2 | 1 | 3 | 1 | 1 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 | 0 | 0 | 1 | 0 | 3 | 2 | 0 | 6
2 |  | SAVAR KUNDLA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 9 | 6 | 6 | 9 | 6 | 7 | 22 | 9 | 6 | 7 |  | 0 | 0 | 0 | 0 | 0 | 1 | 3 | 1 | 0 | 3 | 2 | 4 | 0 | 2 | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 2 | 1 | 2
3 |  | UNA | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 5 | 20 | 0 | 6 | 20 | 1 | 27 | 6 | 20 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 3 | 0 | 2 | 10 | 0 | 0 | 4 | 0 | 1 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 | 2 | 1
4 |  | AMRELI-2 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 8 | 15 | 1 | 8 | 15 | 1 | 24 | 7 | 15 | 1 |  | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 2 | 0 | 2 | 7 | 0 | 0 | 4 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 3 | 1 | 1
10 |  | CIRCLE-TOTAL | 0 | 2 | 2 | 0 | 2 | 2 | 0 | 4 | 1 | 6 | 27 | 49 | 18 | 28 | 49 | 24 | 101 | 26 | 49 | 20 |  | 0 | 0 | 0 | 1 | 0 | 6 | 6 | 8 | 0 | 8 | 22 | 6 | 1 | 13 | 1 | 3 | 2 | 1 | 1 | 1 | 2 | 0 | 1 | 0 | 1 | 1 | 1 | 3 | 1 | 2 | 2 | 0 | 1 | 2 | 0 | 4 | 9 | 4 | 10 | 23
1 | SNR | S'NAGAR-1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 2 | 9 | 3 | 2 | 9 | 5 | 16 | 2 | 9 | 6 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 5 | 2 | 0 | 3 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 1 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 2
2 |  | S'NAGAR-2 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 5 | 8 | 4 | 5 | 8 | 5 | 18 | 3 | 11 | 5 |  | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2 | 2 | 5 | 1 | 0 | 2 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 2 | 0 | 1
3 |  | DHANGADHARA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 5 | 6 | 10 | 6 | 6 | 10 | 22 | 7 | 6 | 9 |  | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 0 | 9 | 2 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 1 | 9
0 |  | CIRCLE-TOTAL | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 3 | 12 | 23 | 17 | 13 | 23 | 20 | 56 | 12 | 26 | 20 |  | 1 | 0 | 0 | 1 | 1 | 0 | 1 | 6 | 4 | 3 | 12 | 1 | 0 | 2 | 1 | 0 | 1 | 2 | 1 | 1 | 0 | 1 | 0 | 11 | 3 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 7 | 1 | 12 | 20
|  | PGVCL | 0 | 5 | 18 | 5 | 10 | 18 | 5 | 15 | 5 | 57 | 197 | 353 | 159 | 202 | 353 | 216 | 771 | 184 | 351 | 201 | 0 | 9 | 6 | 12 | 10 | 5 | 18 | 30 | 85 | 29 | 38 | 142 | 33 | 14 | 61 | 22 | 18 | 19 | 21 | 13 | 11 | 20 | 8 | 7 | 14 | 9 | 8 | 12 | 23 | 5 | 12 | 14 | 2 | 9 | 14 | 2 | 14 | 81 | 35 | 81 | 197 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | Rajkot City |  | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 3 | 8 | 15 | 22 | 8 | 15 | 25 | 48 | 8 | 15 | 23 | 0 | 0 | 0 | 2 | 1 | 0 | 2 | 1 | 7 | 4 | 2 | 5 | 3 | 0 | 0 | 1 | 1 | 0 | 3 | 0 | 2 | 1 | 0 | 0 | 0 | 0 | 1 | 3 | 3 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 3 | 3 | 10 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | Rajkot Rural |  | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 2 | 7 | 23 | 43 | 16 | 25 | 43 | 23 | 91 | 25 | 43 | 22 | 0 | 4 | 1 | 2 | 0 | 1 | 2 | 4 | 10 | 3 | 3 | 18 | 3 | 3 | 3 | 3 | 3 | 7 | 4 | 1 | 0 | 4 | 1 | 3 | 0 | 1 | 0 | 0 | 1 | 0 | 1 | 4 | 0 | 0 | 0 | 0 | 1 | 8 | 3 | 6 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | Morbi |  | 0 | 1 | 3 | 4 | 1 | 3 | 4 | 2 | 0 | 4 | 13 | 20 | 5 | 13 | 20 | 9 | 42 | 10 | 16 | 7 | 0 | 1 | 3 | 0 | 1 | 0 | 1 | 2 | 4 | 0 | 4 | 8 | 1 | 0 | 2 | 0 | 1 | 1 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 1 | 2 | 1 | 0 | 1 | 0 | 0 | 2 | 1 | 1 | 1 | 4 | 2 | 6 | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | Porbandar |  | 0 | 0 | 4 | 0 | 3 | 4 | 0 | 3 | 0 | 4 | 24 | 50 | 9 | 24 | 50 | 13 | 87 | 20 | 50 | 10 | 0 | 0 | 0 | 0 | 2 | 0 | 1 | 4 | 10 | 1 | 2 | 26 | 5 | 3 | 9 | 0 | 4 | 1 | 1 | 0 | 1 | 1 | 1 | 2 | 0 | 1 | 1 | 0 | 2 | 0 | 1 | 1 | 0 | 0 | 4 | 0 | 3 | 9 | 4 | 5 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | Jamnagar |  | 0 | 1 | 3 | 1 | 0 | 3 | 1 | 1 | 0 | 4 | 21 | 49 | 24 | 21 | 49 | 28 | 98 | 18 | 48 | 27 | 0 | 1 | 0 | 0 | 1 | 2 | 0 | 3 | 11 | 7 | 3 | 15 | 3 | 2 | 10 | 7 | 0 | 2 | 3 | 3 | 2 | 4 | 2 | 0 | 0 | 0 | 1 | 1 | 1 | 3 | 1 | 2 | 2 | 1 | 1 | 1 | 1 | 9 | 9 | 8 | 26 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | Bhuj |  | 0 | 0 | 5 | 0 | 1 | 5 | 0 | 1 | 0 | 9 | 27 | 22 | 18 | 27 | 22 | 27 | 76 | 22 | 22 | 26 | 0 | 1 | 0 | 3 | 2 | 0 | 2 | 4 | 11 | 3 | 5 | 4 | 5 | 0 | 4 | 2 | 2 | 1 | 1 | 2 | 0 | 6 | 0 | 0 | 0 | 0 | 1 | 3 | 4 | 1 | 1 | 2 | 0 | 0 | 5 | 0 | 1 | 13 | 2 | 11 | 26 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | Junagadh |  | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 8 | 15 | 43 | 22 | 15 | 43 | 30 | 88 | 15 | 43 | 29 | 0 | 0 | 1 | 3 | 0 | 0 | 4 | 3 | 8 | 1 | 3 | 18 | 5 | 1 | 10 | 7 | 1 | 0 | 3 | 3 | 3 | 1 | 0 | 1 | 3 | 1 | 2 | 0 | 1 | 0 | 1 | 2 | 0 | 1 | 0 | 0 | 1 | 7 | 6 | 7 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | Bhavnagar |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 9 | 23 | 33 | 5 | 24 | 33 | 14 | 71 | 24 | 33 | 14 | 0 | 1 | 1 | 2 | 1 | 1 | 0 | 2 | 10 | 3 | 4 | 10 | 1 | 4 | 6 | 0 | 2 | 4 | 2 | 1 | 1 | 1 | 2 | 0 | 0 | 1 | 0 | 1 | 5 | 0 | 2 | 1 | 0 | 2 | 0 | 0 | 0 | 10 | 1 | 6 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | Botad |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 6 | 3 | 4 | 6 | 3 | 13 | 4 | 6 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 1 | 4 | 0 | 0 | 2 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | Amreli |  | 0 | 2 | 2 | 0 | 2 | 2 | 0 | 4 | 1 | 6 | 27 | 49 | 18 | 28 | 49 | 24 | 101 | 26 | 49 | 20 | 0 | 0 | 0 | 0 | 1 | 0 | 6 | 6 | 8 | 0 | 8 | 22 | 6 | 1 | 13 | 1 | 3 | 2 | 1 | 1 | 1 | 2 | 0 | 1 | 0 | 1 | 1 | 1 | 3 | 1 | 2 | 2 | 0 | 1 | 2 | 0 | 4 | 9 | 4 | 10 | 23 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | Surendranagar |  | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 3 | 12 | 23 | 17 | 13 | 23 | 20 | 56 | 12 | 26 | 20 | 0 | 1 | 0 | 0 | 1 | 1 | 0 | 1 | 6 | 4 | 3 | 12 | 1 | 0 | 2 | 1 | 0 | 1 | 2 | 1 | 1 | 0 | 1 | 0 | 11 | 3 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 7 | 1 | 12 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| PGVCL Total → |  | 0 | 5 | 18 | 5 | 10 | 18 | 5 | 15 | 5 | 57 | 197 | 353 | 159 | 202 | 353 | 216 | 771 | 184 | 351 | 201 | 0 | 9 | 6 | 12 | 10 | 5 | 18 | 30 | 85 | 29 | 38 | 142 | 33 | 14 | 61 | 22 | 18 | 19 | 21 | 13 | 11 | 20 | 8 | 7 | 14 | 9 | 8 | 12 | 23 | 5 | 12 | 14 | 2 | 9 | 14 | 2 | 14 | 81 | 35 | 81 | 197 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0

## Accident (hidden)
Performa – SoP 002: Action taken report for safety
measures complied for the accidents occurred
Circle | DFH | DNFH | OFH | OFA | ONFH | sum | count 002 | Difference | yearly
RJC | [5 empty] | 0 | #REF! | #REF!
Circle | [5 empty] | 0 |  | 0
RJR | [5 empty] | 0 | #REF! | #REF!
Circle | [5 empty] | 0 | #REF! | #REF!
MRB | [5 empty] | 0 | #REF! | #REF!
Circle | [5 empty] | 0 |  | 0
PBR | [5 empty] | 0 | #REF! | #REF!
Circle | [5 empty] | 0 |  | 0
JMN | [5 empty] | 0 | #REF! | #REF!
Circle | [5 empty] | 0 | #REF! | #REF!
BHJ | [5 empty] | 0 | #REF! | #REF!
Circle | [5 empty] | 0 | #REF! | #REF!
JND | [5 empty] | 0 | #REF! | #REF!
Circle | [5 empty] | 0 |  | 0
BVN | [5 empty] | 0 | #REF! | #REF!
Circle | [5 empty] | 0 | #REF! | #REF!
BTD | [5 empty] | 0 | #REF! | #REF!
Circle | [5 empty] | 0 | #REF! | #REF!
AMR | [5 empty] | 0 | #REF! | #REF!
Circle | [5 empty] | 0 |  | 0
SNR | [5 empty] | 0 | #REF! | #REF!
Grand Total | 0 | 0 | 0 | 0 | 0 | 0
RJC | 0 | 0 | 2 | 1 | 6
RJR | 1 | 5 | 6 | 8 | 4
PBR | 1 | 0 | 5 | 1 | 0
JMN | 0 | 2 | 6 | 7 | 1
BHJ | 1 | 2 | 4 | 15 | 8
JND | 0 | 4 | 4 | 11 | 11
BVN | 0 | 6 | 5 | 7 | 3
AMR | 0 | 5 | 4 | 6 | 5
SNR | 0 | 0 | 9 | 4 | 1

## accd-2 (hidden)
PASCHIM GUJARAT VIJ COMPANY LIMITED REGD & CORP OFFICE, RAJKOT
ELECTRICAL ACCIDENTS DETAIL (Cummulative) | [11 empty] | 39508
No. | CIRCLE | DIVISION | S/div | Name of Victim | Date Of Accident | Details of accidents |  |  |  |  | Cause of Accident | Saftery Tools utilised or not? | Action taken against the defaulter
| 1 | 3 |  |  |  | Deprt |  | Outsider |  | FA
| 1 | 3 |  |  |  | FH | NFH | FH | NFH
1 | RJC | RCD-3 | RSD | Jasubhai Bhagwatsinh Rana | 28.04.07 |  | 1 |  |  |  | During restringing of broken LT wire of Ag. Group, suddely return power came and victim got shocked. | N.A. | N.A.
2 | RJC | RCD-1 | Prahlad Plot | L.Z.Goswami | 27.05.07 |  | 1 |  |  |  | While fixing of standard D.O. fuse in place of non standard D.O. fuse, victim got shocked. | N.A. | Disciplinary action against L.I. who was supervising the work is under process.
3 | RJC | RCD-3 | RSD | Buffalow | 10.05.07 |  |  |  |  | 1 | Snapping of Conductor | N.A. | N.A.
4 | RJC | RCD-1 | Prahlad Plot | Rajesh N. Sagathiya | 02.06.2007 |  |  | 1 |  |  | Victim climbed on pole for light repairing unauthorisedly. | N.A. | N.A.
5 | RJC | RCD-2 | Udhyognagar | Shaileshbhai D. Patadiya | 20.06.07 |  |  | 1 |  |  | Victim climbing on iron ladder came in contact with short circuited ceiling fan and got shocked. | N.A. | N.A.
6 | RJC | RCD-2 | Pradhuymannagar | Kushal Pankajbhai Darji | 23.06.07 |  |  | 1 |  |  | Victim came in contact with short circuited street light fixure and got shocked. | N.A. | N.A.
7 | RJC | RCD-2 | Bedinaka | Chandulal D. Prajapati | 23.06.07 |  |  |  | 1 |  | Victim came in contact with street light conductor snapped and got shocked. | N.A. | N.A.
8 | RJC | RCD-3 | Mavdi Road | Durlabhji Sambhubhai Agola & a cow | 18.06.07 |  |  | 1 |  | 1 | Snapping of LT conductor due to heavy wind and rain. | N.A. | N.A.
9 | RJC | RCD-3 | Kalawad Road | Poojaben B. Rajpara | 21.06.07 |  |  | 1 |  |  | Victim was drying clothes on iron wire which came in direct contact with open joint of flexible wire extended in her own house. | N.A. | N.A.
10 | RJC | RCD-3 | Mavdi Road | Cow | 02.06.07 |  |  |  |  | 1 | Snapping of Conductor | N.A. | N.A.
11 | RJC | RCD-3 | Madhapar | Buffalow | 19.06.07 |  |  |  |  | 1 | Snapping of Conductor | N.A. | N.A.
12 | RJC | RCD-3 | RSD | Cow | 21.06.07 |  |  |  |  | 1 | Snapping of Conductor | N.A. | N.A.
13 | RJC | RCD-3 | Mavdi Road | Cow | 22.06.07 |  |  |  |  | 1 | Snapping of Conductor | N.A. | N.A.
14 | RJC | RCD-3 | MRSD | Rameshbhai Madhabhai Sagathiya | 30.7.2007 |  | 1 |  |  |  | A Mechanical Accident, While working he fell down form the PSC pole due to Slip of legs. | NO | NO
15 | RJC | RCD-3 | MRSD | CALF | 2.7.2007 |  |  |  |  | 1 | Snapping of Conductor | N.A. | N.A.
16 | RJC | RCD-3 | MRSD | BUFFALO | 2.7.2007 |  |  |  |  | 1 | Leakage current in guarding wire passed through earthing to pole pit. A buffalow nearby wondering came in contact. | N.A. | N.A.
17 | RJC | RCD-3 | RSD | BUFFALO(RAVA GELA LAMBARIYA) | 8/07/2007. |  |  |  |  | 1 | Leakage Current Flow in Earthing G.I.Wire. | N.A. | T.C.Maint with Earthing
18 | RJC | RCD-3 | RSD | COW(BHARATBHAI SAMATBHAI KOLI) | 25/07/2007. |  |  |  |  | 1 | SNAPPING OF L.T.CONDUCTOR | N.A. | L.T.Maintenance
19 | RJC | RCD-3 | RSD | MAHESH CHHAGANBHAI KOLI | 30/07/2007. |  |  | 1 |  |  | Accidental contact with live electric wire / equipment | N.A. | N.A.
20 | RJC | RCD-2 | MCSD | Ragh ubhai Gobarbhai Bharvad | 13/08/07 |  |  | 1 |  |  | Victim came in contact with short circuited motor in his premises and got shocked. | N.A. | N.A.
21 | RJC | RCD-2 | BNSD | Rajubhai Nagjibhai Parmar | 18/08/07 |  |  | 1 |  |  | Victim came in contact with short circuited ceiling fan while repairing and met with F.A. | N.A. | N.A.
22 | RJC | RCD-3 | RSD | A buffalow | 10/08/07 |  |  |  |  | 1 | Snapping of Conductor | N.A. | N.A.
23 | RJC | RCD-3 | RSD | Sumitaben Chanabhai Uteriya | 31/07/07 |  |  | 1 |  |  | Due to Leakage power from faulty TV - Disc cable in the cabin of ironsheets. | N.A. | N.A.
24 | RJC |  |  | Vijaybhai Chanabhai Uteriya | -do- |  |  |  | 1 |  | -do- | N.A. | N.A.
25 | RJC | RCD-3 | RSD | A cow | 31.08.07 |  |  |  |  | 1 | Victim came in contact with GI wire in which leakagte currenmt flown due to heavy rain and wind. | N.A. | N.A.
26 | RJC | RCD-3 | KRSD | A cow | 31.08.07 |  |  |  |  | 1 | Victim came in contact with GI wire in which leakagte currenmt flown due to heavy rain and wind. | N.A. | N.A.
27 | RJC | RCD-3 | KRSD | Mustaq Ahmed Malik | 31.08.07 |  |  |  | 1 |  | Vic5tim came in contact with MMB which was installed on PSC pole. On account of cable insulations, biting by squirrels during rainy season, short circuit has occurred. Victim came in contact with MMB and got shocked due to induction. | N.A. | N.A.
28 | RJC | RCD-1 | MPSD | A cow | 24.09.07 |  |  |  |  | 1 | Victim came in contact with GI wire in which leakagte currenmt flown due to heavy rain and wind. | N.A. | N.A.
29 | RJC | RCD-2 | UNSD | Rajubhai keshabhai Parmar | 09.11.07 |  |  | 1 |  |  | While opening of mail female pin of flexcible extension wire of the motor which is in running condition, victim came in contact with live part of male pin portion and got shocked, result in fatal accident | N.A. | N.A.
30 | RJC | RCD-2 | UNSD | Nirubhai R Mehta | 12.11.07 |  | 1 |  |  |  | While attending complaint of three phase service, victim was fell down from LT pole (girder) as his grip of hand and leg to the pole was left and fell down hence got injured to both legs. | Yes | N.A.
31 | RJC | RCD-2 | UNSD | Diptiben Viralbhai Patel | 08.01.2008 |  |  | 1 |  |  | While using the domestic heater (immersion type), victim touched the water and got shocked | N.A. | N.A.
32 | RJC | RCD-3 | MPSD | 1. Gordhanbhai Sakhiya, | 12.01.2008 |  |  | 1 |  |  | Leakage current was passing through the fencing wire and victim came in contact with fencing wire. | N.A. | N.A.
32 | RJC | RCD-3 | MPSD | Lalitbhai Sakhiya | 12.01.2008 |  |  | 1 |  |  | Leakage current was passing through the fencing wire and victim came in contact with fencing wire. | N.A. | N.A.
33 | RJC | RCD-2 | UNSD | 1. Vimlaben S. Jaishwal | 19.02.2008 |  |  |  | 1 |  | While carrying out Iron cot on terrace, victim came in contact with live 11 KV line and got shocked. | N.A. | N.A.
33 | RJC | RCD-2 | UNSD | Sharmilaben P. Jaishwal | 19.02.2008 |  |  |  | 1 |  | While carrying out Iron cot on terrace, victim came in contact with live 11 KV line and got shocked. | N.A. | N.A.
34 | RJC | RCD-1 | KOTHARIYA ROAD | 1. Smt. Hansaben Harkantbhai Chauhan | 02.03.2008 |  |  | 1 |  |  | While spraying water to renovated own house, victim came in contact with electric board which was removed from wall. Victim tried to repair the same and by mistake, he came in live contact with the supply. | N.A. | N.A.
1 | RJR | Morbi | Shanala | Rameshbhai Bhaijibhai Tadvi | 24/04/2007 | 1 | 0 | 0 | 0 | 0 | Unbalance from Pole & Hence fall down to earth due to mechanical Injury accident occurred.
2 | RJR | Morbi | WT | Bhaveshbhai D Sitapara | 28/04/2007 | 0 | 1 | 0 | 0 | 0 | PSC Pole get broken from the bottom level & person fall down & hence accident occurred.
3 | RJR | Morbi | MT-1 | Lalitaben Natvarlal Nakum | 2007-01-05 | 0 | 0 | 0 | 1 | 0 | Leakage current through street light fixture.
4 | RJR | Morbi | WT | Bhikhalal Kanjibhai Makvana | 23/05/2007 | 0 | 1 | 0 | 0 | 0 | Reverse Current came in line from unknown appliance(Generator)/place & hence accident occurred.
5 | RJR | Morbi | MR | Bipinpal Sahdevprasad Gardia | 2007-01-06 | 0 | 0 | 1 | 0 | 0 | Short Circuit in internal premises of victim
6 | RJR | Morbi | Shanala | Buffallow | 2007-03-06 | 0 | 0 | 0 | 0 | 1 | Conductor Snapping
7 | RJR | Morbi | MR | Buffallow | 2007-05-06 | 0 | 0 | 0 | 0 | 1 | Leakage Current through LT Pole due to rubbibng of buffallow's horn
8 | RJR | Morbi | WT | Cow | 2007-05-06 | 0 | 0 | 0 | 0 | 1 | Short Circuit of Street Light Fixture of LT Pole
9 | RJR | Morbi | MR | Revuben Naranbhai Tundia | 2007-07-06 | 0 | 0 | 1 | 0 | 0 | Short Circuit in internal premises of victim
10 | RJR | Morbi | MT-1 | Cattle Bull 2 No (ધણ ખૂંટ) | 2007-07-06 | 0 | 0 | 0 | 0 | 1 | Leakage current through street light fixture.
11 | RJR | Morbi | MR | Asif Habib Sandhi | 15/06/2007 | 0 | 0 | 1 | 0 | 0 | Accidental contact with live wire while installing dish TV cable
12 | RJR | Morbi | MT-1 | Kesha Kuka Parmar | 16/06/2007 | 0 | 0 | 1 | 0 | 0 | Short Circuit in internal premises of victim
13 | RJR | Morbi | MT-1 | Cattle Bull 1 No (ધણ ખૂંટ) | 16/06/2007 | 0 | 0 | 0 | 0 | 1 | leakage current through earthing due to broken LT wire from T/C & neutral touched to the fabriction.
14 | RJR | Morbi | MT-2 | M.H.Shilu | 2007-08-07 | 0 | 1 | 0 | 0 | 0 | Mechanical Unbalance while coming down from pole & hence accident occurred.
15 | RJR | Morbi | MR | Buffallow | 2007-11-07 | 0 | 0 | 0 | 0 | 1 | Conductor Snapping
16 | RJR | Morbi | WR | Buffallow | 22/7/2007 | 0 | 0 | 0 | 0 | 1 | Leakage Current Through earth. (PM Report avaited)
17 | RJR | Morbi | TKR | He-Buffallow | 26/7/2007 | 0 | 0 | 0 | 0 | 1 | Leakage Current Through Earthing wire of T/C
18 | RJR | Morbi | WT | Buffallow | 28/7/2007 | 0 | 0 | 0 | 0 | 1 | Leakage Current Through Earthing wire of T/C
19 | RJR | Morbi | MR | Sukhabhai Tejabhai | 30/7/2007 | 0 | 0 | 1 | 0 | 0 | Insulation of service get damaged & leakage current flown through earthing wire
20 | RJR | Morbi | WT | Buffallow | 31/7/2007 | 0 | 0 | 0 | 0 | 1 | Bird Fault on 11 KV & leakage current flown through earth
21 | RJR | Morbi | WT | Buffallow | 2007-01-08 | 0 | 0 | 0 | 0 | 1 | Leakage Current Through earthing wire of T/C Centre
22 | RJR | Morbi | WT | Buffallow | 2007-03-08 | 0 | 0 | 0 | 0 | 1 | Leakage Current Through earthing wire of T/C Centre
23 | RJR | Morbi | MR | Buffallow | 2007-03-08 | 0 | 0 | 0 | 0 | 1 | Conductor Snapping
24 | RJR | Morbi | MR | Buffallow - 2 Nos. | 2007-05-08 | 0 | 0 | 0 | 0 | 1 | Conductor Snapping
25 | RJR | Morbi | MR | Buffallow | 2007-05-08 | 0 | 0 | 0 | 0 | 1 | Conductor Snapping
26 | RJR | Morbi | WR | Bullock | 17/8/2007 | 0 | 0 | 0 | 0 | 1 | Leakage Current Through T/c earthing
27 | RJR | Morbi | WT | Buffallow | 17/8/2007 | 0 | 0 | 0 | 0 | 1 | Leakage current Pass through Guy Wire Which Is Damaged By Buffalo
28 | RJR | Morbi | TKR | Buffallow | 30/08/2007 | 0 | 0 | 0 | 0 | 1 | due to heavy wind phase wire get detached from binding & touched to the c clamp of neutral wire & leakage current flown through earth wire due to wet land.
29 | RJR | Morbi | TKR | Buffallow | 21/09/2007 | 0 | 0 | 0 | 0 | 1 | An electric motor of pumping the water in house of Shri Shamji Moti Vishodiya get its body Short, a return power flows thro' a neutral wire & reaches at a T/C & from it the current flows thro' earth wire to a gnd. level of land & also due to moisture in a
30 | RJR | Morbi | W® | Sh. Bhupatbhai Khodabhai Bambhva | 3.10.2007 | 0 | 0 | 1 | 0 | 0 | While cutting branch of tree accidantly came in contact with near by 11 KV Line & get electric shock.
31 | RJR | Morbi | TKR | Cow | 21/11/2007 | 0 | 0 | 0 | 0 | 1 | 11 kv Chhattar (JGY) Feeders Top Clamp Conductor Snapped And Fall Down On Land (Between Loc. No.306,307) & That Time One No.Of Cow of Sh. Gajera Vijay D. At-Prabhunagar Pass- Out From That Place And Comes In To Contact With Live Wire
32 | RJR | RRD | Jasdan | Devram Devabhai Nakum | 2007-08-05 | 0 | 0 | 1 | 0 | 0 | Victim i.e. labour of contractor of GETCO while doing stringing of new 66KV line, climed live 11KV Kanpar Ag fdr & got Elect. Shock & fall down. | Yes | Accidental contect with live wire
33 | RJR | RRD | Shapar Veraval | Abuben Daudbhai Riyami | 2007-10-05 | 0 | 1 | 0 | 0 | 0 | Victim was checking DO fuse by taking line clear of 11KV Balaji fdr but return power came & he got Elect. Shock. | Yes | Any other Reson
34 | RJR | RRD | Shapar Veraval | Valiben Charan | 21/6/07 | 0 | 0 | 0 | 0 | 1 | Leakage in TC earthing |  | Accidental contect with live wire
35 | RJR | RRD | Vinchhiya | Amra Bhura Bharvad | 23/6/07 | 0 | 0 | 0 | 0 | 1 | Leakage in TC earthing |  | Accidental contect with live wire
36 | RJR | RRD | Vinchhiya | Raziyaben Hanifbhai Lohiya | 23/6/07 | 0 | 0 | 1 | 0 | 0 | Victim came in contact with water pump in his own premises
37 | RJR | RRD | Vinchhiya | Savshibhai Sondabhai | 25/6/07 | 0 | 0 | 0 | 0 | 1 | Cond. Snapping of 11KV Gadhala fdr |  | Snapping of Cond
38 | RJR | RRD | Paddhari | Khimabhai Raodevbhai | 30/6/07 | 0 | 0 | 0 | 0 | 1 | Leakage in TC earthing |  | Accidental contect with live wire
39 | RJR | RRD | Paddhari | Bavanjibhai Karmanbhai | 2007-01-07 | 0 | 0 | 0 | 0 | 1 | In heavy wind & rain LT line cable used as dropper & GI wire touched to c-clamp. & other end of cable broken & touched to lower end of guy wire & cow came in contact with guy wire. |  | Snapping of Cond
40 | RJR | RRD | Shapar Veraval | Jaluben Surabhai Tolia | 2007-05-07 | 0 | 0 | 0 | 0 | 1 | Leakage in TC earthing |  | Accidental contect with live wire
41 | RJR | RRD | Jasdan | Nathu chanabhai Chirodiya | 12.08.08 | 0 | 0 | 0 | 0 | 1 | Leakage in TC earthing |  | Accidental contect with live wire
42 | RJR | RRD | Jasdan | Veljibhai Kalubhai Kaviyad | 23.08.08 | 0 | 1 | 0 | 0 | 0 | Victim slept from the pole |  | Mechanical Accident
43 | RJR | RRD | Jasdan | Laghrabhai Sadurbhai Bharvad | 31.08.07 | 0 | 0 | 0 | 0 | 1 | Return Power came in T/C neutral and earthing due to deffective wiring of near by Industrial connection.
44 | RJR | RRD | Jasdan | Dipakbhai Ladhabhai Nagdadkiya | 8.09.07 | 0 | 0 | 1 | 0 | 0 | Victim eas doing some mischief with earthing wire climbing DP of Polarpar feeder & earthing wire touched jumper od DP. |  |  | Any other Reson
45 | RJR | RRD | Paddhari | Nagajibhai Haribhai Vala | 04.10.07 | 0 | 0 | 0 | 0 | 2 | Metalic fencing wire of the farm house touched Un authorised exteneded wire of AG connection at Targhadi village |  |  | Un authorised work
46 | RJR | RRD | Paddhari | Khengarbhyai Dayabhai Dafada | 09.10.07 | 1 | 0 | 0 | 0 | 0 | On request by victim JE has taken LCP of 11KV Sanosara feeder.but actually work was taken on hand on 11 KV water works feeder. Hence victim touched live wire of 11 KV ww fdr. |  |  | Accidental contect with live wire
47 | RJR | RRD | Jasdan | Vinodbhai A Vaniya | 15.10.07 | 0 | 1 | 0 | 0 | 0 | To attend jumper fault of Kamalpur AG fdr by mistake GO switch of other side was made OFF on main line,while power was ON,from 66 Kv kamaalpur S/S. Victime came in contact with live wire and Fell fown. |  |  | Accidental contect with live wire
48 | RJR | RRD | Jasdan | Panch Uka Gholakiya | 16.10.07 | 0 | 0 | 0 | 0 | 2 | Snapping of Conductor at Jungvad village. |  |  | Snapping of Cond
49 | RJR | RRD | Jasdan | Kum. Jalpaben Vinodrai Mehta | 13.11.07 | 0 | 0 | 0 | 1 | 0 | Because of Extended Balcony. Distance Bet. Balcony and 11 Kv line is less. Victim Came in Contact with this line.
50 | RJR | RRD | Shapar Veraval | Hansraj Savji Solanki | 10.8.07 | 0 | 1 | 0 | 0 | 0 | Acci took place due to leakage current of Neutral.
51 | RJR | RRD | Jasdan | Sh.Rajesh bhai.Vibha bhai Vakatar | 7.12.07 | 0 | 0 | 1 | 0 | 0 | Victim lifted Galvenised pipe upward & This pipe came in contact with 11 kv Virnagar Ag feeder |  |  | Any other Reson
52 | RJR | Dhoraji | Dhoraji (R) | Dinesh Ruda Manvar | 26.03.07 | 0 | 0 | 1 | 0 | 0 | Labour of civil contractor when taking iron pipe from machdo touch the 11 KV line and leakage current pass through body of victim
53 | RJR | Dhoraji | Upleta (T) | Rajendra Babubhai Gadiyal | 07.04.07 | 0 | 1 | 0 | 0 | 0 | Victim claimb another feeder for which line clear was not taken by his own mistake.
54 | RJR | Dhoraji | Jetpur (T) | Jyotsnaben Hakabhai Bhadeliya | 08.04.07 | 0 | 0 | 0 | 1 | 0 | Due to sparking between two conductors it was broken and fallen on wires of the clothes drying. Hence a leakage current passes through this cloth drying wire.Victim contact with this wire and FA occurred.(In Private Premises)
55 | RJR | Dhoraji | Jetpur (R) | Sonalben Kamleshbhai Dobariya | 20.05.07 | 0 | 0 | 1 | 0 | 0 | Accident in private premises
56 | RJR | Dhoraji | Jetpur (R) | FA to bullock of Sh. Ramnikbhai Mandanbhai Radadiya | 20.06.07 | 0 | 0 | 0 | 0 | 1 | Due to snapping of conductor
57 | RJR | Dhoraji | Jetpur (T) | FA to Cow of Sh. Bhikhabhai Bhurabhai | 20.06.07 | 0 | 0 | 0 | 0 | 1 | Leackage of earthing in TC
58 | RJR | Dhoraji | Bhayavadar | FA to Cow without owner | 21.06.07 | 0 | 0 | 0 | 0 | 1 | Due to Burning of insulation of street light wire and touch to socate and leackage current passes through girder pole.
59 | RJR | Dhoraji | Dhoraji (R) | FA to bullock of Sh. Subhashbhai Laljibhai | 27.06.07 | 0 | 0 | 0 | 0 | 1 | Due to heavy wind pressure LT line pole was broken & fallen on earth with broken LT line wire & bullock contact with this LT line wire.
60 | RJR | Dhoraji | Dhoraji (T) | Ashwin I. Chauhan (Helper) | 05.07.07 | 0 | 1 | 0 | 0 | 0 | Installation of terminal of CT's ACB deteriorated & came in contact to the structure, dead short circuit occurred resulted into heavy flesh. Face of victim was near ACB influenced that place & met with not fatal accident.
61 | RJR | Dhoraji | Jetpur (R) | Chhaganbhai R. Kochhra (Helper) | 11.07.07 | 0 | 1 | 0 | 0 | 0 | Fall down from PSC pole while stringing of 11 KV cond. At village Bava-Pipaliya
62 | RJR | Dhoraji | Jamkandorana | Smt. Raliyatben Hansrajbhai Dhanani | 14.07.07 | 0 | 0 | 1 | 0 | 0 | Contact with live snapped conductor
63 | RJR | Dhoraji | Jamkandorana | Smt. Labhuben Nathabhai | 14.07.07 | 0 | 0 | 0 | 1 | 0 | While trying to save Smt. Raliyatben Hansrajbhai who was already contct with live snapped conductor
64 | RJR | Dhoraji | Jamkandorana | Sh. Mahesh Ranchhod | 30.07.07 | 0 | 0 | 1 | 0 | 0 | An outsider person Shri Ramnikbhai Bhikhabhai Savaliya Was fixing 11K D.O. Fuse wire with the help of bamboo at that time 11 Kv main jumper was blowing off and touched to the pole channel of D.P.Structure and leakage current passes through earthing of DP.
65 | RJR | Dhoraji | Jamkandorana | FA to bull of Sh. Pramukh Gauseva Samaj Charel | 08.08.07 | 0 | 0 | 0 | 0 | 1 | R-Phase cable of LT line was burnt and melt which was touched to iron C-clamp, so the returned leakage current passing through T/C earthling wire,(there was rain fall at that time) the bull while passes near T/C structure and contact with earthling wire a
66 | RJR | Dhoraji | Upleta Rural | Sh. Naran Hamir | 03.08.07 | 0 | 0 | 1 | 0 | 0 | In agriculture farm while victim was working near T/C, his hand contact with earthing wire of T/C which was broken inside the ground and not seen out side ground , in this way due to return leakage current flowing through the earthing wire FA occurred to
67 | RJR | Dhoraji | Dhoraji Rural | FA to bullock of Sh. Devshi Ukabhai Paradava | 12.08.07 | 0 | 0 | 0 | 0 | 2 | Due to heavy wind and rain LT line conductor was broken and fallen down on earth while Sh. Devshibhai Ukabhai Paradva passes with his cart near this LT line and his both bullocks came in contact with the live conductor and got an electric shock and died.
68 | RJR | Dhoraji | Dhoraji Rural | Sh. C.S. Bhut (Helper) | 14.08.07 | 0 | 1 | 0 | 0 | 0 | For restringing of LT line conductor, victim climbed on P.S.C. pole for removing of binding at that time pole is breaks & fall down. Hence accident is occurred.
69 | RJR | Dhoraji | Upleta Rural | FA to Buffalo of Sh. Rajesh Jeraj | 17.08.07 | 0 | 0 | 0 | 0 | 1 | Earthing wire of T/C was broken from earthing plate at under ground level buffalo of Sh. Rajeshbhai Jerambhai Ardeshana while passes near this T/C and came in contact with this broken earthing wire from which leakage current flow and got an electric shock
70 | RJR | Dhoraji | Jetpur Town | FA to buffalo of Sh. Naran Vira | 22.08.07 | 0 | 0 | 0 | 0 | 1 | LT cable burned on top of PSC pole so live cable terminal touched to the GI wire which is earthing of PSC pole so leakage current passed through the GI wire while buffalo of Sh. Naran Vira Rabari came in contact with this GI wire and got an electric shock
71 | RJR | Dhoraji | Jetpur Rural | FA to buffalo of Sh. Pragji Mohan | 05.09.07 | 0 | 0 | 0 | 0 | 1 | Transformer neutral failed hence leakage current flowing through the transformer centre earth wire and buffalo of Sh. Pragaji Mohan Paghdar while passes near the T/C and came in contact with earth wire of T/C and got an electric shock and died.
72 | RJR | Dhoraji | Dhoraji Rural | FA to buffalo of Sh. Amra Ala | 14.09.07 | 0 | 0 | 0 | 0 | 1 | On one LT line pole,10 span away from T/C, one LT line conductor, fall down from insulator & touch to "C"clamp, & earthed. Which make a leakage current flow from T/C earthing to that pole earthing. As the earth are watery & Buffalo came in contact with th
73 | RJR | Dhoraji | Dhoraji Town | FA to cow of Sh. Khodabhai Bhutabhai | 20.09.07 | 0 | 0 | 0 | 0 | 1 | Thread/Rag pulled by any resident of multistory building or may be flying of kite guide wire and L.T. live wire was wrilling to each other hence a leakage current flowing through the guide wire to the girder pole while a cow of Sh. Khodabhai Bhutabhai Bha
74 | RJR | Dhoraji | Bhayavadar | FA to Cow of Sh. Menshi Ramshi | 24.09.07 | 0 | 0 | 0 | 0 | 1 | On 11 KV pole of first span ahead agriculture T/C. A pin insulator was becomes faulty and broke out. Due to this 11 KV line conductor snapped from the binding of pin insulator and fallen on the V X Arm and due to shot circuit conductor was broken & fallen
75 | RJR | Dhoraji | Jetpur Rural | FA to bullock of Sh. Arafebbhai Ladhabhai | 25.09.07 | 0 | 0 | 0 | 0 | 1 | Due to deterioration of agriculture LT line conductor one of the phase conductor was broken near the C Clamp and fallen down on the ground. While Sh. Arfebbhai Ladhabhai passes with his bullock-cart near this LT line a bullock came in contact with live LT
76 | RJR | Dhoraji | Upleta ® | FA to bullock of Sh. Nandalal Dharamshi at Vill. Mervadar | 30.9.07 | 0 | 0 | 0 | 0 | 1 | A Big flying bird called "Varvangdu" was found in touching possition between P-P in Ag. LT Line hence P-P Short Circuit was occurred in LT line, Wire was broken and falling on the earth, Shri Nandlal passong with his bullock cart near this LT line and one
77 | RJR | Dhoraji | Dhoraji (R) | NFH to outsider Shri Keshavbhai Naranbhai Rathod at Vill. Kalana | 6.10.07 | 0 | 0 | 0 | 1 | 0
78 | RJR | Dhoraji | Jetpur Rural | NFH to human outsider Sh. Dinesh Lakharam Vanad at Vill: Thanagalol | 13.11.07 | 0 | 0 | 0 | 1 | 0 | Victim climbed on 11 KV pole for tapping work from existing 11 KV line, at that time victim has loosed his balance and fall down from this 11 KV line pole. Hence mechanical accident occurred.
79 | RJR | Dhoraji | Jetpur Rural | NFH to Human outsider Kum. Amita Haribhai Barvadia at vill: Mevasa | 16.11.07 | 0 | 0 | 0 | 1 | 0 | There is a residence building of Sh. Haribhai Parsotambhai Barvadia at village Mevasa. One 11 KV line is passing about 4 feet apart from the wall of this residence Sh. Haribhai Parsotambhai has constructed and extended three feet "RAVES" near the terrace.
80 | RJR | Dhoraji | Upleta Rural | NFH to Helper Sh. Amishkumar Maganlal ghodasara at vill : Khakhi - jalia | 27.12.07 | 0 | 1 | 0 | 0 | 0 | When victim climbed on LT line PSC pole for maintenance work at that time PSC pole was broken and fall down. Hence accident is occurred.
81 | RJR | Dhoraji | Jamkandorana | NFA to Bullock of Sh.Najubhai Bijalbhai Rabari at vill: Tarvada | 15.02.08 | 0 | 0 | 0 | 0 | 1 | 11 KV conductor broke down from load side of 11 KV Sanala JGY feeder and fell down on the earth. Due to this return power flew in the conductor. While shri Najubhai Bijalbhai were passing with his cart, his one no. of bullock came in contact with this bro
82 | RJR | GONDAL | TOWN | RAMBAHADUR LAKHAN MUKHIYA | 2007-01-30 | 0 | 0 | 1 | 0 | 0 | IT WAS OCCURRED DUE TO TRUCK STRIKE WITH LT LINE NUTRAL CONDUCTOR & THE LABOUR FALL DOWN FROM THE TRUCK
83 | RJR | GONDAL | TOWN | SONUBHAI NANDRAM VAGHELA | 2007-04-17 | 0 | 0 | 0 | 1 | 0 | THE VICTIM WAS DOING PAINTING WORK AND TOUCHED TO 11 KV LINE DURING WHILE PAINTING
84 | RJR | GONDAL | VASAVAD | SOMABHAI BHANABHAI | 2007-02-13 | 0 | 0 | 0 | 0 | 1 | DUE TO CONDUCTOR FALL DOWN AND TOUCHED TO C CLAMP AND IT POLE WAS EARTH. THE ANIMAL TOUCHED THE POLE
85 | RJR | GONDAL | VASAVAD | CHANDULAL UMIYASHANKAR | 2007-05-05 | 0 | 0 | 0 | 0 | 1 | DUE TO DROP OF CONDUCTOR FROM SHACKLE INSULATOR & CONDUCTOR TOUCHED THE COW
86 | RJR | GONDAL | KOTDA | Popatbhai Dungarbhai Kakadiya | 2007-05-20 | 0 | 0 | 1 | 0 | 0 | due person repairedd starter on his premises and touch to live wire
87 | RJR | GONDAL | KOTDA | Panchabhai Bachubhai Choriya | 2007-06-04 | 0 | 0 | 0 | 0 | 5 | due to leakage of earthing current at LST transformer
88 | RJR | GONDAL | RURAL | C.J.Jadeja (Helper) | 2007-06-12 | 0 | 1 | 0 | 0 | 0 | man was working on LT line and at that time LT line Touched to 11KV line at crossing of both line
89 | RJR | GONDAL | RURAL | Khenga Machha Ghodasara | 2007-06-28 | 0 | 0 | 0 | 0 | 1 | LT line touched to garding and due to that leakage current accident occured
90 | RJR | GONDAL | LODHIKA | Rupabhai Dayabhai Lal | 2007-07-02 | 0 | 0 | 0 | 0 | 1 | For Changing Faulty Transformer, While Line Inspecor Taking The L.C. the contractor's worker W/O. any Instruction climb on D.P. for removal of LT cable etc. (D.O. fuse was already removed at the time of T/C. fault) and victim (Contractor's worker ) touch
91 | RJR | GONDAL | RURAL | M.G. PAMBHAR(HELPER) | 2007-07-11 | 0 | 1 | 0 | 0 | 0 | While working on pole he fall down from pole
92 | RJR | GONDAL | LODHIKA | MANSUKH PREMJI RAKHOLIYA | 2007-06-26 | 0 | 0 | 1 | 0 | 0 | While Stringing ofL.T.line
93 | RJR | GONDAL | LODHIKA | ATUL PARSHOTAM LILA | 2007-06-26 | 0 | 0 | 1 | 0 | 0 | While Stringing ofL.T.line
94 | RJR | GONDAL | LODHIKA | Mansukh Batuk Vora | 2007-06-26 | 0 | 0 | 0 | 1 | 0 | While Stringing ofL.T.line
95 | RJR | GONDAL | LODHIKA | KantilalBatuk Vora | 2007-06-26 | 0 | 0 | 0 | 1 | 0 | While Stringing ofL.T.line
96 | RJR | GONDAL | LODHIKA | D.M.Damor | 2007-06-26 | 0 | 1 | 0 | 0 | 0 | While Stringing ofL.T.line
97 | RJR | GONDAL | RURAL | MANISHBHAI JAGDISHBHAI CHAUHAN | 2007-06-19 | 0 | 0 | 0 | 1 | 0 | Boy named manish climbed on pole to Catch dove & Shocked
98 | RJR | GONDAL | RURAL | BABU BHANU SARVAIA | 2007-07-31 | 0 | 0 | 0 | 0 | 1 | Shackle insulator of 3 phase 3wireL.t Line Broken & that's why conductor scrap occures. Buffallow puts its leg on it & died at the place
99 | RJR | GONDAL | RURAL | Bhalani Jiva Kachad | 2007-08-10 | 0 | 0 | 0 | 0 | 2 | There is a100 kva transformer for royal cement industries LT connection. Due to any how reason in consumers premises, leakage current flows in transformers earthing.there is a mud and water near transformer surrounding area,buffalow & cow passes near it ,
100 | RJR | GONDAL | RURAL | Gulab Klayan Jadeja | 2007-08-11 | 0 | 0 | 0 | 0 | 1 | IN LT LINE OF W.W. CONNECTION, LT LINES CEMENT POLE BECOME CROSS DUE TO HEAVY WIND, THAT’S WHY LT LINE LIVE WIRE & ITS GUARDING FROM AGLT LINE TOUCHED & LEAKAGE CURRENT PASSES THROUGH POLE'S EARTHINGMUD & WATER LYING NEAR POLES SURROUNDING, COW PUT ITS
101 | RJR | GONDAL | RURAL | Sava Sura Khit | 2007-08-15 | 0 | 0 | 0 | 0 | 1 | in L.T. Line of 25kv Shivarajgadh feeder at ninth pole from T/C L.T. Conductor slip down from shackle insulator to C - Clamp that’s why leackage current flows through transformer earthing Buffallow Goes near transformer & touched with earthing & Get elect
102 | RJR | GONDAL | Kotda | Bhada Ravji Savaliya | 2007-09-05 | 0 | 0 | 0 | 0 | 1 | Load Side Jumper touched to tapping angle & leakage Current Passed
103 | RJR | GONDAL | Lodhika | Raniben Tikhabhai Charan | 2007-09-16 | 0 | 0 | 1 | 0 | 0 | Accident Occurred Due to LT shackle pole guy is released from ground because of rain season the LT line span being loosed Distance from ground is about 3to 4feet it may be possible the victim touch to lt line & accident may be occurred.
104 | RJR | GONDAL | Lodhika | Praful Bhai Vasantji Vyas | 2007-09-25 | 0 | 0 | 0 | 0 | 1 | L.T. Line Main Wire Of Fuse Box is Breaked & Touched to Guy Clamp. Guy Wire is Bound to Telephone Pole with wire so Telephone pole is shocked . Horse touched to telephone pole & Shocked.
105 | RJR | GONDAL | LABORATORY | DHIRUBHAI MODHAVANIYA | 2007-08-17 | 0 | 1 | 0 | 0 | 0 | Blast due to shortening of PT link whil e working
106 | RJR | GONDAL | VASAVAD | BHARATBHAI KESHABHAI KHUNT | 2007-09-02 | 0 | 0 | 0 | 0 | 2 | Due to break down of conductor which falls on earth and two bullocks are passed through it and so due to shock two bullocks has been died
107 | RJR | GONDAL | LODHIKA | Rameshbhai Paru | 10.9.2007 | 0 | 0 | 1 | 0 | 0 | Due to snapping of conductor
108 | RJR | GONDAL | KOTDA | Nareshbhai Mangaldas Asari | 12.10.2007 | 0 | 1 | 0 | 0 | 0 | While carrying out the work on the transformer center he might have fell down to the land.
109 | RJR | GONDAL | GONDAL (T) | Salimbhai Pathan | 17.11.07 | 0 | 1 | 0 | 0 | 0 | During Maintenance work by mistake retain is contect with 11 KV Line and he was socked
110 | RJR | GONDAL | GONDAL (T) | Maganbhai Dayabhai Savaliya | 17.11.07 | 0 | 0 | 0 | 0 | 1 | Because of conductor failed on bufallow by mistake of children playing with thread which was shock on LT line
111 | RJR | GONDAL | KOTDA | Laljibhai Devshibhai Mevada | 25.11.07 | 0 | 0 | 1 | 0 | 0 | At the time of shock this son with jumping hence of victim where such the with live 11 Kv conductor and we volt shock
112 | RJR | GONDAL | GONDAL (T) | Vinod Ashokbhai Solanki | 07.12.07 | 0 | 0 | 0 | 1 | 0 | At the time of cutting leavs of tree victim was touched with live 11 KV conductor and he was shocked
113 | RJR | GONDAL | KOTDA | Kanubhai Jivabhai Makwana |  | 1 | 0 | 0 | 0 | 0 | To Avoid Bird fault problem on 11 Kv Nana Mandwa Ag. Feeder, it was planned to provide 11 Kv support pin below jumpers of Girder D.P. After switching off the feeder, victim climbed Gurder pole DP along with safety belt and helmet. While sitting on DP stru
114 | RJR | MORBI | SHANALA | Sh. JETHABHAI RUDABHAI | 16-3-2008 | 1 | 0 | 0 | 0 | 0 | In The LT Circuit of Modern Hall T/C Between Two LT Pole There is Guarding provided under LT Line. Below this LT Line’s guarding Dish TV Cable is crossing at mid span. This Dish TV cable was found tight at the time of inspection (visiting the site) & due | - | -
1 | PBR | KSD-I | Malia | Sarman Ram Khambhala | 2007-04-09 |  |  |  | 1 |  | Non Fatal Accident Due To Brekage Of T/C Dp At Village Amrapur
2 | PBR | PBR (O&M) | Coastal | Maliben Chanabhai Makwana | 2007-05-02 |  |  |  | 1 |  | Non Fatal Accidentl Occured Due Leakage Current In Wiring In Her Premises At Village Baradia.
3 | PBR | PBR (O&M) | Coastal | Jisgnesh Shivram Joshi | 2007-05-07 |  |  |  | 1 |  | Non Fatal Accidentl Occured At Time Of Attending Lt Service Fault By Private Person At Village Khapat
4 | PBR | PBR (O&M) | Bantwa | Prafulbhai Babubhai Chorvada | 2007-05-08 |  |  | 1 |  |  | Accidently Touching With 11 Kv Line During Unloading Of Marriage Luggage From The Truck At Vill. Limbuda.
5 | PBR | KSD-I | KeshodR-1 | Harsukh Ruda Chhelavada | 2007-05-09 |  |  | 1 |  |  | Suspicious (Reason Under Investigation) At Villagerangpur
6 | PBR | KSD-I | KeshodR-2 | Buffalow - Sh. Haja J. Kangad | 2007-05-11 |  |  |  |  | 1 | Leakage Current In T/C Earth Wire
7 | PBR | PBR (O&M) | Kutiyana | Bullock of Shri Rambhai P. Babariya | 2007-05-27 |  |  |  |  | 1 | Snapping Of Conductor
8 | PBR | PBR (O&M) | Bagvadar | Buffalow - Sh. Rambhai Rajabhai | 2007-06-05 |  |  |  |  | 1 | Snapping Of Conductor
9 | PBR | KSD-I | Keshod-R-2 | Bullock of Safeb Haja Movadia | 2007-06-21 |  |  |  |  | 1 | Leakage Current In Lt Line Earth Wire
10 | PBR | KSD-I | Keshod-R-1 | Buffalow - Jagmal Vajshi Maru | 2007-06-21 |  |  |  |  | 1 | Leakage Current In Lt Line Earth Wire
11 | PBR | KSD-I | Keshod-T | Jayesh Hamirbhai Solanki | 2007-06-24 |  |  |  | 1 |  | Non Fatal Accident Due To Accidental Touching Of 11 Kv By Rod At Keshod Town
12 | PBR | KSD-I | Keshod-R-2 | Buffalow - Rasik Ramji Hadwani | 2007-06-24 |  |  |  |  | 1 | Leakage Current In Lt Line Earth Wire
13 | PBR | PBR (O&M) | Ranavav | Cow - Sh. Polabhai B. Rabari | 2007-06-25 |  |  |  |  | 1 | Snapping Of Conductor
14 | PBR | PBR (City) | PBR City | Babubhai Pamabhai Bardarshahi | 2007-06-26 |  |  | 1 |  |  | In Private Premises While Switching On Electric Motor
15 | PBR | KSD-I | KeshodR-1 | Parbatbhai Masribhai Chocha | 2007-06-26 |  |  | 1 |  |  | Fatal Accident Due To Snapping Of Lt Conductor At Village Revdra
16 | PBR | KSD-II | Chorwad | Buffalow - Bachu Jetha | 2007-06-28 |  |  |  |  | 1 | Leakage Current In Lt Line Earth Wire | NA | NA
17 | PBR | KSD-II | Chorwad | Hasmukhbhai Bachubhai Chauhan | 2007-06-22 |  | 1 |  |  |  | Nfh (Dep.) Occurred Due To Sliping Of Hand During At The Time Of Climbing Of Lt Line Girder Pole
18 | PBR | PBR (O&M) | Kutiyana | Rama Sarman Ratiya | 2007-07-03 |  |  | 1 |  |  | Fatal Human Accident (Os) Occurred At The Time Of Unauthorisedly Climbing Lt Line For Lungar Purpose
19 | PBR | KSD-I | Malia | Bullock (2 Nos.) - Harilal Thakarshi Bhoot | 2007-07-03 |  |  |  |  | 1 | Conductor Snapped
20 | PBR | PBR (O&M) | Kutiyana | Buffalo - Jinabhai Ranabhai Rathod | 2007-07-03 |  |  |  |  | 1 | Leakage Current
21 | PBR | KSD-II | Madhavpur | Buffalo - Tulsibhai Nanabhai | 2007-07-05 |  |  |  |  | 1 | Conductor Snapped | NA | NA
22 | PBR | PBR (O&M) | Coastal | Rambhai N. Ranavaya | 2007-07-07 |  | 1 |  |  |  | Non Fatal Mechnical Accidentl Occured At Time Of Maintenance Of Dist. Transformer Due To Self Unbalancing
23 | PBR | KSD-I | KSD-R-1 | Buffalow (2 Nos.) - 1. Ram Govind Bhuva 2. Mandan Devdan Herbha | 2007-07-08 |  |  |  |  | 1 | Conductor Snapped
24 | PBR | PBR (City) | PBR City | Nilesh Chandrakant Pandya | 2007-07-21 |  | 1 |  |  |  | Non Fatal Mechinical Accident Occurred To Departmental Person (Applm) Sliping Of Lags While Handing Over Tools To Lineman At The Time Of Climbing Of Psc Poles
25 | PBR | PBR (O&M) | Bagvadar | Shantiben Ranavaya | 2007-07-21 |  |  | 1 |  |  | Fatal Human Accident (Os) Occurred In Her Premises At The Time Of Using Own Electrical Applincies (Valona)
26 | PBR | KSD-II | Mangrol® | Dhansukh Ramji Vaja | 2007-07-22 |  |  | 1 |  |  | Fatal Accident Occurred To Os On Account Of Leackage Current In Private Premises Victim Came In To Contact With Leackage Area | NA | NA
27 | PBR | KSD-I | KSD-R-1 | Buffalo - Kanaksinh Ranbir Dodia | 2007-07-22 |  |  |  |  | 1 | Conductor Snapped
28 | PBR | PBR (O&M) | Bagvadar | Vinja Ranmal Chellar | 2007-07-28 |  |  |  | 1 |  | Leakage Current
29 | PBR | PBR (O&M) | Bagvadar | Bullock - Vinja Ranmal | 2007-07-28 |  |  |  |  | 1 | Leakage Current
30 | PBR | PBR (City) | PBR City | Bullock-Shri Deva parbat Kodiyatar | 2007-08-23 |  |  |  |  | 1 | Leakage Current
31 | PBR | KSD-II | Madhavpur | Kanajibhai M. Chamadiya | 2007-08-05 | 1 |  |  |  |  | BY mistake SBO switch "ON" Pata JGY Feeder on which victim was working after taking line clear.
32 | PBR | KSD-II | Chorwad | Bullock-Haji Gani Dosa Tawani | 2007-08-12 |  |  |  |  | 1 | LT Conductor Snapped
33 | PBR | KSD-II | Chorwad | Bufallow-Nagaji Naran | 2007-08-22 |  |  |  |  | 1 | LT Conductor Snapped
34 | PBR | PBR (O&M) | Ranavav | Manoj Rameshchandra | 2007-08-04 |  |  | 1 |  |  | Accident occurred due to defective wiring in private premises
35 | PBR | PBR (O&M) | Kutiyana | Shri Babulal Ravjibhai Tank | 2007-08-04 |  | 1 |  |  |  | while making "ON" 11 KV AB Switch, one bare strand of Cable wire damaged handgloves and current passes through palm.
36 | PBR | PBR (O&M) | Ranavav | Cow-Sh. Bharat Arfeb Karavadara | 2007-08-07 |  |  |  |  | 1 | Leakage Current
37 | PBR | PBR (O&M) | Ranavav | Buffalow-Sh. Vishal Lakha Kodiyatar | 2007-08-09 |  |  |  |  | 1 | LT Pole of village TC tillted , buffalow came in to contact with live wire
38 | PBR | PBR (O&M) | Coastal | Govindbhai Rajshibhai Solanki | 2007-08-10 |  |  | 1 |  |  | Fatal Accident Due To Snapping Of Lt Conductor At Village Miyani
39 | PBR | PBR (O&M) | Ranavav | Bufallow-Sh. Ruda Parbat Mori | 2007-08-10 |  |  |  |  | 1 | LT Pole tillted , buffalow came in to contact with live wire
40 | PBR | PBR (O&M) | Ranavav | Buffallow-Sh. Duda Karshan Odedara | 2007-08-10 |  |  |  |  | 1 | Leakage Current
41 | PBR | PBR (O&M) | Coastal | Smt. Jethiben Bhikhabhai Odedara | 2007-08-11 |  |  | 1 |  |  | Fatal Accident Due To Snapping Of Lt Conductor At Village Navagam
42 | PBR | PBR (O&M) | Coastal | Buffalow-Sh. Bhimbhai Menand Modhavadiya | 2007-08-11 |  |  |  |  | 1 | Leakage Current
43 | PBR | PBR (O&M) | Kutiyana | Bullock-Savdas Govind Bheda | 2007-08-21 |  |  |  |  | 1 | Leakage Current
44 | PBR | KSD-I | KSD-R-1 | Buffalow-Mansing Jivabhai Dodiya | 2007-08-04 |  |  |  |  | 1 | Leakage Current
45 | PBR | KSD-I | Malia | Buffalow-Harsukh Oghadbhai | 2007-08-07 |  |  |  |  | 1 | Leakage Current
46 | PBR | KSD-I | KSD-R-2 | Buffalow-Natha Bhaga Chavda | 2007-08-06 |  |  |  |  | 1 | Leakage Current
47 | PBR | KSD-I | Malia | Buffalow-Karsan Ruda | 2007-08-10 |  |  |  |  | 1 | Leakage Current
48 | PBR | PBR (O&M) | Coastal | Sheep (7 Nos.) - Lakha Parbat Mori | 2007-08-31 |  |  |  |  | 1 | Snapping Of Conductor
49 | PBR | KSD-I | KSD-R-1 | Bullok- Sh. Rama Bhikha | 2007-09-01 |  |  |  |  | 1 | Leakage Current
50 | PBR | KSD-I | KSD-R-1 | Buffalo-Sh. Mukesh Rata Jafara | 2007-09-01 |  |  |  |  | 1 | Snapping Of LT Conductor
51 | PBR | KSD-I | KSD-R-1 | Bullock- Sh. Bhima Vala Solanki | 2007-09-02 |  |  |  |  | 1 | Leakage Current
52 | PBR | KSD-I | KSD-R-1 | Bullock-Rambhai Karnabhai Dangar | 2007-09-11 |  |  |  |  | 1 | Leakage Current
53 | PBR | PBR (O&M) | Ranavav | Buffalo - Sh. Lakhaman Rana Odedara | 2007-09-21 |  |  |  |  | 1 | Leakage Current in earthing
54 | PBR | PBR (O&M) | Ranavav | Buffalo- Sh. Dhana Bhikhu Kodiyatar | 2007-09-22 |  |  |  |  | 1 | Snapping Of LT Conductor
55 | PBR | PBR (O&M) | Ranavav | Buffalo - Sh. Deva jetha Kodiyatar | 2007-09-24 |  |  |  |  | 1 | Leakage Current in load side wiring of Temp. Connection.
56 | PBR | PBR (O&M) | Coastal | Sh. Budhiya Khandu Thakare | 2007-09-27 |  |  | 1 |  |  | Insulation open in consumer's load side wiring. Victim may came in contcat with bare wire electrocuted.
57 | PBR | Keshod-II | Chorwad | Buffalo- Sh. Ramsinh Uka Barad | 2007-09-27 |  |  |  |  | 1 | Leakage Current
58 | PBR | PBR (City) | PBR (City) | Sh. Savajibhai Govindbhai Gadher | 2007-09-27 |  |  | 1 |  |  | accident occurred to Load side of the consumer switch board was as electrical motor was shot circuted the victim came in contact with said shot circuted switch board and got electrotuted
59 | PBR | PBR (O&M) | Ranavav | Sh. Karabhai Gigabhai Godhania | 14/10/07 |  |  | 1 |  |  | In victim's shop STD/PCO printer was short and that printer thouched to freeze hence current flow through body of freeze i.e. freeze short (As there is no any earthing of freeze) and victim touched the freeze and electrocuted.
60 | PBR | KSD-I | KeshodR-1 | Bullock-Shri Bharatbhai Haribhai Goriya | 24/10/07 |  |  |  |  | 1 | Leakage Current
61 | PBR | KSD-II | Mangrol (T) | Sh. B. B. Garchar | 26/10/07 |  | 1 |  |  |  | Telephonically line clear taken by Lineman of 11 KV Dudh talawadi Ag. Dom Feeder for repairing of TC lugs. By mistake 66 KV Mangrol S/S (GETCO) staff has taken out trolly of 11 KV Datar Manzil Ag. Dom. Feeder. Sh. B. B. Garchar (Victim) came in to contac
62 | PBR | PBR (O&M) | Bantwa | Harsur Lakhman Dangar -- Outsider Human | 30.10.07 |  |  | 1 |  |  | Existing Tatkal Connection of shri Harsur Lakhman Danger in vithal ruda mendapara AG group, As per letter of Police department on date 2/11/07 Site visit by DE Bantwa and investigate no any leakage current found in our installation but as per report of e
63 | PBR | KSD-I | Keshod(T) | 3 Nos. Cow --- 2 nos. of shri Narandas Gandhi Gaushala 1nd 1 no. Rovery | 06.11.07 |  |  |  |  | 1 | Due to Rain and wind pressure, L.T Line conductor snapped. All 3 nos Cow came in contact with live wire and electrocuted
64 | PBR | PBR(CITY) | Udyognagar | Out Sider Human - Jaynarayan Shukala | 05.11.07 |  |  | 1 |  |  | Accident occurred while reparing the single phase motor by victim in his premises.
65 | PBR | PBR(O&M) | Coastal | 3 Nos. Cow- 1). Shri Jaga Raja Shamla, 2). Shri Rama Gova Kodiyatar 3). Shri Kisa Bhikha Makwana | 17.11.07 |  |  |  |  | 1 | Due to failure of 11 KV Pin Insulator, 11 KV Conductor Snapped.
66 | PBR | Keshod-1 | Keshod(T) | Out Sider Human - Shri Dhirubhai Mavjibhai (Bhikhabhai) Pipaliya | 19.11.07 |  |  | 1 |  |  | Diring Checking of 3 Phase Power Supply in Kit Kat Fuse by victim in his Private Premises (Agriculture Installation)
67 | PBR | PBR(O&M) | Bagvadar | Departmental - Person - Shri Jagdish M. Vasava - Helper -- Age 40 Years | 22.11.07 |  | 1 |  |  |  | Mechanical Accident Occurred to him due to broken down of LT Psc Pole.
68 | PBR | Keshod-1 | KeshodR-2 | Out Sider Human - Shri Nalinbhai Parshotam Gajera (Age Approx.:- 34 Years) | 24.11.07 |  |  | 1 |  |  | Diring Checking of Power Supply in Kit Kat Fuse by victim in his Private Premises (Agriculture Installation)
69 | PBR | PBR(O&M) | Ranavav | Buffalo - of Shri Bhima Foga Khunti at Village Adityana | 12.12.07 |  |  |  |  | 1 | Leakage Current
70 | PBR | Keshod-1 | Malia | Buffalo of Shri Vikram Rambhai at Village Malia Hatina | 08.01.08 |  |  |  |  | 1 | Leakage Current
71 | PBR | PBR(O&M) | Bagvadar | Outsider Human - Shri Safeb Raja Odedara at Village Bhetakadi | 21.11.07 Reported by EE(O&M) on dated 08.01.08 |  |  | 1 |  |  | Un- Authorised work on Live LT Line by Victim
1 | JMN | kmbl | Bhatia | A Bullock | 2007-04-11 | - | - |  |  | 1 | Due to snapping of neutral conductor from 'c' clamp the conductor falls on bullock and acci. occurred.
2 | JMN | City-2 | Rural S/dn | Shri S.V.Solanki | 2007-05-08 | - | 1 |  |  |  | Burnt 11 kv jumper touched to nearby live 11 kv line due to heavy wind.
3 | JMN | City-1 | Sat Rasta | A Bullock | 2007-05-20 | - | - |  |  | 1 | Leakage current flows, buffalo came in contact with live wire & accident occurred.
4 | JMN | City-2 | Sikka | Goat | 2007-05-20 | - | - |  |  | 1 | Due to Snapping of LT conductor, accident occurred.
5 | JMN | rural | J.J.(E) | A Bullock | 2007-06-01 | - | - |  |  | 1 | Due to Snapping of LT conductor, accident occurred
6 | JMN | rural | Lalpur | Jayantibhai Pithadbhai Chavda | 03.06.07 | - | 1 |  |  |  | During the repairing work on electrical line the deteriorated v-cross arm, clamp broken & victim lost his balance from pole & fall down to earth
7 | JMN | kmbl | Kmbl(T) | Rasiklal Damji | 2007-06-04 | - | - | 1 |  |  | While curing on newly constructed house, victim came in contact with LT line passing above the house ceiling due to wet surface
8 | JMN | City-2 | Ind | A Bullock | 05.06.07 | - | - |  |  | 1 | Due to the fault in 70 mm2 cable which was tied with top angle, leakage current flow through girder pole and earth wire.
9 | JMN | City-2 | Ind | Two Cows | 05.06.07 | - | - |  |  | 1 | Due to heavy wind and rain live joints of service came in contact with connection and leakage current passed through metal fuse box and victim came in contact with stay of girder pole and accident occurred
10 | JMN | rural | Lalpur | Nalinbhai R.Chauhan | 07.06.07 | - | 1 |  |  |  | Made mistake in isolating the line during maintenance work on 11 kv Arikhana feeder he isolated 11 kv Gafeba feeder instead of 11kv Arikhana feeder
11 | JMN | City-1 | Hapa | Shri Haribhai & Smt. Nathiben | 07.06.07 | - | - | 1 |  |  | While unknown vehicle passes under the HT line it pulled & damage the line, there by reducing clearance between ground and 11kv wire. During this period, bullock cart has also passed beneath the line and while passing has touched 11kv line & accident occu
12 | JMN | City-1 | Hapa | Two Bullock | 2007-06-07 | - | - |  |  | 1
13 | JMN | City-1 | Sat Rasta | A Cow | 2007-06-16 | - | - |  |  | 1 | Due to falling of tree on LT line, conductor snapped.
14 | JMN | City-1 | Hapa | Shri Mamta Vijaybhai | 19.06.07 | - | - | 1 |  |  | Direct wire tapped by Ashoksinh from LT line, the joint of unauthorized wire touches with fencing of Ag. farm while playing victim she touches with fancying wire and accident occurred
15 | JMN | kmbl | Dwarka | Aanandi Dhanjibhai | 20.06.07 | - | - |  | 1 |  | Due to defective internal house wiring, victim got electric shock
16 | JMN | rural | Lalpur | A Buffalo | 21.06.07 | - | - |  |  | 1 | One phase-wire was broken at a place where cable comes out from dist-Box, Buffalo came in contact with that T/C and accident occurred.
17 | JMN | City-2 | Sikka | A Cow | 21.06.07 | - | - |  |  | 1 | A cow passed near broken conductor and touched and accident occurred
18 | JMN | rural | Kld(E) | A Bullock | 23.06.07 | - | - |  |  | 1 | LT conductor snapped. Bullock came in contact with conductor and accident occurred
19 | JMN | City-2 | Sikka | A Bullock & A Calf | 23.06.07 | - | - |  |  | 1 | Snapping of LT conductor
20 | JMN | kmbl | Bhanvad | A Bullock | 24.06.07 | - | - |  |  | 1 | From Transformer bushing neutral lug found disconnected and due to same leakage current flow in earthing wire
21 | JMN | rural | Kld(E) | Bharatsinh | 26.06.07 | - | - | 1 |  |  | While giving jumper on 11 kV line after completion of line work, the victim got shock on 11 kv line
22 | JMN | City-2 | Rural | Mahesh Trikambhai Bhadra | 28.06.07 | - | - | 1 |  |  | Due to snapping of LT conductor accident occurred
23 | JMN | kmbl | Okha | A Buffalo | 03.07.07 |  |  |  |  | 1 | Leakage of TC earthing
24 | JMN | City-2 | Rural | Two Buffalo | 05.07.07 |  |  |  |  | 1 | Damage of LT line due to heavy rain and accd. Occurred.
25 | JMN | City-2 | Sikka | A Buffalo | 05.07.07 |  |  |  |  | 1 | Snapping of LT conductor
26 | JMN | City-2 | Sikka | febvi Bharatbhai | 05.07.07 |  |  | 1 |  |  | Snapping of LT conductor
27 | JMN | kmbl | Kalyanpur | A Bullock | 09.07.07 |  |  |  |  | 1 | Snapping of LT conductor
28 | JMN | kmbl | Bhanvad | Ramesh Kana | 09.07.07 |  |  | 1 |  |  | Snapping of LT conductor
29 | JMN | kmbl | Rural | Kababhai Rajsinh | 11.07.07 |  |  | 1 |  |  | Victim climbed on live LT line at his own wish and met with fatal accd.
30 | JMN | City-1 | HT | Atul Bhagvanji Kapuria | 14.07.07 |  |  |  | 1 |  | While touching to 11 kv line from extended Gallery on Road from Building.
31 | JMN | kmbl | Kalyanpur | Hardasbhai Rabari | 14.07.07 |  |  | 1 |  |  | Victim has tried to take unauthorized power supply from existing overhead village L.T. line.
32 | JMN | rural | Kalavad(E) | N.K.Jadeja | 20.07.07 |  | 1 |  |  |  | Mechanical Accident.
33 | JMN | kmbl | Dwarka | A Bullock | 24.07.07 |  |  |  |  | 1 | Snapping of LT conductor
34 | JMN | City-2 | Kmbl Gate | Yunus Dosa | 25.07.07 |  |  | 1 |  |  | Supprot GI wire connected between LT pole and street light fixture fixed on private premises, was came in contact with live phase junction on LT Pole, consequently leakage current passed through said GI wire.Thus electrocution was took place when victim c
35 | JMN | City-1 | Hapa | A Buffalo | 31.07.07 |  |  |  |  | 1 | Snapping of LT conductor
36 | JMN | rural | Lalpur | A Buffalo | 31.07.07 |  |  |  |  | 1 | Earthing is not provide proper, hence leakage flows from earth to earth. When she buffalo came in contact with earth surface and accd. Occurred.
37 | JMN | Rural | Jodia/Rural | Uttam Savji Dudhagara | 01.08.07 |  |  | 1 |  |  | There is no anyposibility of electrical accident.
38 | JMN | kmbl | Bhatia S/dn./Kmbl | Shri Ghanshyam K. Solanki | 02.08.07 |  | 1 |  |  |  | for the operation of GO switch while climbing on 11 kv pole, the victim slipped and fall down mechanical accident.
39 | JMN | kmbl | Bhatia S/dn./Kmbl | Umeshbhai N.Manek | 04.08.07 |  |  | 1 |  |  | The building was constructed Nr. LT line and clearance not maintained while victim climbed on tarace for some work, came in contact with live LT line & accd. Occurred.
40 | JMN | rural | Kld(E)/Jam®dn. | A Cow | 07.08.07 |  |  |  |  | 1 | Due to unbinding of live phase wire from shackle ins. & touching with c-clamp. As it is rainy season whole pole was completely wet and thus pole was shorted. Cow came in contact with the pole and got ele. Shock.
41 | JMN | City-I | Ptl S/dn./City Dn. | A Buffalo | 09.08.07 |  |  |  |  | 1 | A Buffalo was shocked due to transformer's leakage current of neatural earthing.
42 | JMN | rural | J.J'pur(E)/Rural | Shri Arvind Chakubhai | 10.08.07 |  |  | 1 |  |  | while repairing tapping 11 kv line privately way. Victim fall from the pole and died due to hamerage.
43 | JMN | kmbl | Bhatia/Kmbl | A Buffalo | 10.08.07 |  |  |  |  | 1 | Phase cond. binding with sheckle insulator was loosen and conductor touches to angle of pole. Water is surrounded to pole as the buffalo fall in water it electrolucted.
44 | JMN | rural | Dhrol S/dn./Rural dn. | A Buffalo | 10.08.07 |  |  |  |  | 1 | T/C was surrounded by water due to leakage current from LT dist.Box as buffalo fall in water it electrolucted.
45 | JMN | kmbl | Kmbl(R)/Kmbl. | Smt. Manjuben Karubhai Mokaria | 12.08.07 |  |  | 1 |  |  | Due to heavy wind, and rain binding of LT shackle insulator broken and LT live phase conductor touched PSC pole due to which leakage current was passing through earthing wire and victim came in contact with earthing wire and met with accd.
46 | JMN | kmbl | Bhatia/Kmbl | A Bullock | 12.08.07 |  |  |  |  | 1 | fault the cable touches the angle of LT line pole and through angle earthwire energized and as bullock came in contact with pole , accd. Occurred.
47 | JMN | kmbl | Kmbl(R)/Kmbl. | A Buffalo | 13.08.07 |  |  |  |  | 1 | Due to T/C body leakage current passed to earthing wire and animal came in contact with wire of transformer body.
48 | JMN | kmbl | Bhatia/Kmbl | A Buffalo | 14.08.07 |  |  |  |  | 1 | The LT phase conductor loosen from shackle binding it touches cross arm and thus pole earthwire energized while buffalo came in contact with pole earthwire and accd. Occurred.
49 | JMN | kmbl | Kmbl(R)/Kmbl. | Smt. Valiben Karsanbhai Chuchhar | 14.08.07 |  |  | 1 |  |  | Due to breaking of shackle insulator, of LT line pole due to rain and wi9nd presence LT line conductor fall down from pole to ground level. The victim came in contact with this LT conductor and accd. Occurred.
50 | JMN | kmbl | Kmbl(R)/Kmbl. | She Buffalo | 15.08.07 |  |  |  |  | 1 | LT phase wire Ag. Line broken and snapped. Buffalo came in contact with snapped cond. And met with accident.
51 | JMN | rural | Kld(E)/Rural | A Bullock | 16.08.07 |  |  |  |  | 1 | while bullock coming back after drinking from river, it came in contact with live LT wire which were laying on earth due to broken pole by heavy rain and flood. Got ele. Shock and accd. Occurred.
52 | JMN | rural | Kld(E)/Rural | A Buffalo | 16.08.07 |  |  |  |  | 1 | while buffalo was grazing near bank of small river, it came in contact with live LT wire which were laying on earth due to broken pole by heavy rain and flood.
53 | JMN | City-II | Rural S/dn/City-2 | A Buffalo | 16.08.07 |  |  |  |  | 1 | Snappinf of LT conductor
54 | JMN | kmbl | Okha/Kmbl | A Camel | 16.08.07 |  |  |  |  | 1 | Due to heavy rain pole slipped and bend 11 kv line from foundation and hence clearance between ground and conductor reduces as the camel came in contact with wire and accd. Occurred.
55 | JMN | kmbl | Kmbl(T)S/dn./Kmbl | Shri D.D.Parmar | 17.08.07 |  | 1 |  |  |  | The victim was alloted to attend the complain of Jalin Petrol pump while attending the complain on transformer , LT line side the victim came in vicinity of HT line passing above LT line and electrocuted and fall from T/C.
56 | JMN | City-II | Rural S/dn/City-2 | Shri Ahir R.J. | 21.08.07 |  |  |  | 1 |  | Due to heavy rain the pole was fall down and the live LT wires were fall on the victim she
57 | JMN | kmbl | Bhatia/Kmbl | A Buffalo | 22.08.07 |  |  |  |  | 1 | Due to leakage of LT wire and earth wire, buffalo came in contact with leakage wire and got shocked.
58 | JMN | rural | Kld(E)/Rural | Shri Samji Valji Vasoya | 23.08.07 |  |  | 1 |  |  | Internal wiring fault at consumer's premises.
59 | JMN | City-II | Rural/City-II | A Buffalo | 23.08.07 |  |  |  |  | 1 | Due to T/C body leakage current passed to earthing wire and animal came in contact with wire of transformer body.
60 | JMN | kmbl | Dwarka/ Khambhalia | A Buffalo | 24.08.07 |  |  |  |  | 1 | Snapping of LT Conductor.
61 | JMN | City-II | Sikka/City-II | A Buffalo | 25.08.07 |  |  |  |  | 1 | Due to leakage of earth wire buffalo came in contact with earth wire and accd. Occurred.
62 | JMN | City-II | Sikka/City-II | (1)Uttamshinh, (2) Raijibhai | 25.08.07 |  |  |  | 1 |  | Due to heavy rain and wind pin H/W of D.P. touch to other JGY pipali feeder and both are getting shock.
63 | JMN | kmbl | Bhatia/Kmbl | Kanabhai Rajabhai Odedara | 26.08.07 |  |  | 1 |  |  | suspected case of electrical accident. The victim was covering the material of truck parked under 11 kv line. He might have come in visinity of line and fall down from truck.
64 | JMN | rural | J.J(E)/Rural | A Buffalo | 28.08.07 |  |  |  |  | 1 | Due to leakage current of T/C earthing, buffalo came in contact with wire and accd. Occurred.
65 | JMN | rural | Dhrol S/dn./Rural dn. | Lakhman Keshavji Mungra | 28.08.07 |  |  | 1 |  |  | Internal wiring fault at consumer's premises.
66 | JMN | City-II | Rural/City-II | A Buffalo | 28.08.07 |  |  |  |  | 1 | Snapping of HT line buffalo came in contact with wire and accd. Occurred.
67 | JMN | City-I | Ptl S/dn./City Dn. | A Cow | 29.08.07 |  |  |  |  | 1 | cable shorted, leakage current pass through earthing wire, cow came in contact with leakage wire accd. Occurred.
68 | JMN | rural | Kld(E) | A Bullock | 05.09.07 |  |  |  |  | 1 | Snapping of LT conductor
69 | JMN | kmbl | Dwarka | 3 nos. of Buffalo | 05.09.07 |  |  |  |  | 1 | illegally Power tapped from an unauthorised persons through bambu & cable system, as the buffalo rubbed,its body with pole,its body came in contact with illegally tapped cable & Electrolux
70 | JMN | kmbl | Kalyanpur | Ramde Jaga Bhadarka | 08.09.07 |  |  | 1 |  |  | in the premise of victim, when victim goes to start hils ele. Motor at open covered starter, in a room, one phase comes in contact with fingers of the hand and he got ele. Shocked.
71 | JMN | City-II | Sikka | Two Cows | 08.09.07 |  |  |  |  | 1 | Snapping of LT Conductor
72 | JMN | kmbl | Bhanvad | Buffalo | 14.09.07 |  |  |  |  | 1 | Snapping of LT Conductor
73 | JMN | City-II | Rural S/dn | An ox | 15.09.07 |  |  |  |  | 1 | Snapping of LT Conductor
74 | JMN | City-II | Sikka | A Buffalo | 25.09.07 |  |  |  |  | 1 | Earthing leakage of T/C.Water was surrounded by T/C and as Buffalo fall in water it Electro lux
75 | JMN | kmbl | Kmbk® | A Bufflao | 27.09.07 |  |  |  |  | 1 | Leakage current drawn in GI earth wire, buffalo came in contact with wire & accd. Occurred.
76 | JMN | Rural | J.J.(E) | Dipak Ramji | 28.09.07 |  |  |  | 1 |  | While isolating G.O switch forT/C replacement, switch goes to earth and fire arc took place and acc. Occurred.
77 | JMN | Rural | J.J. | Two Buffalo | 29.09.07 |  |  |  |  | 1 | due to line fault 11 kv power flow in earthing as the land was wet and 2 nos buffalo were in water nearby above pole then electrolux.
78 | JMN | Rural | Lalpur | An ox | 29.09.07 |  |  |  |  | 1 | Snapping of LT Conductor
79 | JMN | rural | Lalpur | An ox | 02.10.07 |  |  |  |  | 1 | Snapping of LT conductor
80 | JMN | kmbl | Bhatia | A Cow | 07.10.07 |  |  |  |  | 1 | Snapping of LT conductor
81 | JMN | kmbl | Kmbl(R)/Kmbl. | Kariben Dhanabhai Gamar | 12.10.07 |  |  | 1 |  |  | Victim climbing for green tree cutting at village sutaria. An overhead 11 kv mota gunda ag feeder passing over the above neem tree. Due to that victim touches the live conductor of the 11 kv line. Hence, electric shock passing through her body and died at
82 | JMN | City-I | Hapa S/Dn./City-1 | A Buffalo | 24.10.07 |  |  |  |  | 1 | Snapping of LT conductor
83 | JMN | kmbl | Kmbl(R)/Kmbl. | Jodhabhai Karabhai | 27.10.07 |  |  | 1 |  |  | Victim touches live conductor of inclined LT line conductor hence electric current passes through the body of the boy and died at that time.
84 | JMN | kmbl | Kmbl(R)/Kmbl. | 5 nos.of buffalo | 27.10.07 |  |  |  |  | 1 | A Buffalo came for drinking water in lake after drinking water buffalo passed nearby land due to that buffalo touches live conductor of inclined LT line and accd. Occurred.
85 | JMN | City-I | Hapa S/Dn./City-1 | A Buffalo | 27.10.07 |  |  |  |  | 1 | Snapping of LT conductor
86 | JMN | City-I | Hapa S/Dn./City-1 | Rajesh Balvant Khat | 30.10.07 |  |  |  | 1 |  | Erection of Ag group for road crossing instead of 11 kv nagarsim feeder L/C asked/ issued for vijarkhi feeder hence victim got ele.shock(explanation asked from concern.)
87 | JMN | Kmbl | Kalyanpur | Jethiben Arfebbhai Khandhar | 05.11.07 |  |  |  | 1 |  | At the time of accident flow was single phasing and snapped cond. Was not live but the victim got ele. Shock due to induction of power in snapped cond.
88 | JMN | Rural | Kld.(E) | 4 nos. of Goats | 07.11.07 |  |  |  |  | 1 | Breakage of LT conductor from circuit pole. Mischief made by unknown person by cutting another side of broken conductor which was touching the live wire, goat came in contact with live wire & accd. Occurred.
89 | JMN | Kmbl | Bhanvad | Shri Nahim | 09.11.07 |  |  | 1 |  |  | A Fisherman named Nahim died when 11 kv conductor snapped on a boat in river Triveni Bhanvad.
90 | JMN | Kmbl | Dwarka | A Camel | 10.11.07 |  |  |  |  | 1
91 | JMN | Rural | J.J.(E) | A Buffalo | 19.11.07 |  |  |  |  | 1
92 | JMN | Rural | Kalavad(E) | Smt Kasurben Samsurbhai | 6.12.07 |  |  | 1 |  |  | Motor switch was foud opened during inspection in private premises
93 | JMN | Rural | Kalavad(E) | J B Damor | 5.1.08 |  | 1 |  |  |  | During the repalacement work of service wire on PSC pole, while stringing G.I.wire,victim lost his balance from pole & fall down to earth
94 | JMN | kmbl | Kalyanpur | Lakhman Devsi Gorania | 13.1.08 |  |  |  | 1 |  | Victim by self work to check power in kit-kat fuse of T/C and by mistake his hand touch accidentally live phase of kit-kat fuse and accident occurred
94 | JMN | City-1 | HT | Shri Jayrajsinh Vijaysinh | 14.01.08 |  |  |  | 1
95 | JMN | Kmbl | Kalyanpur | Shri Manishaben Keshubhai Solanki | 04.02.08 |  |  | 1 |  |  | In her home, victim was making tea in vessal on hot plate that time flow of tea occurred and she touch the vessal and she got electric shock & accident took place.
96 | JMN | kmbl | Bhatia | A Cow | 07.02.08 |  |  |  |  | 1 | Due to one current leading to breaking of coductor, which fall on cow & accd. Occurred.
97 | JMN | City-II | Rural | A Buffalo | 16.02.08 |  |  |  |  | 1 | Snapping of Conductor
98 | JMN | City-II | Sikka | Shri Nathabhai Karabhai Karamata | 21.02.08 |  |  | 1 |  |  | While cutting tree branches for food of his animals with the help of iron Rod, he came in contact with 11 kv phase wire through that rod and electrolux and died.
100 | JMN | Rural | JJ(W) | 3-nos. of Bufffalo | 01.03.08 |  |  |  |  | 1 | Snapping of Conductor
101 | JMN | kmbl | Bhatia | Ullasba Jayendra Sinh Jadeja | 03.03.09 |  |  | 1 |  |  | Victim was trying to start house floormill & accidently got electric shock
1 | BHJ | Anjar | Anjar® | Babu jesang Khungal | 2007-04-04 |  | 1 |  |  |  | Mechanical accident, fall down from Pole
2 | BHJ | Mandvi | Mundra | V.P.Siyani | 06.4.07 |  |  | 1 |  |  | Came in contact with live HT line
3 | BHJ | G'DHAM | Adipur | Nitin Arafebdas Kapta | 09.04.07 |  |  |  | 1 |  | Snapped cond. Lying on road victim on motorcycle, he applied the breaks & slipped. | NA | snapped cond. Joined
4 | BHJ | Bhuj | NAKHATRANA | RAJESH NARSHI NUT | 25/06/2007 | - | - | 1 | - | - | Due to heavy wind pressure tree branch Fall down on L.T. circuit,phase & neutral short circuited & conductor snapped on the victim, resulted into fatal accident | Not Applicable | Not Applicable
5 | BHJ | Bhuj | NAKHATRANA | COW | [5 empty] | 1 | Snapping of Conductor | Not Applicable | Not Applicable
6 | BHJ | Bhuj | BHUJ CITY-2 | COW | 26/06/07 |  |  |  |  | 1 | Leakage current flow through trans.center earthing | Not Applicable | Not Applicable
7 | BHJ | Anjar | Rapar | Cow & Ox | 2007-06-05 |  |  |  |  | 1 | May be induction with girder Pole
8 | BHJ | Anjar | Rapar | Savjibhai P Bhutak | 2007-06-12 |  |  | 1 |  |  | Reparing service line on the Pole
9 | BHJ | Anjar | Anjar® | Manjulaben P Goyal | 2007-06-12 |  |  | 1 |  |  | Private Premises(In Bathroom came in contact with wet switch Board
10 | BHJ | Mandvi | Mandvi(T) | Mukesh Meghji Marvada | 07.06.07 |  |  | 1 |  |  | He was trying to cut the earth wire of LST and got shock and died.
11 | BHJ | Mandvi | Mandvi(T) | Ajmal K.Maheshwari | 26.6.07 |  |  |  | 1 |  | Victim climbed on pole and caught the live LT line to attend the private complaint fell down and non fatal accident occured.
12 | BHJ | Mandvi | Kothara | Calf | 23.06.07 |  |  |  |  | 1 | Due to heavy wind pressure & rain there is leakage current passes through earth wire of transformer centre the calf passes near the t/c came in contact with earth wire resulted into fatal accident
13 | BHJ | Mandvi | Dahinsara | Two Cow | 26.06.07 |  |  |  |  | 1 | Due to Disk fault current pass through earthing wire.
14 | BHJ | G'DHAM | Gandidham | G. D. Chavda (Lineman) | 13.06.07 |  | 1 |  |  |  | Attending the service line on roof Loosing his balance & slipped | YES | concern instructed to follow safety rules
15 | BHJ | G'DHAM | Adipur | Kamal Jagdish Dagad | 26.06.07 |  |  | 1 |  |  | Victim climbed on overhighted truck Accidently coming in contact with 11kv line | NA | NA
16 | BHJ | BHUJ | BHUJ CITY-2 | FULCHAND DWARKAPRASAD | 2007-02-07 | - | - | 1 | - | - | The Victim had tied the string for drying wel clothes with the service support angle and due to bad climate condition and heavy rain fall, there was leakage of power in service suport angle.while removing wet clothes from the string,victim got electrocat | Not Applicable | Not Applicable
17 | BHJ | BHUJ | DESHALPAR | ALPESH K. SAGARPUTRA | 16/07/07 |  | 1 |  |  |  | Line staff was carring out LT line maint. Agter switching off LT supply.Single LT wire of dead span at HT line crossing came in contact with HT line, which resulted into Non Fatal Accident. | Utilised | Not Applicable
18 | BHJ | BHUJ | NAKHATRANA | HUSSAIN SIDDIK | 20/07/07 |  |  | 1 |  |  | While the victim was removing broken tree branch lying on 1 phase S/L in front yard of his house, the GI wire broken and one end of it came in contact with live L.T.line, the second end of GI wire was in contact with the victim, hense got electrocuted & r | Not Applicable | Not Applicable
19 | BHJ | BHUJ | BHUJ RURAL | SIDDIK SUMAR NODE | 22/07/07 |  |  | 1 |  |  | No any avidence is found, which lead to leakage of current resulted into accident. | Not Applicable | Not Applicable
20 | BHJ | BHUJ | Bhachau | Buffalo & Calf | 2007-07-01 |  |  |  |  | 1 | Due to snapping of conductor as Pin Blast
21 | BHJ | BHUJ | Anjar© | Bharat R Parmar | 2007-07-03 |  | 1 |  |  |  | Although lin was cleared power came in 11KV Line and victim fallen down from 11KV Girder Pole
22 | BHJ | BHUJ | Bhimasar | Ramehsbhai K Koli | 2007-07-08 |  |  | 1 |  |  | Taking direct power supply form existing LT Line
23 | BHJ | BHUJ | Anjar© | Pushpaben Dabhi | 2007-07-28 |  |  | 1 |  |  | Electrocuted by electric motor while sprinkling water to newly built house.(Pribvate Premises)
24 | BHJ | Mandvi | Dahinsara | C.N.Kharadi | 01.07.07 |  | 1 |  |  |  | carelessness of isolation in power
25 | BHJ | Mandvi | Mundra | 1-buffalow | 04.07.07 |  |  |  |  | 1 | conductor snapping
26 | BHJ | Mandvi | Dahinsara | 1-cow | 11.07.07 |  |  |  |  | 1 | conductor snapping
27 | BHJ | Mandvi | Kothara | Salemamad Osman Kunbhar | 22.07.07 |  |  | 1 |  |  | conductor snapping
28 | BHJ | Mandvi | Kothara | Manjulaben R.Dalit | 14.07.07 |  |  | 1 |  |  | accident took place in Private primises
29 | BHJ | Anjar | Anjar® | P. J. Kharadi | 20.8.07 |  | 1 |  |  |  | Victim fell down from LT pole while attending complain at vill. Sapeda | Yes | N.A.
30 | BHJ | Mandvi | Mandvi® | 1-buffalow | 01.08.07 |  |  |  |  | 1 | conductor snapping
31 | BHJ | Mandvi | Mandvi® | 4-cow and 2-calf | 05.08.07 |  |  |  |  | 6 | conductor snapping
32 | BHJ | Mandvi | Naliya | 1-cow | 02.08.07 |  |  |  |  | 1 | Leakage current
33 | BHJ | Mandvi | Mandvi(T) | 1-buffalow | 13.08.07 |  |  |  |  | 1 | conductor snapping
34 | BHJ | Mandvi | Naliya | Kirtikumar A.Patel | 25.08.07 | 1 |  |  |  |  | Without isolating the LT power he climbed on pole to repair jumper fault and died due to elecric shock. | No
35 | BHJ | Mandvi | Mundra | 1-buffalow | 29.08.07 |  |  |  |  | 1 | conductor snapping
36 | BHJ | Bhuj | Bhuj City-1 | Cow | 2007-03-08 |  |  |  |  | 1 | LT Conductor Snapping | Not Applicable | Not Applicable
37 | BHJ | Bhuj | Bhuj Rural | Buffallo | 25/08/07 |  |  |  |  | 2 | 11 KV Pole broken | Not Applicable | Not Applicable
38 | BHJ | Bhuj | Bhuj City-2 | Ali Asgar | 2007-07-08 | 0 | 0 | 1 | 0 | 0 | Defective appliances at consumer's premises | Not Applicable | Not Applicable
39 | BHJ | Anjar | Bhachau | Koli Ranchhod U | 2007-09-15 |  |  | 1 |  |  | A Trailor carrying logs of wood was passing on the road the rear side of the logs touch the LT Line pole. As a result the LT Pole fell down and the LT Line touch the victim | N.A. | Party has lodged FIR Against the driver of Trailor
40 | BHJ | Anjar | Bhimasar | Laxman Arfeb Parmar | 2007-09-24 |  |  |  | 1 |  | Due to heavy rain and wind pressure a very old PSC Pole broken down and victim passing nearby that pole got injured | N.A. | N.A.
41 | BHJ | Bhuj | Bhuj Rural | Cow | 2007-06-09 | 0 | 0 | 0 | 0 | 1 | Power leckage in earthing of TC center the cow came in contact of pole and get electrocuted and spot dead. | Not Applicable | Not Applicable
42 | BHJ | Bhuj | Nakhatrana | Cow | 20/09/07 | 0 | 0 | 0 | 0 | 2 | Due to Pin Insulator's fault 11 KV conductor of Jetavira feeder was stupped and fallen on two nos of cow passing under line and cowa got electrocuted and spot dead. | Not Applicable | Not Applicable
43 | BHJ | G'DHAM | Gandidham | Two cows | 23.09.07 |  |  |  |  | 1 | Due to snapping of B-phase of LT Line, the live wire come in contact of 2nos. Cows. | NA | LT cond. Replaced, losse jumpers replaced by the new.
44 | BHJ | Mandvi | Mundra | Two Buffelow | 24.09.07 |  |  |  |  | 2 | LT line of 11 KV Fdr is broken & two buffelows were came in contact with live LT wire | NA | LT span replaced & maint. Carried out
45 | BHJ | Mandvi | Mundra | Sajid Sadgu Khan | 24.09.07 | 0 |  | 1 |  |  | Trolly of Dumper touched to 11 KV Fdr & the men maintaning the gear box got shocked & died. | NA | NA
46 | BHJ | Anjar | Rapar | Mansukh B Sadhu | 2007-10-03 |  |  | 1 |  |  | Victim was covering the truck with tarpouline(Talpatri), while doing so he touch 11KV line and got electrocuted | N.A. | N.A.
47 | BHJ | BHUJ | Bhuj Rural | 3 nos of Buffalo | 2008-10-01 | 0 | 0 | 0 | 0 | 3 | 11 KV pole broken | NA | NA
48 | BHJ | G'DHAM | Adipur | Haresh N. Jethva | 08.02.08 |  | 1 |  |  |  | slipped from pole | YES
49 | BHJ | Anjar | Anjar-R | Shri Kantibhai V. Baria | 15.03.08 |  |  |  | 1 |  | Victim(Unauthorized person) was doing some illegal work on X'mer Centre and met with electrical accident. |  | Notice given to Victim & villagers has been warned for not do unauthorized and illegal work on lines & T/C
50 | BHJ | BHUJ | Bhuj Rural | Rajendra Trivedi | 2008-03-03 | 0 | 1 | 0 | 0 | 0 | While attending fault, on 11KV Medisar JGY feeder, person got electric sock. Due to tuching of 11 conductor of 11 KV sumarasar feeder to 11 KV Medisar JGY feeder. | Yes | NIL
51 | BHJ | BHUJ | Deshalpar | Viththal Mithu Maheshwari | 8.03.08 | 0 | 0 | 1 | 0 | 0 | Person was climed on tree branches & came in contact of live conductor | NIL | NIL
1 | JND | City Division | GIDC JND | Sh. Suresh Ravaji Chauhan | 2007-04-17 |  |  | 1 |  |  | In Private premises of Kiran Traders, The victim came in contact with the electric circuited iron roof which arranged by the factory holder to prevent theft of material. He got the shock and met with the fatal accident in premises of Kiran traders | Not Applicable | Not Applicable
2 | JND | Rural Division-1 | Bhesan | Sh. S.P.Joshi | 2007-04-04 |  | 1 |  |  |  | While taking details on TC. came in to induction zone | No | EE, Rural Divison-1 has been asked to inquire the victim
3 | JND | Rural Division-1 | Visavadar-2 | Sh. Ramesh Bhanubhai | 2007-04-04 |  |  | 1 |  |  | LT Line shock doubtful may be in private premises | Not Applicable | Not Applicable
4 | JND | Rural Division-1 | Junagadh(R) | Buffalo | 2007-04-12 |  |  |  |  | 1 | Due to leakage of current in TC Earthing | Not Applicable | Not Applicable
5 | JND | Rural Division-1 | Visavadar-1 | Sh.Babubhai Parbatbhai | 2007-04-18 |  |  |  | 1 |  | 11 KV DO Fuse operation with wet rod | No | Not Applicable
6 | JND | Veraval | Veraval Town | Anonymous Person | 2007-03-31 |  |  |  | 1 |  | Due to touching of live line while carrying out construction below live 11 KV line | Not Applicable | Not Applicable
7 | JND | Rural Division-1 | Bilkha | Ms. Nikita B Shapariya | 2007-05-03 |  |  | 1 |  |  | Come into the direct touch to live holder in private premises | Not Applicable | Not Applicable
8 | JND | Rural Division-1 | Visavadar-2 | Sh. Bhavesh M Trivedi (VS-HLP) | 2007-05-05 |  | 1 |  |  |  | Slipping from PSC pole mechanical accident | Safety Belt was not allocated | Not Applicable
9 | JND | Rural Division-1 | Bilkha | Sh. Bhagaram Banaram | 2007-05-09 |  |  |  | 1 |  | Electrocuted from another supply while working | Not Applicable(Unauthorized Operation by consumer) | Not Applicable
10 | JND | Rural Division-1 | Visavadar-2 | Sh. Gagjibhai Jinabahi | 2007-05-16 |  |  | 1 |  |  | In private premises while removing electric motor from bore well | Not Applicable | Not Applicable
11 | JND | Veraval | Veraval Town | Sh. Varshben M Goswami | 2007-05-02 |  |  | 1 |  |  | Accident is occurred in her premises when she was going to remove pin from plug. The live wire of the pin may come in contact with her & this accident may occurred | Not Applicable | Not Applicable
12 | JND | Veraval | Talala | Sh. Parshbhai Sigala & Sh. Mansukh M Kachhadiya | 2007-05-07 |  |  |  | 1 |  | Accident is occurred when they were working on TC for cabling work. | Not Applicable | Not Applicable
13 | JND | City Division | Central | Mrs. Shahina Iiyas Shekh | 2007-06-12 |  |  | 1 |  |  | The GI wire which is used to hang the wet clothes, that wire came into contact with the phase of load side wiring. The load side owner was too old and deterioted. So its insulation broke down and its phase came into contact with GI wire n current passed t | Not Applicable | Not Applicable
14 | JND | City Division | GIDC JND | Sh. Hardik Naran | 2007-06-23 |  |  |  | 1 |  | Accident occurred due to heavy rainfall with more wind pressure so that LT pole is tilted, hence the live phase was touched the guard wire and was earthed through pole earthing and at that time victim had touched the earthing lead and victim was electrocu | Not Applicable | Not Applicable
15 | JND | City Division | GIDC JND | Sh. Ashok Kishorchand | 2007-06-25 |  |  | 1 |  |  | Accident was occurred during laying of illegal wiring for un-authorized power taking from nearby house in private premises. | Not Applicable | Not Applicable
16 | JND | City Division | GIDC JND | Buffalo | 2007-06-08 |  |  |  |  | 1 | Accident was occurred due to snapping of LT conductors which was snapped due to frequently jumping of monkeys from nearby tree. | Not Applicable | Not Applicable
17 | JND | Rural Division-1 | Visavadar-2 | Sh. Kesubhai Gokalbhai | 2007-06-09 |  |  |  | 1 |  | Unauthorized climbing on pole on LT pole | Not Applicable | Not Applicable
18 | JND | Rural Division-1 | Visavadar-1 | Sh. Lalji Arfeb | 2007-06-11 |  |  |  | 1 |  | Due to leakage current of TC earthing | Not Applicable | Not Applicable
19 | JND | Rural Division-1 | Bhesan | Buffalo | 2007-06-22 |  |  |  |  | 1 | LT conductor snapped | Not Applicable | Not Applicable
20 | JND | Rural Division-1 | Junagadh(R) | Sh. D D Pandya (Helper) | 2007-06-25 |  | 1 |  |  |  | Leakage current in service line | Not Applicable | Not Applicable
21 | JND | Rural Division-1 | Junagadh(R) | Sh. M G Parmar (ALM) | 2007-06-25 |  | 1 |  |  |  | Mechanical NFA at the time of tree cutting in 11kV vadal feeder. | Not Applicable | Not Applicable
22 | JND | Rural Division-2 | Manavadar-2 | Smt. Manishaben Rajeshkumar Trambaliya | 2007-06-06 |  |  | 1 |  |  | A fatal accident occurred to Victim due to her wiring short circuit. | Not Applicable | Not Applicable
23 | JND | Rural Division-2 | Mendarda | Sh. Karsanbhai Mulubhai Vala | 2007-06-20 |  |  | 1 |  |  | A fatal accident occurred to victim when he is climbing the LT line on his own risk in the farm of Sh. Rambhai Safebbhai Gal | Not Applicable | Not Applicable
24 | JND | Rural Division-2 | Mendarda | Buffalo | 2007-06-23 |  |  |  |  | 1 | A fatal accident occurred to A buffalo at Vill: Mendarda due to leakage current of telephone galvanized pole & current pass nearby LT to a buffalo. | Not Applicable | Not Applicable
25 | JND | Veraval | Prabhas Patan | Buffalos | 2007-06-17 |  |  |  |  | 1 | Due to leakage of jumper in 11kV line | Not Applicable | Not Applicable
26 | JND | Veraval | GIDC VRL | Buffalo | 2007-06-21 |  |  |  |  | 1 | Due to leakage of current in TC DP | Not Applicable | Not Applicable
27 | JND | Veraval | Talala | Bullok | 2007-06-23 |  |  |  |  | 1 | This accident is occurred in railway premises. | Not Applicable | Not Applicable
28 | JND | City Division | GIDC JND | Mrs. Rekhaben Bharatbhai Lathiya | 2007-07-06 |  |  |  | 1 |  | The victim come in contact with steel stair rail which charged through short- defective ceiling fan of her neighbor of row houses with minor injury in private premises. | Not Applicable | Not Applicable
29 | JND | City Division | Satellite | Cow | 2007-06-26 |  |  |  |  | 1 | The 1Ø service line has jointed near at pole. The insulation of 1Ø service joints was rusted and broken and contacting with the supporting GI wire. Hence, the leakage current was passed through the GI wire, LT X-arm ,earth wire of PSC pole to earth. At th | Not Applicable | Not Applicable
30 | JND | Rural Division-1 | Bhesan | Shri. Hitesh Vithalbhai | 2007-07-01 |  |  | 1 |  |  | Leakage in Private premises at the time of replacing Electric motor in Bore | Not Applicable | Not Applicable
31 | JND | Rural Division-1 | Visavadar-1 | Smt. Hansaben Vithalbhai | 2007-06-29 |  |  |  | 1 |  | Unauthorized construction below 11kV line touched to it. | Not Applicable | Not Applicable
32 | JND | Rural Division-1 | Junagadh(R) | Cow | 2007-07-03 |  |  |  |  | 1 | Leakage in TC Earthing | Not Applicable | Not Applicable
33 | JND | Rural Division-1 | Visavadar-2 | Cow | 2007-07-07 |  |  |  |  | 1 | Leakage in TC Earthing | Not Applicable | Not Applicable
34 | JND | Rural Division-2 | Mendarda | Smt. Hemiben Vinubhai Vaghasiya | 2007-06-27 |  |  | 1 |  |  | A fatal accident occurred to Smt. Hemi Ben Vinbhai Vaghasiiya due to leakage current passes through meter body to leakage and touched victim in private premises | Not Applicable | Not Applicable
35 | JND | Rural Division-2 | Manavadar-2 | Sh. Arfeb Chhagan Rathod | 2007-06-30 |  |  | 1 |  |  | A fatal accident occurred at ag group lighting lamp wiring insulation damage and touched with cloth hanging wire angle and leakage current pass and meet fatal accident | Not Applicable | Not Applicable
36 | JND | Rural Division-2 | Mendarda | Sh. Rameshbhai Somabhai Sahiya | 2007-07-02 |  |  | 1 |  |  | Due to heavy rain and wind when victim passes on road nearby LT line conductor breakdown and touches the LT cross arm & accident occurred | Not Applicable | Not Applicable
37 | JND | Rural Division-2 | Mendarda | Sh. Sanjaybhai Lalubhai Makvana | 2007-07-24 |  |  |  | 1 |  | During TC replacement working on 11kV Alidhra feeder line clear returned by Sh. G. G. Kalola, Mendarda Sub-division
38 | JND | Rural Division-2 | Mendarda | Buffalo | 2007-07-14 |  |  |  |  | 1 | Due to snapping of LT conductor | Not Applicable | Not Applicable
39 | JND | Veraval | Veraval Town | Cow | 2007-07-02 |  |  |  |  | 1 | Due to touching flexible wire to sign board and through sign board leakage was passing in the door | Not Applicable | Not Applicable
40 | JND | Veraval | Veraval Town | Cow | 2007-07-02 |  |  |  |  | 1 | Due to leakage of current at T/C D.P. earthing | Not Applicable | Not Applicable
41 | JND | Veraval | Talala | Smt. Hemiben Bhaya Balash | 2007-07-12 |  |  |  | 1 |  | The LT Line cond.was snapped due to Lungaries | Not Applicable | Not Applicable
42 | JND | Veraval | Talala | Buffalo | 2007-07-13 |  |  |  |  | 1 | Jumper was broken and touching to pole earth wire | Not Applicable | Not Applicable
43 | JND | Veraval | Talala | Buffalo | 2007-07-18 |  |  |  |  | 1 | Due to broken binding from LT Shackle, Cond. Was lying on "U" Clamp and so leakage was passing through pole | Not Applicable | Not Applicable
44 | JND | Rural Division-1 | Bilkha | Sh. Chandubhai Raghav Vaghela | 2007-07-25 |  |  |  | 1 |  | Due to jerk in neutral wire at the time of fixing street light | Not Applicable | BEING A GRAM PANCHAYAT PERSON Not Applicable
45 | JND | Rural Division-1 | Bilkha | A Calf & A Cow | 2007-07-28 |  |  |  |  | 1 | LT line leakage in earthing | Not Applicable | Not Applicable
46 | JND | Rural Division-1 | Bhesan | Smt. Vliben Ravajibhai & Pankaj Ravaji | 2007-08-04 |  |  |  | 1 |  | Due to heavy rain and wind pressure conductor binding damage and LT line conductor fall on c clamp | Not Applicable | Not Applicable
47 | JND | Rural Division-1 | Bilkha | Buffalo | 2007-08-08 |  |  |  |  | 1 | Due to heavy rain and wind pressure LT line conductor snapped. | Not Applicable | Not Applicable
48 | JND | Rural Division-1 | Visavadar-1 | Smt. Rasilaben Ratibhai | 2007-08-10 |  |  |  | 1 |  | Due to internal wiring leakage in private premises | Not Applicable | Not Applicable
49 | JND | Rural Division-1 | Bhesan | Bullock | 2007-08-10 |  |  |  |  | 1 | Due to heavy rain and wind pressure conductor binding damage and LT line conductor fall on c clamp | Not Applicable | Not Applicable
50 | JND | Rural Division-1 | Bhesan | Cow | 2007-08-12 |  |  |  |  | 1 | Leakage in insulation of 1 phase service wire | Not Applicable | Not Applicable
51 | JND | Rural Division-1 | Visavadar-2 | Buffalo | 2007-08-17 |  |  |  |  | 1 | Due to heavy rain and wind pressure conductor binding damage and LT line conductor fall on c clamp | Not Applicable | Not Applicable
52 | JND | Rural Division-1 | Bhesan | Ku. Monikaben Vinubhai & Ku. Bhumikaben Kamleshbhai | 2007-08-19 |  |  |  | 1 |  | Due to touching of live 11 kV line passes near terrace | Not Applicable | Not Applicable
53 | JND | Rural Division-1 | Bilkha | 2 Nos Of Buffalo | 2007-08-20 |  |  |  |  | 1 | Due to touching of LT phase wire with neutral wire. Neutral wire was fall on c clamp. | Not Applicable | Not Applicable
54 | JND | Rural Division-1 | Visavadar-1 | Buffalo | 2007-08-22 |  |  |  |  | 1 | Due to touching of LT phase wire with guard wire, bird fault | Not Applicable | Not Applicable
55 | JND | Rural Division-2 | Shapur | One Buffalo | 2007-07-29 |  |  |  |  | 1 | Due to came to contact with the Kit Kat fuse on LT side of TC | Not Applicable | Not Applicable
56 | JND | Rural Division-2 | Shapur | Sh. Arfebgar Dhangar Aparnathi | 2008-08-02 |  | 1 |  |  |  | Due to broke down of 11kV Line pole when he was working on line | Not Applicable | Not Applicable
57 | JND | Rural Division-2 | Manavadar-1 | A Calf | 2007-08-06 |  |  |  |  | 1 | Due to rain situation minor leakage current passed through earthing and at that time victim came to contact with the earthing wire and electrocuted. | Not Applicable | Not Applicable
58 | JND | Rural Division-2 | Mendarda | A Buffalo | 2007-08-15 |  |  |  |  | 1 | Due to leakage current passed through 100kVA transformer earthing | Not Applicable | Not Applicable
59 | JND | Rural Division-2 | Mendarda | A Cow | 2007-08-18 |  |  |  |  | 1 | Due to snapping of LT Conductor when victim passing near 63kVA TC named Mohan Manji Pansuriya Group and came to contact with live wire. | Not Applicable | Not Applicable
60 | JND | Rural Division-2 | Mendarda | A Buffalo | 2007-08-22 |  |  |  |  | 1 | Due to leakage current passed through transformer earthing and victim rubs its body and met to accident. | Not Applicable | Not Applicable
61 | JND | Veraval | GIDC VRL | Sh. Mohmadsahid Mohmadkarim Bhadarka | 2007-07-27 |  |  | 1 |  |  | Due to leakage current passed through the earthing of the PSC LT pole due to breaking of the service line and touched to earthing wire of the pole, | Not Applicable | Not Applicable
62 | JND | Veraval | Veraval Town | Kum. Fazilat Altaf Bhoda | 2007-08-03 |  |  |  | 1 |  | Due to leakage current passed through the earthing of the PSC LT pole due to breaking of the service line and touched to earthing wire of the pole, | Not Applicable | Not Applicable
63 | JND | Veraval | Prabhas Patan | A Buffalo | 2007-08-04 |  |  |  |  | 1 | Due to snapping of the neutral wire in 1Ø service line. | Not Applicable | Not Applicable
64 | JND | Veraval | Talala | A Cow | 2007-08-07 |  |  |  |  | 1 | Due to leakage current in TC earthing | Not Applicable | Not Applicable
65 | JND | Veraval | Prabhas Patan | Sh. Bodu Abdul Sidi | 2007-08-12 |  |  | 1 |  |  | Due to broken of LT line pole | Not Applicable | Not Applicable
66 | JND | Veraval | GIDC VRL | Sh. Raghubhai K Padhiyar | 2007-08-18 |  | 1 |  |  |  | Due to cracking of the boarder of the PSC pole while climbing the pole. so he loose his balance and fall down to the earth and met the mechanical accident. | Not Applicable | Not Applicable
67 | JND | Veraval | Prabhas Patan | A Cow | 2007-08-23 |  |  |  |  | 1 | Due to leakage current in LT pole earthing. | Not Applicable | Not Applicable
68 | JND | Veraval | Pranchi | A Bullock | 2007-08-05 |  |  |  |  | 1 | Due to leakage current in TC earthing | Not Applicable | Not Applicable
69 | JND | Veraval | Talala | A Buffalo | 2007-08-04 |  |  |  |  | 1 | Due to touching of scratched cable to guy wire and buffalo has come in contact with this guy wire | Not Applicable | Not Applicable
70 | JND | Veraval | Talala | A Buffalo | 2007-08-04 |  |  |  |  | 1 | Due to snapping of LT line wire and both the Buffalo passed near the snapped cond. & come in contact and electrocuted. | Not Applicable | Not Applicable
71 | JND | Veraval | Prabhas Patan | A Cow | 2007-08-17 |  |  |  |  | 1 | Due to Pin puncture leakage current was passing in pole | Not Applicable | Not Applicable
72 | JND | Veraval | Pranchi | A Buffalo | 2007-08-18 |  |  |  |  | 1 | Due to leakage of current in earthing of service pole | Not Applicable | Not Applicable
73 | JND | Veraval | Prabhas Patan | A Cow | 2007-08-20 |  |  |  |  | 1 | Snapping og conductor in LT line ph. wire | Not Applicable | Not Applicable
74 | JND | Rural Division-1 | Visavadar-2 | CALF | 2007-08-28 |  |  |  |  | 1 | Due to heavy rain and wind LT. line conductor snapped | Not Applicable | Not Applicable
75 | JND | Rural Division-1 | Bilkha | SHRI LAKHABHAI LALABHAI | 2007-05-09 |  | 1 |  |  |  | Line clear was taken but feedback owner supply came due to another source. Un authorized operation by outsider | Not Applicable | Not Applicable
76 | JND | Rural Division-1 | Visavadar-2 | BULLOCK | 2007-09-23 |  |  |  |  | 1 | Due to heavy rain and wind LT. line conductor snapped | Not Applicable | Not Applicable
77 | JND | Rural Division-2 | Mendarda | Two Buffalo | 2007-08-30 |  |  |  |  | 1 | Due to heavy rain and wind LT. line conductor snapped | Not Applicable | Not Applicable
78 | JND | Veraval | Talala | A Cow | 2007-09-01 |  |  |  |  | 1 | Due to leakage of current in T/C. Earthing | Not Applicable | Not Applicable
79 | JND | Veraval | Pranchi | Sh. Pithabhai Rambhai Rathod | 2007-08-29 |  |  | 1 |  |  | Leakage of Current in 1 PG motor due to some problem in his premises | Not Applicable | Not Applicable
80 | JND | Veraval | Talala | Sh. Ramesh Vira Chudasama | 2007-09-07 |  |  |  | 1 |  | During cutting work in monsoon period victim may came in vicinity of 11 KV line & met with N.F.A. | Not Applicable | Not Applicable
81 | JND | Veraval | Talala | A Buffalo | 2007-09-09 |  |  |  |  | 1 | T/C earthing was leakage in monsoon period victim might came in contact with T/C and met with F.A. | Not Applicable | Not Applicable
82 | JND | Veraval | Talala | A Buffalo | 2007-09-12 |  |  |  |  | 1 | Due to minor leakage current in T/C earthing and buffalo accidently came in contact and electrocuted. | Not Applicable | Not Applicable
83 | JND | Veraval | Veraval Town | A Buffalo | 2007-09-13 |  |  |  |  | 1 | Victim while passes near the 11 KV pole Loc. № MTH/BLP/38 broken the guy wire & upper wire of guy came in contact with live D.O. Jumper through which victim come in contact and got electrocuted | Not Applicable | Not Applicable
84 | JND | Veraval | GIDC VRL | Sh. Maheshbhai Karshan Gadhiya | 2007-09-17 |  |  |  | 1 |  | Due to broken and fall down of LT Line PSC Pole he fall down on earth | Not Applicable | Not Applicable
85 | JND | Veraval | Prabhas Patan | Sh. Ashok Gokaldas Solanki (Helper) | 2007-09-21 |  | 1 |  |  |  | Due to climbing of 11 KV DP where two feeders are passing namely Deva & Vidyutnagar on which only one line L.C. was taken (Devka) & another line was in live condition, so during jumpering work on Devka Feeder Jumper wire may touched to the live wire and t | Not Applicable | Not Applicable
86 | JND | Veraval | Pranchi | A Cow | 2007-09-21 |  |  |  |  | 1 | Due to snapping of LT line conductor. | Not Applicable | Not Applicable
87 | JND | Veraval | Pranchi | Sh. Dhirubhai Mandanbhai Solanki | 2007-09-22 |  |  | 1 |  |  | Victim may come in contact with live broken service wire | Not Applicable | Not Applicable
88 | JND | Veraval | Talala | A Buffalo | 2007-09-24 |  |  |  |  | 1 | Due to broken of AG LT line in monsoon period victim might came in contact and met with F.A. | Not Applicable | Not Applicable
89 | JND | Veraval | Talala | A Buffalo | 2007-09-24 |  |  |  |  | 1 | Due to T/C earthing was leakage in monsson period victim might have came in contact with F.A. | Not Applicable | Not Applicable
90 | JND | City Division | Satellite | A Buffalo's Calf | 2007-09-25 |  |  |  |  | 1 | Due to snapping of LT line conductor. | Not Applicable | Not Applicable
91 | JND | Rural Division-1 | Visavadar-1 | A Cow | 2007-09-27 |  |  |  |  | 1 | Due to snapping of LT line conductor. | Not Applicable | Not Applicable
92 | JND | Rural Division-1 | Visavadar-2 | Shri Manilal Somabhai | 2007-09-27 |  | 1 |  |  |  | DUE TO PSC POLE BROKEN. MECHANICAL ACCIDENT | Not Applicable | Not Applicable
93 | JND | Rural Division-1 | Bilkha | Shri Yunus Ismail Savan | 2007-09-28 |  |  |  | 1 |  | DIRECT TOUCHING TO LIVE 11 K.V. LINE | No | Not Applicable
94 | JND | Rural Division-1 | Visavadar-2 | Shri Bharatsinh Chhatrasinh | 2007-10-14 |  | 1 |  |  |  | DUE TO UN ISOLATION OF G.O. SWITCH CONTACT | No | No
95 | JND | Rural Division-1 | Bilkha | BUFFALO | 2007-10-16 |  |  |  |  | 1 | DUE TO SNAPPING OF L.T. LINE COND. | Not Applicable | Not Applicable
96 | JND | Rural Division-2 | Mendarda | BUFFALO | 2007-09-30 |  |  |  |  | 1 | Due to leakage current of TC earthing | Not Applicable | Not Applicable
97 | JND | Rural Division-2 | Manavadar-1 | Sh. Bholabhai Merubhai Kamariya | 2007-09-29 |  |  |  | 1 |  | When Victim was trying to connect VCD Player wire in Stereo wire in private primises at that time due to short circuit of VCD player victim Electrocuted and met with Non Fatal Accidedent. | Not Applicable | Not Applicable
98 | JND | Rural Division-2 | Mendarda | Sh. Anantrai Laxmanbhai Bhimani | 2007-10-09 |  |  | 1 |  |  | Due to Electric Shock while he was switching off hos motor in his farm room where meter was attached and met with Human Fatal Accident. | Not Applicable | Not Applicable
99 | JND | Rural Division-2 | Mendarda | Sh. Shaileshbhai Rupabhai Palas Vill. Helper VS | 2007-10-18 |  | 1 |  |  |  | Due to 11 KV Deterioted Angle of Karavalu Ag Group. To Sh. Shaileshbhai Rupabhai Palas Vill. Helper (V/S) | Yes | Not Applicable
100 | JND | Veraval | Pranchi | A Bullock | 2007-09-26 |  |  |  |  | 1 | Due to Broken incoming LT Line and Bullock was came in contact with broken wire and met with electrical accident | Not Applicable | Not Applicable
101 | JND | Veraval | Prabhas Patan | A Buffalo | 2007-09-29 |  |  |  |  | 1 | Due to unauthorised wiring done by the farmer in his fancing of the farm | Not Applicable | Not Applicable
102 | JND | Veraval | Talala | A Buffalo | 2007-09-30 |  |  |  |  | 1 | Due to leakage current passing from T/C earthing when buffalo passwed and came in contact with T/C earthing it may be electro- cuted | Not Applicable | Not Applicable
103 | JND | Veraval | GIDC VRL | Sh. Dineshbhai Jagmalbhai Pampania | 2007-10-03 |  |  | 1 |  |  | Due to touching the 11 KV Live Line on load side DP after Gangswitch | Not Applicable | Not Applicable
104 | JND | Veraval | Prabhas Patan | Sh. Laxmanbhai Malabhai Solanki | 2007-10-20 |  |  | 1 |  |  | When victim repaired TV in his own house contact with live open wire of his house wiring and got shocked and met with accident | Not Applicable | Not Applicable
105 | JND | City Division | Satellite | A Buffalo | 2007-11-04 |  |  |  |  | 1 | Due to falling the tree in the heavy rain and high wind pressure atmosphere snapping of the LT Conductor on the buffalo | Not Applicable | Not Applicable
106 | JND | Rural Division-1 | Junagadh(R) | Sh. Munnabhai Urfe Muneshvar Mahavir | 2007-11-05 |  |  |  | 1 |  | Come into the induction zone of 11kV line | Not Applicable | Not Applicable
107 | JND | Rural Division-1 | Visavadar-1 | Sh. Viththalbhai Kalabhai | 2007-11-06 |  |  | 1 |  |  | Due to snapping of LT conductor | Not Applicable | Not Applicable
108 | JND | Rural Division-1 | Junagadh(R) | Sh. Ranjit Vikram Mandaviya | 2007-11-24 |  |  | 1 |  |  | Come to contact with the 11kV line. | Not Applicable | Not Applicable
109 | JND | Veraval | Pranchi | A Cow | 2007-11-05 |  |  |  |  | 1 | Due to broken of inside LT line when cow passed near this broken line and got electrical accident | Not Applicable | Not Applicable
110 | JND | Rural Division-2 | Manavadar-1 | Sh. Abdulkhan Ibrahim Belim | 2007-12-03 |  |  |  | 1 |  | Due to come in induction zone of the 66kV. | Not Applicable | Not Applicable
111 | JND | Veraval | Prabhas Patan | Sh. Ibrahim Pira Thobhat | 2007-11-30 |  |  | 1 |  |  | Due to conductor snapping, but not clear reason found yet. | Not Applicable
112 | JND | City Division | Gandhigram | Mansukh Tulsidas Vaghela | 2007-12-28 |  |  |  | 1 |  | The victim slept his leg while he was fixing a junction box on L.T. line Girder pole and fall down from the girder and meet with non-fatal mechanical accident | Not Applicable | Not Applicable
113 | JND | Rural Division-2 | Manavadar-1 | Smt. Kanchanben Harsukhbhai Parmar | 2008-01-25 |  |  | 1 |  |  | We haven't informed by party.The rojkam is done after Newspaper Sandesh pressnote on 30.01.08.The accident has been occurred near HT-LT circuit line.Still no-strong reason has been found but came to know that victim tryed to connect lungaria to 11KV line | Not Applicable | Not Applicable
114 | JND | Rural Division-2 | Manavadar-1 | smt. Narmadaben Bavanjibhai Maradiya | 2008-01-28 |  |  | 1 |  |  | Due to short circuit of 1-Ph.Motor in private premises | Not Applicable | Not Applicable
115 | JND | Veraval | Pranchi | Sh Rajesh Bachubhai Barad | 2008-01-07 |  |  | 1 |  |  | During change of loads in service at his primises | Not Applicable | Not Applicable
116 | JND | Rural Division-1 | Bhesan | Sh.Bharat Jasyantkant Dave(Helper) | 2008-03-07 |  | 1 |  |  |  | While Victim was attending the new release of connection and installing the meter, slipped down leg from the stool table and met to mechanical accident | Not Applicable | Not Applicable
117 | JND | Veraval | Prabhas Patan | Sh.Kaushik Kana Pampaniya | 2008-03-05 |  |  | 1 |  |  | We have not informed by party. The information received from daily News paper “Divya Bhaskar” press note on 07.03.08. The accident has been occurred in Private premises. During starting of his motor-might have come in contact with live wire | Not Applicable | Not Applicable
1 | BVN | City-1 | HT | Manoj Ravishankar Joshi | 23-6-07 | 1 |  |  |  |  | Sliping from PSC pole mecahnical accident | Meeting arranged for use of safety belt at s/dn.
2 | BVN | City-1 | Power House | Urvashi Manaji Dhakhara | 18-6-07 |  |  | 1 |  |  | Come into the direct touch to live holder in private primises
3 | BVN | City-1 | Kalanala | Rahil Rahim Dariya | 25-6-07 |  |  |  | 1 |  | Come into the direct touch to live holder in private primises
4 | BVN | City-2 | Hill Drive | S.S.MAHIDA | 2007-06-25 |  | 1 |  |  |  | Electrocuted due to common neutral | necessary action taken
5 | BVN | City-2 | Kalvibid | M.J.VAGHELA | 2007-06-25 |  | 1 |  |  |  | Due while repairing of comaplatins of consumer , he felt jerk and fall down from compound wall | necessary action taken
6 | BVN | BVN-R | Dhola | Sh. P.D.Parmar (App. L.M.) | 2007-05-21 |  | 1 |  |  |  | Electrocuted from another supply while working due to crossing of line | Necessary action taken
7 | BVN | BVN-R | Sihor-R | Sh. Girish D Solanki (VS-HLP) | 2007-06-21 |  | 1 |  |  |  | After isolating A.B. Switch of 11 KV Line tim has short line with piece of conductor and due to sparking met with N.F.A. | Necessary action taken
8 | BVN | BVN-R | Vallabhipur | Sh. Vinodbhai Haribhai Jadvani | 22/6/2007 |  |  | 1 |  |  | Come into the direct touch to live holder in private primises | Necessary action taken
9 | BVN | Mahuva | Jesar | Ghanshyambhai Jasmatbhai Jethava | 2007-04-16 |  |  | 1 |  |  | Tempo was struck to the LT PSC Pole and psc pole fallen on victim with live conductor | Necessary action taken
10 | BVN | Mahuva | Rural-2 | Bachubhai kanabhai Hadiya | 2007-06-10 |  |  | 1 |  |  | Victim has try to fix-up DO fuse of TC and came in contact with live 11 KV line and met with F.A | Necessary action taken
11 | BVN | Mahuva | Rural-2 | Gumanbhai Umedsangbhai | 2007-04-28 |  |  |  | 1 |  | accident was occurred on 28-4-07, but our official was informed by party on 21-5-07, on investigation no evidence found at place of accident about accident occurred by our network | Necessary action taken
12 | BVN | Palitana | Palitan -R | Manubhai Lakhabhai Parmar | 2007-05-03 |  |  | 1 |  |  | Unaothorised climbing on pole LT | Necessary action taken
13 | BVN | Palitana | Gariyadhar | Ishwarbhai Jivabhai Kharadi App LM | 2007-04-20 |  | 1 |  |  |  | While working on 11 KV line, PSC pole was tilted and lost his balance' hence fall down on ground | Necessary action taken
14 | BVN | Palitana | Gariyadhar | Mukesh Ratilal Dodiya Helper | 2007-06-27 |  | 1 |  |  |  | While working on 11 KV line, PSC pole was broken hence fall down on ground | Necessary action taken
15 | BVN | Botad | Dhasa | Dhiru Vallabh Kathiriya | 2007-04-11 |  |  | 1 |  |  | Try to work on TC un athorised | Not Applicable
16 | BVN | Botad | Paliyad | Jeram Ladha prajapati | 2007-04-17 |  |  |  | 1 |  | Try to work on TC un athorised | Not Applicable
17 | BVN | Botad | Town-2 | Sandip jayesh Kosiya | 2007-04-21 |  |  | 1 |  |  | leakage current flow from ideal pole of TC to earth, due deterioted PVC cable. | LT PVC Cable replace
18 | BVN | Botad | Barwala | J.V.Chavda | 2007-04-25 | 1 |  |  |  |  | While working on line by taking tripping, due to one pole of breaker was not isolated and victim got shock | Necessary action taken
19 | BVN | Botad | Gadhada | C.K.Makwana | 2007-06-06 |  | 1 |  |  |  | While working on line of 11 KV, another 11 KV line touch to line on which work taken on hand due to wind pressure | Proper guarding done and clearance increased
20 | BVN | Mahuva |  | 1 Cow & 1 Calf | 2007-06-15 |  |  |  |  | 2 | LT Conductor was snapped and was touch to LT shackle, so leakage current was flow in pole earthing and victim got shock.
21 | BVN | Palitana |  | Bufallow | 2007-06-10 |  |  |  |  | 1 | Unauthoried line extension by unknown person
22 | BVN | Palitana |  | Bufallow | 2007-05-21 |  |  |  |  | 1 | Snapping of LT conductor
23 | BVN | Palitana |  | Cow | 2007-06-04 |  |  |  |  | 1 | Leakage current passed through guy wire of TC
24 | BVN | Palitana |  | Cow | 2007-06-25 |  |  |  |  | 1 | Snapping of LT conductor
25 | BVN | BVN-R |  | Cow | 2007-06-22 |  |  |  |  | 1 | Leakage Current through the earth wire of tc
26 | BVN | BVN-R |  | Bullock | 2007-06-24 |  |  |  |  | 1 | Came in direct contact with live conductor
27 | BVN | City-1 |  | Female Buffalo | 2007-06-22 |  |  |  |  | 1 | Electrocuted from another supply while Waking
28 | BVN | BVN-R | Sihor-R | Animal | 2007-07-02 | 0 |  |  |  | 1 | Snapping of Conductor
29 | BVN | BVN-R | Vall'pur | Mohansing Udesing Ravat | 2007-07-11 |  |  | 1 |  |  | Snapping of Conductor
30 | BVN | Palitana | Gariyadhar | Animal | 2007-07-04 |  |  |  |  | 1 | Neutral was touching with C-Clamp and the neutral was common with t/c earth. Animal touch with earthing wire.
31 | BVN | Palitana | Gariyadhar | Animal | 2007-07-04 |  |  |  |  | 1 | Meter was provided on T/c. It was provided with MMB. The neutral was touching with MMB. The MMB was also earthed with T/c. earth and the ani,mal thouhed with earting.
32 | BVN | Palitana | Palitana _-T | Animal | 2007-07-03 |  |  |  |  | 1 | Snapping of Conductor
33 | BVN | Palitana | Trapaj | Animal | 2007-07-12 |  |  |  |  | 1 | LT jumper touched with Guy wire. Guy insulator was broken. Animal thouched with guy wire and it get shock.
34 | BVN | Palitana | Talaja | Animal | 2007-07-29 |  |  |  |  | 1 | Due to heavy rain and wind LT jumper touched with C-clamp and Current pass thorugh earting of GI Wire at PSC Pole.
35 | BVN | Mahuva | Jesar | Jaysukhbhai Somatbhai Parmar | 2007-07-02 |  |  | 1 |  |  | Snapping of Conductor
36 | BVN | Mahuva | Mahvua R-2 | Animal | 2007-07-08 |  |  |  | 1 |  | Snapping of Conductor
37 | BVN | Botad | Paliyad | Animal | 2007-07-01 |  |  |  |  | 1 | The earthing of the T/c. was leakage. Due to rain the water was clogging in surrounding area. So the leakage current was passing in the water. The animal came in contact with the was water and it get shock.
38 | BVN | Botad | Gadhada | Anil H. Badhia | 2007-07-26 |  | 1 |  |  |  | The DE Gadhada has demanded the line clear of Tatam JGY for to reconnect the DO Fuse of Nana Sakhpar Section. So the SBO of 66KV Tatam S/s. had give the line clear of Nana Sakhpar Ag. feeder instead of Tatam JGY Feeder. The line clear was demanded on C | Yes
39 | BVN | Mahuva | Mahvua R-2 | Animal | 2007-08-01 |  |  |  |  | 1 | The B-phase of out going cable from D. B. was deteriorated and it was thouching with distribution box. The animal came in contact with this D.B. hence it got shock and it died.
40 | BVN | Mahuva | Jesar | Animal | 2007-08-05 |  |  |  |  | 1 | Snapping of LT conductor
41 | BVN | Palitana | Gariyadhar | Animal | 2007-08-08 |  |  |  |  | 1 | Leakage Current was passing through earthing wire. The current was passing in surrounding area. The animal came in contact with the earhing wire and it get shock and it ided
42 | BVN | BVN-R | Vartej | Animal | 2007-08-05 |  |  |  |  | 1 | A truck was struck with the girder pole. Hence the accident is Occurred
43 | BVN | Mahuva | Mahvua R-2 | Human | 2007-08-28 |  |  |  | 1 |  | The victim was working on the Khadsaliya Ag. Feeder. Due number of crossing of 220KV line, 66KV line and Malvav JGY feeder the victim meight have feel the induction. Hence the accident is only due to induction of the other feeder.
44 | BVN | Botad | Dhasa | Animal | 2007-08-15 |  |  |  |  | 1 | Snapping of LT conductor
45 | BVN | Mahuva | Mahvua R-1 | Human | 2007-08-31 |  |  | 2 | 1 |  | At anandjibhai Kalyanjibhai trust Ag. Land Chhapariyali village, PGVCL's LT Line has been passed. Under this line direct connection taken (illegally) by the victim's parents for electrification of one lamp in the hut under the farm. As per the statement o
46 | BVN | Botad | Paliyad | Animal | 2007-08-31 |  |  |  |  | 1 | Leackage current from the earthing of the DTC.
47 | BVN | Palitana | Gariyadhar | Animal | 2007-08-20 |  |  |  |  | 1 | The cable of the DTC was deteriorated and it was thouching with the DB. The animal came in contact with this DB and it get shcock and died.
48 | BVN | Palitana | Talaja | Human | 2007-08-24 |  |  | 1 |  |  | Snapping of LT Conductor
49 | BVN | Palitana | Talaja | Human | 2007-08-30 |  |  | 1 |  |  | Snapping of coatted conductor due to heavy rain.
50 | BVN | City-1 | Diaimond Chowk | Human ALM Name : Bipinbhai Kanajibhai Undaviya. | 2007-09-14 |  | 1 |  |  |  | Street light phase was ON. The victim came in contact with the strreet light phase and he got shock.
51 | BVN | BVN-R | Vallabhipur | Animal | 2007-09-21 |  |  |  |  | 1 | Snapping of LT conductor
52 | BVN | BVN-R | Dhola | Animal | 2007-09-22 |  |  |  |  | 1 | The LT guard wire was touching with the LT phase wire. Hence the current was pssing through the guard wire and the Girder pole. The animal came in contact with this girder and it got shock and it died.
53 | BVN | BVN-R | Dhola | Animal | 2007-08-30 |  |  |  |  | 1 | The conductor was touching with the LT X-arm due to the damage of binding wire of the shackle insulater. So the path was completed through the x-zrm and the girder pole. The animal came in contact with this girder and it got shock and it died.
54 | BVN | BVN-R | Sihor (R) | Animal | 2007-09-05 |  |  |  |  | 1 | Snapping of LT conductor
55 | BVN | Mahuva | Jesar | Animal | 2007-09-22 |  |  |  |  | 1 | Snapping of LT conductor
56 | BVN | Botad | Dhasa | Animal | 2007-09-19 |  |  |  |  | 1 | The load side cable of the transformer i.e. LT side cable was deterirated and the animal came in contact with this cable and it got shock and it died.
57 | BVN | Botad | Dhasa | Animal | 2007-09-22 |  |  |  |  | 1 | Due to brken of binding wire and deteriorated jumper the conductor was touching with the c-clamp and the current was passing through the c-clamp and the earthing wire. The animal came in contact with this earthing wire and it got shock and it died.
58 | BVN | Palitana | Palitana -R | Fatal Human Nikunj Kanajibhai | 2007-09-05 |  |  | 1 |  |  | The 11 KV line was passing over the house at village Bharatimba. The victim was on the tarrace and accidently he came in contact with the feeder wire and he got shock and he died.
59 | BVN | Palitana | Palitana-T | Animal | 2007-09-28 |  |  |  |  | 1 | Due to weak earthing tof the T/c the current was pssing through the earth of DP structure. The cow was passing near the DP and came in contct with the DP and it got shock and died. | The earthing is reactivated
60 | BVN | Palitana | Palitana-T | Non Fatal Human (Girl) Komalben Ramahibhai | 2007-10-10 |  |  |  | 1 |  | The accident is occured at Baharpara, Adpur Road, jurisdiction of the Palitna-T, the victim meight ahve in contact with the joint of broken single phase service line and she got shock. But there is no any evidance like black spot or blood on the service l | The deteriorated service is replaced.
61 | BVN | Palitana | Palitana-T | Animal | 2007-10-10 |  |  |  |  | 1 | Due to snapping of the street light conductor was fall down. The cow came in contact and it get shock and died. | Necessary maitenance is carried out
62 | BVN | Botad | Barwala | Bherumal Jethalal Bhil | 2007-10-11 |  |  |  | 1 |  | Due to electrocution the victim fall down and get injured. The victim is labourman of a contractor, he and co-worker are not giving any statement regarding the occrance of the accident. | Due to non giving statement of the coworker the factual reason is not coming out.
63 | BVN | Botad | Lakhavad (Dhol) | Animal | 2007-10-18 |  |  |  |  | 2 | Due to snapping of the conductor the animals came in contact with this snapped conductor and got shock and they died. | Necessary maitenance is carried out
64 | BVN | Palitana | Palitana-R | Non Fatal Human(Boy) Prakash Raghavbhai Chauhan | 2007-10-23 |  |  |  | 1 |  | Due to snapping of HT conductor the load side of the conductor was fall down and it was touching eith the fancing. The fancing was binded with the main iron gate of the temple. The victim came in contact with the gate and he got shock. | The three span to the HT line is replaced.
65 | BVN | BVN-R | Vallabhipur | Animal | 2007-10-28 |  |  |  |  | 1 | As per party's information PSC Pole was broken and fall downon buffallow and due to live wire of the pole the animal got shock and it died. But as per the rojkam there is no wire on the pole and the animal was 10' away from the broken pole.
66 | BVN | Palitana | Palitana-Rural | Fatal Human - Shri Bhupatbhai Shamjibhai Varsadiya | 2007-11-06 |  |  | 1
67 | BVN | City - 1 | Khargate | Non Fatal Human to Staff |  |  | 1
68 | BVN | BVN-R | SHIHOR-R | Fatal human | 2007-12-01 |  |  | 1 |  |  | Wire extended from nearby house to use electricity.It touched G I Wire used for drying cloths. Victim touched the G I Wire & got shocked & dead.
69 | BVN | BVN-R | SHIHOR-T | Fatal Animal-buffalow | 2007-12-20 |  |  |  |  | 1 | Phase cond of dead line of 11 kv nesda feeder are snapped and fall on 11kv shakun feeder and this dead line became live.Buffalow passing nearby came in contact with this live wire and shocked and died.
70 | BVN | city-1 | Diaimond Chowk | C N SOLANKI | 2008-01-08 |  | 1 |  |  |  | Main switch of streetlight fired due to earth fault when he switched on the main switch after attending fault
71 | BVN | palitana | palitana-r | Pravinbhai Govindbhai | 2008-01-09 |  |  | 1 |  |  | Victim was climbed on ag t/c and he touch live conductor and got shocked
72 | BVN | city-1 | Diaimond Chowk | Bhupatbhai Bachubhai Chauhan | 2008-01-09 |  | 1 |  |  |  | While climbing round pole he lost balance and fell down on ground
73 | BVN | BOTAD | BOTAD T-2 | Fatal Animal-buffalow | 2008-01-15 |  |  |  |  | 1 | SNAPPING OF CONDUCTOR
74 | BVN | CITY-1 | POWERHOUSE | THAKARSHIBHAI MAKAWANA | 2008-01-18 |  | 1 |  |  |  | Link switch of TC was disconnected before execution of work but power supply was not disconnected
75 | BVN | Palitana | PALITANA-R | Sajalben Bharatbhai Gohil | 02.02.08 |  |  |  | 1 |  | The victim was cutting the imali from the ambali tree with the help of an iron rod. The iron rod came in contact with HT live wire &get electrocuted.
76 | BVN | Palitana | PALITANA-R | Ghanshyambhai Jagdishbhai Gohil | 02.02.08 |  |  |  | 1 |  | The victim was cutting the imali from the ambali tree with the help of an iron rod. The iron rod came in contact with HT live wire &get electrocuted.
77 | BVN | Mahuva | mahuva-r | Bachubhai Jodhubhai , sh. Bhagvanbhai dayabhai | 07.02.08 |  |  |  | 1 |  | The wire broken due to truck accident
78 | BVN | Mahuva | mahuva-r | Bhola bhai Hakabhai Baraiya | 2008-07-02 |  |  | 1 |  |  | The victim touched with open starter and get electric shock . The accident is occurred at load side of the consumer
79 | BVN | Botad | paliyad | sh. Vinod bhai and batukbhai | 2008-02-21 |  |  |  | 1 |  | During the maintenance of Rangpur AG feeder the PSC pole broken and the two victim godhariya fall down with the pole 7 GET INJURED. This is a mechanical accident
80 | BVN | Botad | botad-r | sh. Kalusinh. | 22/02/08 |  |  |  | 1 |  | During the working on 11 kv feeder the victim got electrocution at 11 kv level and fall down.
81 | BVN | Botad | Botad-t | sh. Anopsinh ukabhai parmar | 23/02/08 | 1 |  |  |  |  | The victim climb the pole to attend complain no-533. He dis connect the power supply from the D.O Box of the T/C. The line was three phase 5-wire lt including the street light phase was dead. But when the victim came in contact with the street light phase
82 | BVN | Palitana | Trapaj | Dharaben Vinubhai | 2008-12-03 |  |  |  | 1 |  | Due to leakge from electric pump in office primises
83 | BVN | Bhavnagar rural | shihor-r | bhopabhai kalubhai koli | 2008-03-05 |  |  | 1 |  |  | due to collaps of truck to the pole and it was broken and falls on victim &get died.
1 | AMR | Amreli-1 | Liliya | Sh. Khushalbhai Shambubhai Gajera | 2007-04-17 | 0 |  | 1 |  |  | Winding the DO in his Ag. group without permission of company
2 | AMR | Una | Una-1 | Sh. Bhupendra Kantilal Bariya | 2007-04-20 |  |  |  | 1 |  | Contractor man felt from the pole and the mech. accident occurred
3 | AMR | Amreli-1 | Lathi | A buffalo of Sh. Merambhai Vaghabhai | 2007-04-21 |  |  |  |  | 1 | Buffelo had died due to contact with live condctor..
4 | AMR | Amreli-1 | Babra | A cow of Sh. Pathubhai Basiya | 2007-04-21 |  |  |  |  | 1 | Snapping of conductor
5 | AMR | Amreli-1 | Babra | Sh. Vinubhai Ramji | 2007-05-04 |  |  | 1 |  |  | While sharpening the Ag. motor cable in his own room the accident occurred
6 | AMR | S'Kundla | Rajula | FH-(1) Sh. Laljibhai Devayatbhai (2) Smt. Nayanaben Devayatbhai ; NFH-(1) Sh. Devayatbhai Tapubhai (2) Smt. Chakuben devayatbhai ; FA-2 bullock | 2007-05-06 |  |  | 2 | 2 | 2 | 11 KV conductor fell and touched his bullock cart
7 | AMR | S'Kundla | SKD (T) | Sh. Ramesh R. Damor, ALM | 2007-05-15 |  | 1 |  |  |  | Fell from the gurder pole and the mech. accident occurred |  | Not utilised due to not issued by Division
8 | AMR | Amreli-2 | Bagasara | Smt. Chanduben Babubhai | 2007-06-08 |  |  | 1 |  |  | Contact with short circuit motor in his house
9 | AMR | Amreli-2 | Bagasara | A buffalo of Sh. Bharat Jilubhai Vala | 2007-06-15 |  |  |  |  | 1 | Contact with PSC pole earthing
10 | AMR | Una | Una (T) | (1) Sh. Salimbhai Mohabatsah (2) Smt. Rehanaben Salimbhai | 2007-06-17 |  |  |  | 2 |  | Due to broken of 11KV feeder jumper fualt on dish TV cable power had passed on it
11 | AMR | Una | Una-1 | A bullock of Sh. Bijal Bhikha Bambhaniya | 2007-06-19 |  |  |  |  | 1 | Contact with LT live conductor
12 | AMR | Amreli-1 | Liliya | A buffalo of Sh. Babubhau Jadavbhai | 2007-06-23 |  |  |  |  | 1 | Snapping of LT conductor
13 | AMR | Amreli-1 | Lathi | Sh. Shambhubhai Nagjibhai Radadia | 2007-06-24 |  |  | 1 |  |  | Contact with live wire fallen from LT pin insulator
14 | AMR | Una | Una-1 | A buffalo of Sh. Kanubhai Bhimbhai Jasani | 2007-06-24 |  |  |  |  | 1 | Due to leakage from T/C earthing wire
15 | AMR | Una | Kodinar-2 | Buffalo of Sh. Govind Mala Chavda | 2007-06-24 |  |  |  |  | 1 | Contact with live earthing wire
16 | AMR | S'Kundla | SKD(R) | (1) Sh. Zakir Husen Usman Miya V.S. Helper (2) Sh. Gautam Lalji Dafda | 2007-06-25 |  | 2 |  |  |  | While working on the T/C, suddenly the induction was started from live LT condctors. |  | Sefty belt issued in gang but not used
17 | AMR | Amreli-1 | Lathi | Two bullock of sh. Pravinbhai Virjibhai Malavia | 1907-06-04 |  |  |  |  | 2 | Snapping of LT conductor
18 | AMR | Amreli-1 | Chalala | Ankhlo of Sh. Hanifbhai Kasambhai | 1907-06-29 |  |  |  |  | 1 | Leckage of power at street light brocken,open cond. Tutch the pole
19 | AMR | Una | Una-1 | A cow of Sh. Ramjibhai Khimjibahi Parmar | 1907-06-25 |  |  |  |  | 1 | Snapping of LT conductor
20 | AMR | Una | Kodinar-2 | A buffalo of Sh. Rama Sidi | 1907-06-17 |  |  |  |  | 1 | Snapping of LT conductor
21 | AMR | Amreli-1 | Damnagar | Sh. Praduman Chhotala Joshi | 3-7-07 |  |  |  | 1 |  | Fall from the pole and mech. Accident | Victim is Panchayat helper but he has not used any safety tools while working on line. | Instruction has already been given to line staff for using safety tools while working.
22 | AMR | Amreli-1 | Amreli R | Bullock of Sh. Bhupatbhai Valkubhai | 12-7-07 |  |  |  |  | 1 | Snapping of LT conductor
23 | AMR | Amreli-1 | Babra | Smt. Shardaben Mavjibhai | 23-7-07 |  |  | 1 |  |  | Contect with leakage current from butter milk making machine motor.
24 | AMR | Amreli-1 | Babra | A Four Sheep of Sh. Khima Amrabhai | 24-7-07 |  |  |  |  | 1 | Snapping of LT conductor
25 | AMR | Amreli-1 | Chital | A Cow of Sh. Kalubhai Harsurbhai | 25-7-07 |  |  |  |  | 1 | Leckage power of T/C earthing
26 | AMR | S'Kundla | Jafrabad | A Bullock of sh. Chitarbhai Kadvabhai | 28-7-07 |  |  |  |  | 1 | 11KV cond. Fall from Disc Insulator and Bullock tutch.
27 | AMR | S'Kundla | Rajula | A Buffalow of Sh. Ghosabhai Jeturbhai | 29-7-07 |  |  |  |  | 1 | LT conductor fall rfrom the pole and contect.
28 | AMR | Una | Kodinar-1 | A Buffalow of Sh. Karsanbhai Rambhai | 6-7-07 |  |  |  |  | 1 | Contect with live 11KV conductor
29 | AMR | Una | Kodinar-2 | A cow of Sh. Dhirubhai Jikabhai | 30/6/07 reporting on July - 07 |  |  |  |  | 1 | Leckage power of T/C earthing wire
30 | AMR | Una | Kodinar-1 | A two Buffalow of Sh. Alabhai Chinabhai | 1-7-07 |  |  |  |  | 1 | Snapping of conductor.
31 | AMR | Una | Una-2 | A Buffalow of Sh. Mohan Rana | 10-7-07 |  |  |  |  | 1 | Tuch of LT cable of T/C center.
32 | AMR | Amreli-2 | Kunkavav | Sh. Keshubhai Karsanbhai | 28/6/07 reporting on July - 07 |  |  |  | 1 |  | Accident took place when cond. of LT line fell in C clamp and came into contact of earthing wire.
33 | AMR | Amreli-2 | Chalala | A buffalow of sh Laljibhai Devabhai | 9/7/2007 |  |  |  |  | 1 | Contect with LT Conductor.
34 | AMR | Amreli-2 | Dhari | A Cow of Sh. Hirabhai Arfebbhai | 21/6/07 reporting on July-07 |  |  |  |  | 1 | Leckage of PSC pole earthing
35 | AMR | Amreli-2 | Dhari | A Cow of Sh. Anakbhai Gabhrubhai | 24/6/07 reporting on July - 07 |  |  |  |  | 1 | Leckage power of transformer earthing
36 | AMR | Amreli-2 | Dhari | A Bullock of Sh. Nanjibhai Savjibhai | 8-7-07 |  |  |  |  | 1 | Leckage of GUY wire
37 | AMR | Amreli-2 | Vadia | Sh. Yasvantbhai Bhupatbhai Solanki | 29-7-07 |  |  |  | 1 |  | Victim is Panchayat helper and Accident occurred when the crossing live line came into contact of the span of dead line on which victim was working |  | It is necessary to instruct line staff strictly to make all crossing live lines dead, where the work is to be carried out by disconnecting the flow of supply before starting the work.
38 | AMR | Una | Una-2 | Sh. Mala Ram Sanklhat | 28-7-07 |  |  |  | 1 |  | Victim was tutched live 11KV cond. Near his Balcony. |  | Notice has been served to the victim, either to dismantle the balcony or to produce the permission given by the connected Nagarpalika regarding construction of the balcony.
39 | AMR | Amreli-1 | Babra | A Buffalow of Sh.Valabhbhai Shamjibhai. | 29/7/2007. Reporting on Aug."07 |  |  |  |  | 1 | Leakage power of Tranformer earthing.
40 | AMR | Amreli-1 | Liliya | Sh. Popatbhai Maganbhai Dhanani | 2007-09-08 |  |  |  | 1 |  | Snapping of LT conductor at shakle point. |  |  | Aug-08
41 | AMR | S'Kundla | Khambha | Sh.A.R.Bhatt. (App. Line Man) | 2007-10-08 |  | 1 |  |  |  | When working on 11kv nanudi feeder, He experienced induction and fall from the pole. | Not used any safety tools while working on line. | Instruction has already been given to line staff for using safety tools while working. | Aug-08
42 | AMR | S'Kundla | SKD(R) | Sh. Rambhai Chhaganbhai Dhameliya. | 28/7/2007 Reporting on Aug.07 |  |  | 1 |  |  | Victim brother informe on dt.30.7.07, after two days of accedent occurred. We have not found any evidance at the site but victime had try to Lungar from Ex.Lt line. |  |  | Aug-08
43 | AMR | Una | Una-2 | A cow of Sh. Kiritbhai Anupbhai | 3-8-07 |  |  |  |  | 1 | Snapping of LT conductor |  |  | Aug-08
44 | AMR | Una | Una-1 | A buffalo of Babubhai Mulubhai | 6-8-07 |  |  |  |  | 1 | Snapping of LT conductor |  |  | Aug-08
45 | AMR | Una | Una-1 | A buffalo of Hirabhai Vaghbhai | 13-8-07 |  |  |  |  | 1 | Snapping of 11 KV conductor |  |  | Aug-08
46 | AMR | Una | Una-2 | A buffalo of Jayantibhai Rambhai | 16-8-07 |  |  |  |  | 1 | Snapping of LT conductor |  |  | Aug-08
47 | AMR | Amreli-2 | Dhari | A buffalo of Bhagvanbhai Thakarshibhai | 17-7-07 Reporting on Aug. 07 |  |  |  |  | 1 | Leakage current of LT pole earthing |  |  | Aug-08
48 | AMR | Amreli-2 | Kunkavav | Sh. Shankarbhai Lakahbhai Nayak | 2-8-07 |  |  | 1 |  |  | Leakage earthing wire of transformer, and touched with guy wire, victim was touched guy wire |  | Necessary maintenance of transformer is carried out | Aug-08
49 | AMR | Amreli-2 | Kunkavav | Sh. V.M. Dabhi (V.S. Helper) | 9-8-07 |  | 1 |  |  |  | Sh. V.M. Dabhi was attending a lighting fault on PSC pole, and he experienced induction and fell from pole | He has not used any safety tools while working on line | Instruction has already been given to line staff for using safety tools while working. | Aug-08
50 | AMR | Amreli-2 | Chalala | A buffalo of Sh. Ghanshyamhai Ukabhai | 11-8-07 |  |  |  |  | 1 | Leakage of transformer earthing wire |  |  | Aug-08
51 | AMR | Amreli-2 | Bagasara | A buffalo of Ghelabhai Ukabhai | 14-8-07 |  |  |  |  | 1 | Snapping of LT conductor |  |  | Aug-08
52 | AMR | Amreli-2 | Kunkavav | Sh. Hiteshbhai Devabhai Padhiyar | 18-8-07 |  |  | 1 |  |  | Victim was removing flexible wire from plug one wire were on his hand, and other wire in plug, he touched open wire |  |  | Aug-08
53 | AMR | Amreli-2 | Bagasara | A cow of Sh. Jasabhai Devayatbhai | 26-8-07 |  |  |  |  | 1 | Snapping of L.T. cond. |  |  | Aug-08
54 | AMR | Amreli-2 | Dhari | A buffalo of Punjabhai Caprajbhai | 10-8-07 |  |  |  |  | 1 | Leakage power of X'mer earthing |  |  | Aug-08
55 | AMR | S'Kundla | Rajula | FH - Sh. Rameshbhai Jivabhai NFH - (1) Sh. Kanubhai Ravjibhai | 19-8-07 |  |  | 1 | 1 |  | Due to heavy rain and wind presure tree branch fall on L.T. live cond. |  |  | Aug-08
56 | AMR | Una | Kodinar-1 | A buffalo of Sh. Bhimabhai Balubhai | 11-8-07 |  |  |  |  | 1 | Leakage power of Tranformer earthing. |  |  | Aug-08
57 | AMR | Una | Kodinar-2 | A buffalo of Mandanbhai Hamirbhai | 12-8-07 |  |  |  |  | 1 | Leakage power of PSC pole earthing |  |  | Aug-08
58 | AMR | Una | Una-1 | A buffalo of Ranabhai Sarmanbhai | 27-8-07 |  |  |  |  | 1 | Leakage power of Tranformer earthing. |  |  | Aug-08
59 | AMR | Una | Kodinar-1 | A buffalo of Masaribhai Bhagvanbhai | 28-8-07 |  |  |  |  | 1 | Snapping of L.T. cond. |  |  | Aug-08
60 | AMR | Una | Kodinar-1 | A bullock of Pratapbhai Kacharabhai | 29-8-07 |  |  |  |  | 1 | Snapping of L.T. cond. |  |  | Aug-08
61 | AMR | Una | Una-2 | Smt. Rudiben Kanabhai Sankhat | 11-8-07 |  |  |  | 1 |  | Snapping of L.T. cond. |  |  | Aug-08
62 | AMR | Una | Una-2 | A buffalo of Lajibhai Bhanabhai | 10-8-07 |  |  |  |  | 1 | Snapping of L.T. cond. |  |  | Aug-08
63 | AMR | Una | Una (T) | A bullock of ValiMahmad Chauhan | 10-8-07 |  |  |  |  | 1 | Snapping of L.T. cond. |  |  | Aug-08
64 | AMR | Una | Una-2 | A bullock of Hajibhai Lakhabhai | 22-8-07 |  |  |  |  | 1 | Snapping of L.T. cond. |  |  | Aug-08
65 | AMR | Amreli-1 | Babra | Nirenbhai Rameshbhai Parmar | 30-8-07 |  |  | 1 |  |  | The victim came in contact with live 1 Ph wire due to faulty two pin connected with 1 Ph motor in his private premises. |  |  | Aug-08
66 | AMR | Amreli-1 | Babra | Sh.Arvindbhai Chhatrasing Bariya (contractar Man) | 2007-09-09 |  |  | 1 |  |  | Victim was working on line and fell from the pole Mech Acct.
67 | AMR | Amreli-1 | Amreli-R | 2no's Bullock of Sh.Govindbhai Nanjibhai | 2007-09-10 |  |  |  |  | 1 | Snapping of LT conductor
68 | AMR | Amreli-2 | Chalala | A Bullock of Sh.Nareshbhai Kanabhai. | 2007-09-03 |  |  |  |  | 1 | Snapping of LT conductor
69 | AMR | Amreli-2 | Dhari | Sh.Ashokbhai Laxmanbhai Rathava (ALM) | 2007-09-09 |  | 1 |  |  |  | Viktim was working 11kv fdr.but LT of Other fdr.cross and victim experienced induction and fell from pole. | He has not used any safety tools while working on line | Instruction has already been given to line staff for using safety tools while working.
70 | AMR | Amreli-2 | Dhari | Smt.Bhanube Kantilal | 20-09-07 |  |  | 1 |  |  | Accident accured in his premises.
71 | AMR | Amreli-2 | Dhari | 2no's cow of Sh.Gokalbhai Danabhai | 24-09-07 |  |  |  |  | 1 | Snapping of LT conductor
72 | AMR | Amreli-2 | Dhari | Buffalo of Sh. Madhabhai Dhanjibhai | 27-09-07 |  |  |  |  | 1 | Snapping of LT conductor
73 | AMR | S'Kundla | Savarkundla® | Buffalo of Sh.Rameshbhai Virjibhai. | 2007-03-09 |  |  |  |  | 1 | Leakage current of LT pole earthing
74 | AMR | S'Kundla | Rajula | Buffalo of Sh.Mulubhai Smatbhai. | 25-09-07 |  |  |  |  | 1 | Leakage current of LT pole earthing
75 | AMR | Una | Una-2 | Bullock of sh.Ajibhai lakhabhai | 22-08-07 |  |  |  |  | 1 | Snaping of LT conductor
76 | AMR | Una | Una-1 | Buffalo of sh.Natha dana | 2007-01-09 |  |  |  |  | 1 | Leakage current of Transeformer earthing wire
77 | AMR | Una | Una-2 | Buffalo of sh.Nanabhai atabhai | 16-09-07 |  |  |  |  | 1 | Leakage current of Transeformer earthing wire
78 | AMR | Una | Una-1 | Buffalo of sh.Hamirbhai Jethabhai | 20-09-07 |  |  |  |  | 1 | Snaping of LT conductor
79 | AMR | Una | Una-1 | 3'no of Buffalo sh.Bhikhabhai baubhai | 21-09-07 |  |  |  |  | 1 | Snaping of LT conductor
80 | AMR | Una | Kodinar-2 | Buffalo of sh.kadubhai ukabhai | 22-09-07 |  |  |  |  | 1 | Snaping of LT conductor
81 | AMR | Una | Kodinar-2 | Buffalo of sh.Dadubhai sardulbhai | 27-08-07 |  |  |  |  | 1 | Leakage current of Transeformer earthing wire
82 | AMR | Una | Kodinar-2 | Buffalo of sh.Manubhai naranbhai | 29-08-07 |  |  |  |  | 1 | Snaping of LT conductor
83 | AMR | Una | Una-1 | A cow of sh.Nanabhai pachabhai | 27-09-07 |  |  |  |  | 1 | Leakage current of Transeformer earthing wire
84 | AMR | Una | Kodinar-2 | Buffalo of sh.Ghelabhai tapubhai | 18-09-07 |  |  |  |  | 1 | Leakage current of Transeformer earthing wire
85 | AMR | Una | Kodinar-2 | Buffalo of sh.Ranjitbhai naranbhai | 26-09-07 |  |  |  |  | 1 | Leakage current of Transeformer earthing wire
86 | AMR | Una | una_1 | FA to small ox of Shri Balubhai Kalubhai Gujariya | 29.09.2007 |  |  |  |  | 1 | not found any kind of fault in PGVCL line, accident occurred due to any reason.
87 | AMR | Una | Kodinar-1 | Farid Hussain Dhoki | 30.09.2007 |  |  | 1 |  |  | by taking illigeal power supply from pole non consumer and electrocuted.
88 | AMR | AMR-I | AMR-T | Champaben Harjibhai Solanki | 1.10.2007 |  |  |  | 1 |  | pvc twin core s/L accidently broken by private vehicle and said broken s/L wounded around the neck of victim
89 | AMR | Una | kodinar-2 | NF_Mechanical accident to Shri Samat Hira Madha | 2.10.2007 |  |  |  | 1 |  | due to breaking of psc pole.
90 | AMR | AMR-II | Bagasara | FA to cow of shri Lalabhai Gababhai Matiya | 3.10.2007 |  |  |  |  | 1 | snapping of 11 kv conductor from disc insulator
91 | AMR | Una | una_2 | FA to 2 no of Buffallo (1) shri Lakha Bhaya jadav & (2) shri Jivabhai Rambhai Parmar | 5.10.2007 |  |  |  |  | 1 | snapping of LT conductor
92 | AMR | Una | kodinar-I | FA to Buffalo of shri Oghadbhai Ranabhai Parmar | 9.10.2007 |  |  |  |  | 1 | due to snapping of conductor
93 | AMR | Amreli-2 | Bagasara | NFH_Mechanical accident to Deptt. Person Shri A.H.Chauhan (ALM) | 9.10.2007 |  | 1 |  |  |  | loosing balance during working on DP Structure due to slipping of conductor from disc insulator
94 | AMR | AMR-II | Dhari | FA to Chhagan Parsottam Sardhara | 9.10.2007 |  |  | 1 |  |  | Snapping of LT conductor
95 | AMR | Amreli-2 | Dhari | NFH to Deptt. Person Manishkumar M Pandya_VS Helper | 9.10.2007 |  | 1 |  |  |  | while attending the jumper fault experience jerk and felt from the transformer center.
96 | AMR | AMR-II | Dhari | FA to cow (Rowery) | 13.10.2007 |  |  |  |  | 1 | Snapping of LT conductor
97 | AMR | AMR-II | Dhari | FA to 5 nos of wild animal (3 lioness + 2 cub) | 12.10.2007 informed on dtd. 19.10.2007 |  |  |  |  | 1 | Ag-consumer have illigelly connected power supply from LT line passing through his field in the fencing lying around his ag. Land. The said animals came in contact and electrocuted.
98 | AMR | AMR-II | Chalala | NF_Mechanical Accident to o/s human shri Rajubhai Nanjibhai Rathod age_22 yrs at village Lakhapadar | 24.10.2007 |  |  |  | 1 |  | due to breaking of psc pole
99 | AMR | AMR-I | AMRELI RURAL | Non fatal accident to Shri Hanubha Takhtasinh Jadeja age 40 yrs at village Bai Dudhala | 3.11.07 |  |  |  | 1 |  | While providing DO fuse wire of TC Victim used Short Bamboo rod and climb at some height on TC pole, DO fuse wire touched to DO Angle, Victim got electric shock through Earth wire and met with Non fatal accident | partially utlilized | victim is a contractor person and issued a notice to the victim for utlization of safety tools
100 | AMR | UNA | UNA-II | fatal accident to buffallo of shri Balubhai Lakhabhai Dangodra at village Juna_Ugala | 4.11.07 |  |  |  |  | 1 | snapping of 11 KV conductor |  | maintainance work carried out
101 | AMR | UNA | kodinar-II | fatal accident to cow of shri Hirabhai Ranabhai Jotava at village vadnagar | 5.11.07 |  |  |  |  | 1 | due to heavy rain and wind pressure conductor snapped |  | maintainance work carried out
102 | AMR | UNA | kodinar-II | fatal accident to Nathiben Jeshabhai Gadhe and Non fatal Accident to Valiben Kalabhai Chandera | 11.11.07 |  |  | 1 | 1 |  | L T pole was broken by truck driver Motigar Arfebbhai Goswami while driving truck No. GJ -10W -7981 in rough manner. One woman fell down due to breaking of LT P.S.C. pole and met with fatal accident. Another got electric shock due to falling of live cond |  | FIR LODGE AGAINST THE TRUCK DRIVER BY THE CONCERN DE vide no 114/07
103 | AMR | UNA | kodinar-II | fatal accident to o/s late Arshibhai Kanabhai Chudasama at village Dolasa | 16.11.07 |  |  | 1 |  |  | while pulling out mobile charger from the three pin socket accidently came in contact of live phase and electrocuted | victim himself is responsible | victim himself was responsible, said accident occurred in his private premises.
104 | AMR | Una | kodinar-II | Fatal accident to O/S late Rajesh Govind Vaja at village Mityaz Navapara | 29.12.07 | 0 | 0 | 1 | 0 | 0 | snapping of 11KV conductor from the shackle point insulator hardware and snapped conductor from load side lying on the road and at a same time victim passing through the road and came in contact with the snapped conductor and electrocuted.
105 | AMR | S'Kundla | Jafrabad | Non fatal accident to Shri Sarvansinh age 40 yrs at village Gangad Taluka Jafrabad | 31.12.07 | 0 | 0 | 0 | 1 | 0 | container having height having 9.6' touched the 11 kv line and tyre of the container was totally burnt, when victim came in the contact of live part of the container, he got the electric shock.
106 | AMR | Una | kodinar-II | Fatal accident to buffallo of shri Bhupatbhai Kantibhai Soanki at villageNani Garmali tal:Chalala | 7.01.08 | 0 | 0 | 0 | 0 | 1 | leakage of current from the transformer earthing of village t/c |  | maintainance work carried out.
107 | AMR | Amreli_I | Chital | Fatal accident to O/S human late sumitraben VajupariGosai-age 32 yrs at village Manchiyala taluka amreli dist amreli | 06.3.08 | 0 | 0 | 1 | 0 | 0 | open extention code wire touched the iron roof of house and hence leakage current flow through the iron string utlised for hanging the wet clothes, victim touched the iron string and got electric shock. |  | victims herself was responsible and hence said accident occurred in her private primises.
108 | AMR | Amreli_I | Lilya | Fatal accident to he-buffallo and she buffallo of shri Kanubhai Dayabhai Bambha at village Mota kankot Tal;Lilya, Dist Amreli | 25.03.08 | 0 | 0 | 0 | 0 | 2 | private truckGJ11U 8691 damaged the psc pole and hence conductor snapped on the animals and animal came contact with live conductor and electrocuted |  | FIR lodge against the vehicle driver of v.no:GJ11 U 869. FIR lodge by the owner of the animal shri Kanubhai Dayabhai Bambha.
1 | SNR | SNR 1 | LIMBADI ( T) | Hasmukhbhai Bababhai | 2007-05-17 |  |  |  | 1 |  | Snapping of Conductor | NA | NA
2 | SNR | SNR 1 | S`nagar city 1 | Daxaben Pareshbhai Parmar | 2007-05-24 |  |  | 1 |  |  | Internal wiring | NA | NA
3 | SNR | SNR 1 | LIMBADI ( T) | Bijalbhai Ishwerbhai Rangpara | 2007-06-12 |  | 1 |  |  |  | Slipping from pole |  | NA
4 | SNR | SNR 1 | Jorawernagar | Dhirubhai Devjibhai Makwana | 2007-06-29 |  | 1 |  |  |  | Entered in induction zone of HT while working on LT Line
5 | SNR | SNR 2 | Muli | Nakubhai Hathibhai | 2007-06-01 |  |  |  | 1 |  | Snapping of Conductor | NA | NA
6 | SNR | SNR 2 | Muli | Mukeshbhai Bijalbhai | 2007-06-01 |  |  |  | 1 |  | Snapping of Conductor | NA | NA
7 | SNR | DHG | DGH R | Rajeshbhai Ratilal Darji | 2007-06-05 |  |  |  | 1 |  | Snapping of conductor | NA | NA
8 | SNR | SNR 1 | LSD R | BUFF of Bhikhubhai Shivubhai | 2007-06-01 |  |  |  |  | 1 | Broken of LT Pole | NA | NA
9 | SNR | SNR 1 | Wadhwan | Cow of Bijalbhai Sagrambhai | 2007-06-21 |  |  |  |  | 1 | Snapping of Conductor | NA | NA
10 | SNR | SNR 1 | LSD R | BUFF of Nazabhai Dhanabhai | 2007-06-21 |  |  |  |  | 1 | TC Earthing Leakage | NA | NA
11 | SNR | SNR 1 | S`nagar city 2 | Cow of Sagrambhai Malabhai | 2007-06-06 |  |  |  |  | 1 | Snapping of Conductor | NA | NA
12 | SNR | SNR 1 | LSD R | BUFF of Kasirambhai Nagarbhai | 2007-06-15 |  |  |  |  | 1 | Pole Earthing Leakage | NA | NA
13 | SNR | SNR 2 | Sayla | Panchabhai Nathabhai Bharwad | 2007-06-17 |  |  |  |  | 1 | TC Earthing Leakage | NA | NA
14 | SNR | SNR 2 | Muli | Buffalow of Madhuben Becharbhai | 2007-06-18 |  |  |  |  | 1 | TC Earthing Leakage | NA | NA
15 | SNR | SNR 2 | Muli | Bufallow of Ratansang Malubhai | 2007-06-21 |  |  |  |  | 1 | HT Pole earthing GI wire struct in horn of BUFF. Which touch to jumper on pole | NA | NA
16 | SNR | SNR 2 | Chotila | BUFF of Rupabhai Khimabhai | 2007-06-19 |  |  |  |  | 1 | Pole Earthing Leakage | NA | NA
17 | SNR | DHG | Patdi | Buffalow of Balubha Jalamsang | 2007-06-15 |  |  |  |  | 1 | Snapping of conductor | NA | NA
18 | SNR | SNR 2 | Sayla | Panchabhai Nathabhai Bharwad | 2007-06-17 |  |  | 1 |  |  | TC Earthing Leakage | NA | NA
19 | SNR | DHG | Rajsitapur | Kanjibhai Rajabhai Rabari | 2007-05-31 |  |  | 1 |  |  | Internal wiring | NA | NA
20 | SNR | DHG | DGH R | Altafbhai Bachubhai Sipai | 2007-06-05 |  |  |  | 1 |  | Snapping of conductor | NA | NA
21 | SNR | DHG | DGH R | Kalubhai Amarshibhai | 2007-06-05 |  |  |  | 1 |  | Snapping of conductor | NA | NA
22 | SNR | DHG | Halwad | Satabhai Butabhai Bharwad |  |  |  |  | 1 |  | Mech Accedent Pole broken | NA | NA
23 | SNR | SNR 1 | S`nagar city 1 | Cow of Bhimabhai Satabhai Bharwad | 2007-07-09 |  |  |  |  | 1 | Leakage from st ltg fixture | NA | NA
24 | SNR | SNR 2 | Than | BUFF of Bhabhalubhai Vastabhai Khachar | 2007-07-05 |  |  |  |  | 1 | TC Earthing Leakage | NA | NA
25 | SNR | DHG | Rajsitapur | Maheshbhai Ranchhobhai Koli | 2007-07-01 |  |  | 1 |  |  | Direct contact with 22 KV line | NA
26 | SNR | DHG | Halwad | BUFF of Musa Daud Ghanchi | 2007-07-05 |  |  |  |  | 1 | Snapping of conductor | NA | NA
27 | SNR | DHG | Halwad | BUFF Of Dilipbhai Shivabhai Patel | 2007-07-02 |  |  |  |  | 1 | Snapping of conductor | NA | NA
28 | SNR | DHG | Halwad | BUFF Of Bipinbhai Chhaganbhai | 2007-07-14 |  |  |  |  | 1 | TC Earthing Leakage | NA | NA
29 | SNR | DHG | Patdi | BUFF of GovindbhaiSandhabhai | 2007-06-30 |  |  |  |  | 1 | Snapping of conductor | NA | NA
30 | SNR | SNR 2 | Muli | Kanchanben Dhirubhai Rathod | 2007-06-01 |  |  | 1 |  |  | Internal wiring | NA | NA
31 | SNR | DHG | Patdi | Babubhai Bhagwandas Mali | 2007-06-25 |  |  | 1 |  |  | Internal wiring | NA | NA
32 | SNR | SNR 1 | LSD R | Kishorbhai Bhavanbhai Chawda | 2007-07-13 |  |  | 1 |  |  | Internal wiring | NA | NA
33 | SNR | SNR 1 | LSD R | BULL OF SHARIFABEN RUSTAMBHAI | 2007-07-15 |  |  |  |  | 1 | Snapping of conductar | NA | NA
34 | SNR | SNR 1 | LSD R | Shafiq Yakubbhai Bhadula | 2007-07-31 |  |  | 1 |  |  | Snapping of conductar | NA | NA
35 | SNR | SNR 1 | LSD R | Kanjibhai Keshubhai Makwana | 2007-08-04 |  |  | 1 |  |  | Internal wiring | NA | NA
36 | SNR | SNR 1 | Jorawernagar | Atulbhai Devendrabhai Trivedi ALM | 2007-08-03 |  | 1 |  |  |  | Mechanical Accedent | Not
37 | SNR | SNR 2 | S`nagar Rural | Buff. Of Laxmanbhai Kalubhai | 2007-08-01 |  |  |  |  | 1 | TC Earthing Leakage
38 | SNR | DHG | DHG Rural | Bhikhubhai Hindubhai Saraiya | 2007-08-08 |  |  | 1 |  |  | Internal wiring | NA | NA
39 | SNR | DHG | Halwad | Hiteshbhai Jamanbhai Jasani | 2007-08-14 |  |  | 1 |  |  | Matter is under investigation | NA | NA
40 | SNR | SNR 2 | Chotila | She Horse Of Sh Bhabhlubhai Pithubhai | 2007-08-03 |  |  |  |  | 1 | Leakage of earthing | NA | NA
41 | SNR | SNR 1 | Wadhwan | Kapil Khimjibhai Bhatt | 2007-08-28 |  |  | 1 |  |  | Came in contact of live LT Phase, while climbed on truck. | NA | NA
42 | SNR | SNR 1 | S`nagar city 2 | Nilamben | 2007-07-10 |  |  |  | 1 |  | Leakage from st ltg fixture | NA | NA
43 | SNR | SNR 1 | S`nagar city 1 | Cow of Sh Devabhai Kunvarabhai | 2007-07-02 |  |  |  |  | 1 | Snapping of Conductor | NA | NA
44 | SNR | SNR 1 | LSD R | BUFF of Dashrathbhai Gangubhai | 2007-08-27 |  |  |  |  | 1 | Snapping of conductar | NA | NA
45 | SNR | DHG | PATADI | Buff of Somabhai Gandabhai | 2007-07-29 |  |  |  |  | 1 | Snapping of conductor | NA | NA
46 | SNR | SNR 1 | LSD R | BUFF of Sh Kasam Umar | 2007-09-10 |  |  |  |  | 1 | Leakage of earthing | NA | NA
47 | SNR | SNR 2 | Sara | Buff of Sh Chhhana Chatur | 2007-09-25 |  |  |  |  | 1 | Bufalow came in contact of 11 KV through Stay, while rubbing head with stay | NA | NA
48 | SNR | SNR 2 | Sayla | Lalabhai Kacharabhai Patel | 2007-09-12 |  |  | 1 |  |  | Came in contact of live 11 KV Line on Roof of hotel | NA | NA
49 | SNR | SNR 2 | Sayla | Ox of Sh Hamirbhai Dolabhai | 2007-09-29 |  |  |  |  | 1 | Snapping of Conductor | NA | NA
50 | SNR | SNR 2 | S`nagar Rural | Cow of Sh Manjibhai Chhaganbhai Panara | 2007-09-28 |  |  |  |  | 1 | Snapping of Conductor | NA | NA
51 | SNR | DHG | Halwad | Buff of Sh Rameshbhai Bhurabhai Bharwad | 2007-09-24 |  |  |  |  | 1 | Snapping of Conductor | NA | NA
52 | SNR | DHG | PATADI | Cow of Sh Hindubhai Vastabhai | 2007-08-29 |  |  |  |  | 1 | Snapping of Conductor | NA | NA
53 | SNR | SNR 1 | LSD R | Hiteshkumar Dalpatbhai at vill Khambhalav | 2007-09-19 |  |  |  | 1 |  | Came in contact of HT Line | n a
54 | SNR | SNR 1 | S`nagar city 1 | Meenaben Bhupatbhai Vaghela | 2007-09-22 |  |  | 1 |  |  | Internal wiring
55 | SNR | SNR 1 | LSD R | BUFF of Sh Rameshbhai Dayaram Dalwadi Karmad | 2007-09-23 |  |  |  |  | 1 | Leakage of earthing
56 | SNR | SNR 1 | S`nagar city 2 | Dipakbhai Premjibhai Parmar Employee P&T | 2007-10-03 |  |  | 1 |  |  | Came in contact of LT while tying the P&T line on LT Pole
57 | SNR | SNR 1 | LSD R | Hiraben Dalpatbhai Rathod At vill Ankevaliya | 2007-10-03 |  |  |  | 1 |  | Snapping of LT Conductor
58 | SNR | SNR 1 | LSD R | BUFF of Sh Bhagwan Arfeb Jograna At vill Ranagadh | 2007-10-11 |  |  |  |  | 1 | Snapping of LT Conductor
59 | SNR | DHG | DHG Rural | Sh Girishbhai Natvarbhai Raval LM | 2007-10-05 | 1 |  |  |  |  | Mech. Accd. Due to PSC Pole Broken
60 | SNR | SNR 2 | S`nagar Rural | Cow of Sh Manji Chhagan At vill Dudhrej | 2007-09-28 |  |  |  |  | 1 | Snapping of HT Conductor
61 | SNR | SNR 1 | S`nagar city 1 | Buff of Sh Laljibhai Merabhai Bharwad | 2007-11-08 |  |  |  |  | 1 | Leakage of StreetLight Ph
62 | SNR | SNR 2 | Chotila | Buff of Sh Ranchhodbhai Dayabhai Rajpara vill Mokasar | 2007-11-08 |  |  |  |  | 1 | Leakage of earthing
63 | SNR | DHG | Rajsitapur | R G Vora ALM, Rajubhai Masarusinh, Madanbhai Masrusinh at vill Dudapur | 2007-11-19 |  | 1 |  |  |  | Cont.`s labor climbed on live line for rejumpering, while ALM & other one working on dead section got momentory jerk of 11 KV Power.
64 | SNR | SNR 1 | LSD R | Sh Ghanshyambhai Bhikhabhai Chauhan At vill Chokadi | 2008-07-03 |  |  | 1 |  |  | Came in direct contact of 11 KV line while filling the building Slabe. | NA | NA
65 | SNR | SNR 1 | LIMBADI ( T) | Sh Mukeshbhai Mohanbhai Nakiya App. LM at vill Limbdi | 27-03-08 |  | 1 |  |  |  | Climbed up on wrong feeder pole. |  | Explanation from ALM Sh M D Chauhan is asked.
66 | SNR | DHG | Charadwa | Sh Mansukhbhai Bhavabhai At vill Chupani | 31-03-08 |  |  | 1 |  |  | Came in direct contact of 11 KV line when he climbed on Tree. | NA | NA
Total | [5 empty] | 10 | 80 | 179 | 101 | 409
[6 empty] | 10 | 81 | 181 | 101 | 409